## WindTurbineConfiguration
3.4 MW IEA Task 37 Onshore Wind Turbine
Wind Turbine Configuration Data
Class and Category | IEC Class 3A
Rotor Rotation | Clockwise rotation
Rotor Orientation | Upwind
Number of Blades | 3
Control | Variable speed collective pitch
Drivetrain | Single Stage
Rated Aerodynamic Power | 3.6 | [MW]
Rotor Diameter | 130 | [m]
Hub Height | 110 | [m]
Rotor Cone Angle | 3 | [deg]
Nacelle Uptilt Angle | 5 | [deg]
Rotor Overhang | 5 | [m]
Length Blade Root Flange | 2 | [m]
Hub Mass | 27975 | [kg]
Nacelle Mass | 190612 | [kg]
Generator Mass | 0 | [kg]
Blade Mass | 16441.1896 | [kg]
Tower Mass | 553.1702 | [tons]
Blade Cost | 120901.5661 | [$]
Tower Cost | 829755.2825 | [$]
Aerodynamic AEP static | 14985.3259 | [MWh]
Electrical AEP static | 13936.3531 | [MWh]
Aerodynamic AEP turbulent | 14134.9797 | [MWh]
Electrical AEP turbulent | 13145.5311 | [MWh]
CoE | 44.1813 | [$/MWh]
Version | Date | Author | Institution | Comments
1 | 2016-03-23 | Charles Giachetti | TUM
2 | 2016-08-24 | Pietro Bortolotti | TUM | New mech power, new tip speed
3 | 2016-11-09 | Pietro Bortolotti | TUM | Design optimization
3.2 | 2016-11-11 | Pietro Bortolotti | TUM | 3 Seeds DLC 11,13
3.3 | 2016-12-19 | Pietro Bortolotti | TUM | New chord, new t/c
3.4 | 2017-01-09 | Pietro Bortolotti | TUM | Prebend limited to 2.5 m
3.5 | 2017-05-02 | Pietro Bortolotti | TUM | New blade root
3.6 | 2017-08-25 | Pietro Bortolotti | TUM | Correction nsm, new overhang (+1m), chord distrib adjusted
3.7 | 2017-09-19 | Pietro Bortolotti | TUM | Straight LE, new blade root thickness, internal geometry of blade struct.ure adjusted
3.8 | 2017-09-29 | Pietro Bortolotti | TUM | Max chord 4.3 m, flatback airfoils
3.9 | 2017-12-19 | Pietro Bortolotti | TUM | Slight adjustment of blade internal structure
4 | 2018-01-15 | Pietro Bortolotti | TUM | New polars for flatback airfoils, new struct opt
4.1 | 2018-07-13 | Pietro Bortolotti | TUM | Reduced nacelle and generator mass and new efficiency from new DriveSE calculations
4.2 | 2018-07-16 | Helena Canet | TUM | Nacelle, Hub, DT and Actuators tab adapted to Cp-Max v38; Generator considered in the nacelle
4.3 | 2018-08-30 | Helena Canet | TUM | Loads updated

## WTControl
Wind Turbine Control Data
Cp Rated | 0.47304 | [-]
Pitch Rated | 0.86965 | [deg]
TSR Rated | 8.1633 | [-]
Omega Rated | 11.753 | [rpm]
Torque Rated | 2.925 | [MNm]
Max Tip Speed | 80 | [m/s]
Cut In Wind Speed | 3 | [m/s]
Cut Out Wind Speed | 25 | [m/s]
Wind Speed Rated | 9.8 | [m/s]
Min Rotor Speed | 3.7677 | [rpm]
Max Rotor Speed | 12.9283 | [rpm]
Sample Time Controller | 0.02 | [s]
Look Up Table WT States | [6 empty] | Turbulent Mech Power Curve
Wind Speed | Cp | Pitch angle | TSR | Omega | Torque | Power | Wind Speed | Aero Power | Electr. Power | Aero Power Min | Electr. Power Min | Aero Power Max | Electr. Power Max. | Aero Power Std | Electr. Power Std.
[m/s] | [-] | [deg] | [-] | [rpm] | [MNm] | [MW] | [m/s] | [MW] | [MW] | [MW] | [MW] | [MW] | [MW] | [MW] | [MW]
3 | 0.47647 | 1.1728 | 8.5487 | 3.7677 | 0.26508 | 0.10459 | 3.994 | 0.31163 | 0.3054 | 0.027425 | 0.026877 | 0.70651 | 0.69238 | 0.1369 | 0.13416
3.1 | 0.47657 | 1.1728 | 8.5487 | 3.8933 | 0.28311 | 0.11542 | 4.0686 | 0.33533 | 0.32862 | 0.05756 | 0.056409 | 0.80874 | 0.79257 | 0.19425 | 0.19036
3.2 | 0.47667 | 1.1728 | 8.5487 | 4.0189 | 0.30173 | 0.12698 | 4.0639 | 0.3182 | 0.31183 | 0.044016 | 0.043136 | 0.98711 | 0.96736 | 0.15809 | 0.15493
3.3 | 0.47677 | 1.1728 | 8.5487 | 4.1445 | 0.32095 | 0.13929 | 5.0032 | 0.55865 | 0.54748 | 0.016324 | 0.015997 | 1.2551 | 1.23 | 0.29759 | 0.29164
3.4 | 0.47687 | 1.1728 | 8.5487 | 4.2701 | 0.34076 | 0.15238 | 5.031 | 0.6166 | 0.60427 | 0.039868 | 0.039071 | 2.0496 | 2.0086 | 0.42595 | 0.41743
3.5 | 0.47697 | 1.1728 | 8.5487 | 4.3957 | 0.36118 | 0.16626 | 4.9211 | 0.57684 | 0.5653 | 0.10141 | 0.099382 | 1.3626 | 1.3353 | 0.29257 | 0.28672
3.6 | 0.47707 | 1.1728 | 8.5487 | 4.5213 | 0.38219 | 0.18095 | 7.0577 | 1.5016 | 1.4716 | 0.19461 | 0.19072 | 2.8592 | 2.802 | 0.58939 | 0.57761
3.7 | 0.47716 | 1.1728 | 8.5487 | 4.6469 | 0.4038 | 0.1965 | 6.9171 | 1.5012 | 1.4711 | 0.25717 | 0.25203 | 3.1966 | 3.1327 | 0.71127 | 0.69705
3.8 | 0.47726 | 1.1728 | 8.5487 | 4.7724 | 0.42601 | 0.21291 | 6.8769 | 1.4018 | 1.3738 | 0.36039 | 0.35318 | 2.8321 | 2.7754 | 0.53349 | 0.52282
3.9 | 0.47736 | 1.1728 | 8.5487 | 4.898 | 0.44882 | 0.23021 | 8.7478 | 2.7708 | 2.7154 | 0.50341 | 0.49334 | 5.1677 | 5.0644 | 0.82385 | 0.80737
4 | 0.47746 | 1.1728 | 8.5487 | 5.0236 | 0.47223 | 0.24843 | 8.9869 | 2.8097 | 2.7535 | 0.93885 | 0.92007 | 5.5033 | 5.3933 | 1.0691 | 1.0477
4.1 | 0.47756 | 1.1728 | 8.5487 | 5.1492 | 0.49624 | 0.26758 | 9.1623 | 2.8978 | 2.8398 | 1.2717 | 1.2463 | 5.1057 | 5.0036 | 0.82113 | 0.8047
4.2 | 0.47766 | 1.1728 | 8.5487 | 5.2748 | 0.52085 | 0.28771 | 10.8945 | 3.5857 | 3.514 | 1.5228 | 1.4924 | 5.4519 | 5.3429 | 0.65215 | 0.6391
4.3 | 0.47776 | 1.1728 | 8.5487 | 5.4004 | 0.54606 | 0.30881 | 11.0715 | 3.7001 | 3.6261 | 1.4015 | 1.3735 | 5.0779 | 4.9763 | 0.49468 | 0.48479
4.4 | 0.47786 | 1.1728 | 8.5487 | 5.526 | 0.57187 | 0.33093 | 11.0705 | 3.6598 | 3.5866 | 2.0731 | 2.0317 | 5.3531 | 5.2461 | 0.48175 | 0.47211
4.5 | 0.47795 | 1.1728 | 8.5487 | 5.6516 | 0.59828 | 0.35408 | 13.1035 | 3.8396 | 3.7628 | 3.3395 | 3.2727 | 4.6951 | 4.6012 | 0.22283 | 0.21838
4.6 | 0.47805 | 1.1728 | 8.5487 | 5.7772 | 0.6253 | 0.3783 | 13.0132 | 3.8513 | 3.7743 | 3.0927 | 3.0308 | 6.0188 | 5.8984 | 0.34096 | 0.33414
4.7 | 0.47815 | 1.1728 | 8.5487 | 5.9028 | 0.65292 | 0.40359 | 12.9579 | 3.8483 | 3.7714 | 3.1734 | 3.11 | 5.6103 | 5.4981 | 0.28022 | 0.27461
4.8 | 0.47825 | 1.1728 | 8.5487 | 6.0284 | 0.68114 | 0.42999 | 15.0084 | 3.8187 | 3.7423 | 3.5467 | 3.4758 | 5.2507 | 5.1457 | 0.14736 | 0.14442
4.9 | 0.47835 | 1.1728 | 8.5487 | 6.1539 | 0.70996 | 0.45753 | 15.1229 | 3.8283 | 3.7517 | 3.4766 | 3.407 | 5.301 | 5.195 | 0.16544 | 0.16214
5 | 0.47845 | 1.1728 | 8.5487 | 6.2795 | 0.73939 | 0.48621 | 14.9899 | 3.8156 | 3.7393 | 3.541 | 3.4702 | 4.1586 | 4.0754 | 0.074635 | 0.073142
5.1 | 0.47855 | 1.1728 | 8.5487 | 6.4051 | 0.76941 | 0.51608 | 16.8575 | 3.8085 | 3.7323 | 3.623 | 3.5505 | 4.0341 | 3.9534 | 0.05536 | 0.054253
5.2 | 0.47864 | 1.1728 | 8.5487 | 6.5307 | 0.80005 | 0.54715 | 17.0383 | 3.8057 | 3.7296 | 3.6643 | 3.5911 | 3.987 | 3.9073 | 0.049969 | 0.04897
5.3 | 0.47874 | 1.1728 | 8.5487 | 6.6563 | 0.83129 | 0.57945 | 16.8355 | 3.808 | 3.7318 | 3.6715 | 3.598 | 3.9739 | 3.8944 | 0.040807 | 0.039991
5.4 | 0.47884 | 1.1728 | 8.5487 | 6.7819 | 0.86313 | 0.61299 | 18.8439 | 3.8051 | 3.729 | 3.622 | 3.5496 | 3.9667 | 3.8874 | 0.050505 | 0.049495
5.5 | 0.47894 | 1.1728 | 8.5487 | 6.9075 | 0.89558 | 0.64782 | 19.0407 | 3.8043 | 3.7282 | 3.6472 | 3.5742 | 3.9766 | 3.897 | 0.050812 | 0.049796
5.6 | 0.47904 | 1.1728 | 8.5487 | 7.0331 | 0.92863 | 0.68394 | 18.8253 | 3.8062 | 3.7301 | 3.6613 | 3.5881 | 3.948 | 3.8691 | 0.04099 | 0.04017
5.7 | 0.47914 | 1.1728 | 8.5487 | 7.1587 | 0.96229 | 0.72139 | 20.8393 | 3.8038 | 3.7277 | 3.5897 | 3.5179 | 3.9997 | 3.9197 | 0.05252 | 0.05147
5.8 | 0.47924 | 1.1728 | 8.5487 | 7.2843 | 0.99656 | 0.76018 | 20.893 | 3.8052 | 3.7291 | 3.6236 | 3.5511 | 3.9671 | 3.8878 | 0.055228 | 0.054124
5.9 | 0.47934 | 1.1728 | 8.5487 | 7.4098 | 1.0314 | 0.80035 | 20.8975 | 3.8046 | 3.7285 | 3.6141 | 3.5418 | 3.9962 | 3.9162 | 0.055693 | 0.05458
6 | 0.47943 | 1.1728 | 8.5487 | 7.5354 | 1.0669 | 0.84191 | 22.8265 | 3.8033 | 3.7272 | 3.5748 | 3.5033 | 4.0024 | 3.9223 | 0.055931 | 0.054812
6.1 | 0.47953 | 1.1728 | 8.5487 | 7.661 | 1.103 | 0.88489 | 22.8872 | 3.8047 | 3.7286 | 3.6108 | 3.5386 | 3.9839 | 3.9042 | 0.058922 | 0.057744
6.2 | 0.47963 | 1.1728 | 8.5487 | 7.7866 | 1.1397 | 0.92932 | 22.8956 | 3.804 | 3.7279 | 3.5892 | 3.5174 | 3.9992 | 3.9192 | 0.059066 | 0.057885
6.3 | 0.47973 | 1.1728 | 8.5487 | 7.9122 | 1.177 | 0.97522 | 24.827 | 3.8039 | 3.7278 | 3.6238 | 3.5513 | 4.0003 | 3.9203 | 0.061058 | 0.059837
6.4 | 0.47983 | 1.1728 | 8.5487 | 8.0378 | 1.2149 | 1.0226 | 25.0874 | 3.8034 | 3.7273 | 3.5946 | 3.5227 | 4.0341 | 3.9534 | 0.06073 | 0.059515
6.5 | 0.47993 | 1.1728 | 8.5487 | 8.1634 | 1.2534 | 1.0715 | 24.8107 | 3.8053 | 3.7292 | 3.6389 | 3.5661 | 3.9537 | 3.8746 | 0.046807 | 0.04587
6.6 | 0.48003 | 1.1728 | 8.5487 | 8.289 | 1.2926 | 1.122
6.7 | 0.48012 | 1.1728 | 8.5487 | 8.4146 | 1.3323 | 1.174
6.8 | 0.48022 | 1.1728 | 8.5487 | 8.5402 | 1.3726 | 1.2276
6.9 | 0.48032 | 1.1728 | 8.5487 | 8.6658 | 1.4136 | 1.2828
7 | 0.48042 | 1.1728 | 8.5487 | 8.7913 | 1.4552 | 1.3397
7.1 | 0.4802 | 1.1728 | 8.5487 | 8.9169 | 1.4963 | 1.3973
7.2 | 0.47997 | 1.1728 | 8.5487 | 9.0425 | 1.5381 | 1.4565
7.3 | 0.47975 | 1.1728 | 8.5487 | 9.1681 | 1.5804 | 1.5173
7.4 | 0.47953 | 1.1728 | 8.5487 | 9.2937 | 1.6232 | 1.5798
7.5 | 0.4793 | 1.1728 | 8.5487 | 9.4193 | 1.6666 | 1.6439
7.6 | 0.47908 | 1.1728 | 8.5487 | 9.5449 | 1.7105 | 1.7097
7.7 | 0.47886 | 1.1728 | 8.5487 | 9.6705 | 1.755 | 1.7773
7.8 | 0.47863 | 1.1728 | 8.5487 | 9.7961 | 1.8001 | 1.8466
7.9 | 0.47841 | 1.1728 | 8.5487 | 9.9217 | 1.8457 | 1.9176
8 | 0.47819 | 1.1728 | 8.5487 | 10.0473 | 1.8918 | 1.9904
8.1 | 0.47796 | 1.1728 | 8.5487 | 10.1728 | 1.9385 | 2.0651
8.2 | 0.47774 | 1.1728 | 8.5487 | 10.2984 | 1.9857 | 2.1415
8.3 | 0.47752 | 1.1728 | 8.5487 | 10.424 | 2.0335 | 2.2197
8.4 | 0.47729 | 1.1728 | 8.5487 | 10.5496 | 2.0818 | 2.2999
8.5 | 0.47707 | 1.1728 | 8.5487 | 10.6752 | 2.1307 | 2.3819
8.6 | 0.47684 | 1.1728 | 8.5487 | 10.8008 | 2.1801 | 2.4658
8.7 | 0.47662 | 1.1728 | 8.5487 | 10.9264 | 2.23 | 2.5516
8.8 | 0.4764 | 1.1728 | 8.5487 | 11.052 | 2.2805 | 2.6394
8.9 | 0.47617 | 1.1728 | 8.5487 | 11.1776 | 2.3315 | 2.7291
9 | 0.47595 | 1.1728 | 8.5487 | 11.3032 | 2.3831 | 2.8208
9.1 | 0.47573 | 1.1728 | 8.5487 | 11.4288 | 2.4352 | 2.9145
9.2 | 0.4755 | 1.1728 | 8.5487 | 11.5543 | 2.4879 | 3.0102
9.3 | 0.47528 | 1.1728 | 8.5487 | 11.6799 | 2.541 | 3.108
9.4 | 0.47507 | 1.0872 | 8.5106 | 11.753 | 2.6064 | 3.2079
9.5 | 0.47473 | 1.0341 | 8.4211 | 11.753 | 2.6886 | 3.309
9.6 | 0.47427 | 0.98041 | 8.3333 | 11.753 | 2.7717 | 3.4113
9.7 | 0.47371 | 0.92641 | 8.2474 | 11.753 | 2.8558 | 3.5149
9.8 | 0.47304 | 0.86965 | 8.1633 | 11.753 | 2.925 | 3.6
9.9 | 0.45637 | 2.7009 | 8.0808 | 11.753 | 2.925 | 3.6
10 | 0.44281 | 3.3353 | 8 | 11.753 | 2.925 | 3.6
10.1 | 0.42979 | 3.8417 | 7.9208 | 11.753 | 2.925 | 3.6
10.2 | 0.41727 | 4.2745 | 7.8431 | 11.753 | 2.925 | 3.6
10.3 | 0.40524 | 4.6583 | 7.767 | 11.753 | 2.925 | 3.6
10.4 | 0.39366 | 5.0084 | 7.6923 | 11.753 | 2.925 | 3.6
10.5 | 0.38252 | 5.332 | 7.619 | 11.753 | 2.925 | 3.6
10.6 | 0.37179 | 5.6362 | 7.5472 | 11.753 | 2.925 | 3.6
10.7 | 0.36147 | 5.9245 | 7.4766 | 11.753 | 2.925 | 3.6
10.8 | 0.35152 | 6.1998 | 7.4074 | 11.753 | 2.925 | 3.6
10.9 | 0.34193 | 6.4642 | 7.3394 | 11.753 | 2.925 | 3.6
11 | 0.33269 | 6.7191 | 7.2727 | 11.753 | 2.925 | 3.6
11.1 | 0.32378 | 6.9658 | 7.2072 | 11.753 | 2.925 | 3.6
11.2 | 0.31519 | 7.2052 | 7.1429 | 11.753 | 2.925 | 3.6
11.3 | 0.30689 | 7.438 | 7.0796 | 11.753 | 2.925 | 3.6
11.4 | 0.29889 | 7.6648 | 7.0175 | 11.753 | 2.925 | 3.6
11.5 | 0.29116 | 7.8862 | 6.9565 | 11.753 | 2.925 | 3.6
11.6 | 0.28369 | 8.1026 | 6.8966 | 11.753 | 2.925 | 3.6
11.7 | 0.27648 | 8.3138 | 6.8376 | 11.753 | 2.925 | 3.6
11.8 | 0.26951 | 8.5207 | 6.7797 | 11.753 | 2.925 | 3.6
11.9 | 0.26277 | 8.7236 | 6.7227 | 11.753 | 2.925 | 3.6
12 | 0.25626 | 8.9226 | 6.6667 | 11.753 | 2.925 | 3.6
12.1 | 0.24996 | 9.118 | 6.6116 | 11.753 | 2.925 | 3.6
12.2 | 0.24386 | 9.3089 | 6.5574 | 11.753 | 2.925 | 3.6
12.3 | 0.23796 | 9.497 | 6.5041 | 11.753 | 2.925 | 3.6
12.4 | 0.23225 | 9.6819 | 6.4516 | 11.753 | 2.925 | 3.6
12.5 | 0.22672 | 9.8635 | 6.4 | 11.753 | 2.925 | 3.6
12.6 | 0.22136 | 10.0421 | 6.3492 | 11.753 | 2.925 | 3.6
12.7 | 0.21618 | 10.2177 | 6.2992 | 11.753 | 2.925 | 3.6
12.8 | 0.21115 | 10.3905 | 6.25 | 11.753 | 2.925 | 3.6
12.9 | 0.20628 | 10.5607 | 6.2016 | 11.753 | 2.925 | 3.6
13 | 0.20155 | 10.7282 | 6.1538 | 11.753 | 2.925 | 3.6
13.1 | 0.19697 | 10.9005 | 6.1069 | 11.753 | 2.925 | 3.6
13.2 | 0.19253 | 11.0705 | 6.0606 | 11.753 | 2.925 | 3.6
13.3 | 0.18822 | 11.2383 | 6.015 | 11.753 | 2.925 | 3.6
13.4 | 0.18404 | 11.404 | 5.9701 | 11.753 | 2.925 | 3.6
13.5 | 0.17998 | 11.5679 | 5.9259 | 11.753 | 2.925 | 3.6
13.6 | 0.17604 | 11.7299 | 5.8824 | 11.753 | 2.925 | 3.6
13.7 | 0.17221 | 11.8902 | 5.8394 | 11.753 | 2.925 | 3.6
13.8 | 0.16849 | 12.0489 | 5.7971 | 11.753 | 2.925 | 3.6
13.9 | 0.16488 | 12.2061 | 5.7554 | 11.753 | 2.925 | 3.6
14 | 0.16137 | 12.3619 | 5.7143 | 11.753 | 2.925 | 3.6
14.1 | 0.15797 | 12.5165 | 5.6738 | 11.753 | 2.925 | 3.6
14.2 | 0.15465 | 12.6699 | 5.6338 | 11.753 | 2.925 | 3.6
14.3 | 0.15143 | 12.8232 | 5.5944 | 11.753 | 2.925 | 3.6
14.4 | 0.1483 | 12.9746 | 5.5556 | 11.753 | 2.925 | 3.6
14.5 | 0.14525 | 13.1252 | 5.5172 | 11.753 | 2.925 | 3.6
14.6 | 0.14229 | 13.2752 | 5.4795 | 11.753 | 2.925 | 3.6
14.7 | 0.1394 | 13.4246 | 5.4422 | 11.753 | 2.925 | 3.6
14.8 | 0.13659 | 13.5735 | 5.4054 | 11.753 | 2.925 | 3.6
14.9 | 0.13386 | 13.7221 | 5.3691 | 11.753 | 2.925 | 3.6
15 | 0.1312 | 13.8703 | 5.3333 | 11.753 | 2.925 | 3.6
15.1 | 0.12861 | 14.0183 | 5.298 | 11.753 | 2.925 | 3.6
15.2 | 0.12609 | 14.1661 | 5.2632 | 11.753 | 2.925 | 3.6
15.3 | 0.12364 | 14.3137 | 5.2288 | 11.753 | 2.925 | 3.6
15.4 | 0.12124 | 14.4613 | 5.1948 | 11.753 | 2.925 | 3.6
15.5 | 0.11891 | 14.6089 | 5.1613 | 11.753 | 2.925 | 3.6
15.6 | 0.11664 | 14.7564 | 5.1282 | 11.753 | 2.925 | 3.6
15.7 | 0.11442 | 14.904 | 5.0955 | 11.753 | 2.925 | 3.6
15.8 | 0.11227 | 15.0515 | 5.0633 | 11.753 | 2.925 | 3.6
15.9 | 0.11016 | 15.1991 | 5.0314 | 11.753 | 2.925 | 3.6
16 | 0.10811 | 15.3467 | 5 | 11.753 | 2.925 | 3.6
16.1 | 0.10611 | 15.4944 | 4.9689 | 11.753 | 2.925 | 3.6
16.2 | 0.10415 | 15.6419 | 4.9383 | 11.753 | 2.925 | 3.6
16.3 | 0.10225 | 15.7883 | 4.908 | 11.753 | 2.925 | 3.6
16.4 | 0.10039 | 15.9366 | 4.878 | 11.753 | 2.925 | 3.6
16.5 | 0.098575 | 16.0837 | 4.8485 | 11.753 | 2.925 | 3.6
16.6 | 0.096805 | 16.2304 | 4.8193 | 11.753 | 2.925 | 3.6
16.7 | 0.095076 | 16.3767 | 4.7904 | 11.753 | 2.925 | 3.6
16.8 | 0.093388 | 16.5227 | 4.7619 | 11.753 | 2.925 | 3.6
16.9 | 0.09174 | 16.6681 | 4.7337 | 11.753 | 2.925 | 3.6
17 | 0.090131 | 16.8129 | 4.7059 | 11.753 | 2.925 | 3.6
17.1 | 0.088559 | 16.9571 | 4.6784 | 11.753 | 2.925 | 3.6
17.2 | 0.087023 | 17.1007 | 4.6512 | 11.753 | 2.925 | 3.6
17.3 | 0.085523 | 17.2435 | 4.6243 | 11.753 | 2.925 | 3.6
17.4 | 0.084057 | 17.3856 | 4.5977 | 11.753 | 2.925 | 3.6
17.5 | 0.082624 | 17.5269 | 4.5714 | 11.753 | 2.925 | 3.6
17.6 | 0.081224 | 17.6673 | 4.5455 | 11.753 | 2.925 | 3.6
17.7 | 0.079855 | 17.8069 | 4.5198 | 11.753 | 2.925 | 3.6
17.8 | 0.078516 | 17.9456 | 4.4944 | 11.753 | 2.925 | 3.6
17.9 | 0.077208 | 18.0834 | 4.4693 | 11.753 | 2.925 | 3.6
18 | 0.075928 | 18.2203 | 4.4444 | 11.753 | 2.925 | 3.6
18.1 | 0.074677 | 18.3562 | 4.4199 | 11.753 | 2.925 | 3.6
18.2 | 0.073452 | 18.4912 | 4.3956 | 11.753 | 2.925 | 3.6
18.3 | 0.072255 | 18.6253 | 4.3716 | 11.753 | 2.925 | 3.6
18.4 | 0.071083 | 18.7585 | 4.3478 | 11.753 | 2.925 | 3.6
18.5 | 0.069937 | 18.8907 | 4.3243 | 11.753 | 2.925 | 3.6
18.6 | 0.068815 | 19.0221 | 4.3011 | 11.753 | 2.925 | 3.6
18.7 | 0.067717 | 19.1525 | 4.2781 | 11.753 | 2.925 | 3.6
18.8 | 0.066642 | 19.2841 | 4.2553 | 11.753 | 2.925 | 3.6
18.9 | 0.06559 | 19.4124 | 4.2328 | 11.753 | 2.925 | 3.6
19 | 0.064559 | 19.54 | 4.2105 | 11.753 | 2.925 | 3.6
19.1 | 0.063551 | 19.6668 | 4.1885 | 11.753 | 2.925 | 3.6
19.2 | 0.062563 | 19.793 | 4.1667 | 11.753 | 2.925 | 3.6
19.3 | 0.061595 | 19.9185 | 4.1451 | 11.753 | 2.925 | 3.6
19.4 | 0.060648 | 20.0434 | 4.1237 | 11.753 | 2.925 | 3.6
19.5 | 0.059719 | 20.1678 | 4.1026 | 11.753 | 2.925 | 3.6
19.6 | 0.05881 | 20.2915 | 4.0816 | 11.753 | 2.925 | 3.6
19.7 | 0.057919 | 20.4148 | 4.0609 | 11.753 | 2.925 | 3.6
19.8 | 0.057046 | 20.5374 | 4.0404 | 11.753 | 2.925 | 3.6
19.9 | 0.05619 | 20.6594 | 4.0201 | 11.753 | 2.925 | 3.6
20 | 0.055352 | 20.7808 | 4 | 11.753 | 2.925 | 3.6
20.1 | 0.05453 | 20.9018 | 3.9801 | 11.753 | 2.925 | 3.6
20.2 | 0.053724 | 21.0222 | 3.9604 | 11.753 | 2.925 | 3.6
20.3 | 0.052934 | 21.1421 | 3.9409 | 11.753 | 2.925 | 3.6
20.4 | 0.052159 | 21.2615 | 3.9216 | 11.753 | 2.925 | 3.6
20.5 | 0.051399 | 21.3804 | 3.9024 | 11.753 | 2.925 | 3.6
20.6 | 0.050655 | 21.499 | 3.8835 | 11.753 | 2.925 | 3.6
20.7 | 0.049924 | 21.617 | 3.8647 | 11.753 | 2.925 | 3.6
20.8 | 0.049207 | 21.7347 | 3.8462 | 11.753 | 2.925 | 3.6
20.9 | 0.048504 | 21.852 | 3.8278 | 11.753 | 2.925 | 3.6
21 | 0.047815 | 21.9689 | 3.8095 | 11.753 | 2.925 | 3.6
21.1 | 0.047138 | 22.0854 | 3.7915 | 11.753 | 2.925 | 3.6
21.2 | 0.046474 | 22.2016 | 3.7736 | 11.753 | 2.925 | 3.6
21.3 | 0.045823 | 22.316 | 3.7559 | 11.753 | 2.925 | 3.6
21.4 | 0.045183 | 22.4349 | 3.7383 | 11.753 | 2.925 | 3.6
21.5 | 0.044556 | 22.5484 | 3.7209 | 11.753 | 2.925 | 3.6
21.6 | 0.04394 | 22.6634 | 3.7037 | 11.753 | 2.925 | 3.6
21.7 | 0.043335 | 22.7781 | 3.6866 | 11.753 | 2.925 | 3.6
21.8 | 0.042742 | 22.8926 | 3.6697 | 11.753 | 2.925 | 3.6
21.9 | 0.042159 | 23.0069 | 3.653 | 11.753 | 2.925 | 3.6
22 | 0.041586 | 23.1209 | 3.6364 | 11.753 | 2.925 | 3.6
22.1 | 0.041024 | 23.2347 | 3.6199 | 11.753 | 2.925 | 3.6
22.2 | 0.040473 | 23.3483 | 3.6036 | 11.753 | 2.925 | 3.6
22.3 | 0.039931 | 23.4618 | 3.5874 | 11.753 | 2.925 | 3.6
22.4 | 0.039398 | 23.575 | 3.5714 | 11.753 | 2.925 | 3.6
22.5 | 0.038875 | 23.688 | 3.5556 | 11.753 | 2.925 | 3.6
22.6 | 0.038361 | 23.8009 | 3.5398 | 11.753 | 2.925 | 3.6
22.7 | 0.037857 | 23.9136 | 3.5242 | 11.753 | 2.925 | 3.6
22.8 | 0.037361 | 24.0262 | 3.5088 | 11.753 | 2.925 | 3.6
22.9 | 0.036873 | 24.1386 | 3.4934 | 11.753 | 2.925 | 3.6
23 | 0.036395 | 24.2509 | 3.4783 | 11.753 | 2.925 | 3.6
23.1 | 0.035924 | 24.363 | 3.4632 | 11.753 | 2.925 | 3.6
23.2 | 0.035461 | 24.4749 | 3.4483 | 11.753 | 2.925 | 3.6
23.3 | 0.035007 | 24.5868 | 3.4335 | 11.753 | 2.925 | 3.6
23.4 | 0.03456 | 24.6984 | 3.4188 | 11.753 | 2.925 | 3.6
23.5 | 0.034121 | 24.81 | 3.4043 | 11.753 | 2.925 | 3.6
23.6 | 0.033689 | 24.9214 | 3.3898 | 11.753 | 2.925 | 3.6
23.7 | 0.033264 | 25.0326 | 3.3755 | 11.753 | 2.925 | 3.6
23.8 | 0.032846 | 25.1437 | 3.3613 | 11.753 | 2.925 | 3.6
23.9 | 0.032436 | 25.2546 | 3.3473 | 11.753 | 2.925 | 3.6
24 | 0.032032 | 25.3654 | 3.3333 | 11.753 | 2.925 | 3.6
24.1 | 0.031635 | 25.476 | 3.3195 | 11.753 | 2.925 | 3.6
24.2 | 0.031245 | 25.593 | 3.3058 | 11.753 | 2.925 | 3.6
24.3 | 0.03086 | 25.702 | 3.2922 | 11.753 | 2.925 | 3.6
24.4 | 0.030482 | 25.8108 | 3.2787 | 11.753 | 2.925 | 3.6
24.5 | 0.030111 | 25.9196 | 3.2653 | 11.753 | 2.925 | 3.6
24.6 | 0.029745 | 26.0282 | 3.252 | 11.753 | 2.925 | 3.6
24.7 | 0.029385 | 26.1368 | 3.2389 | 11.753 | 2.925 | 3.6
24.8 | 0.029031 | 26.2454 | 3.2258 | 11.753 | 2.925 | 3.6
24.9 | 0.028683 | 26.3539 | 3.2129 | 11.753 | 2.925 | 3.6
25 | 0.02834 | 26.4623 | 3.2 | 11.753 | 2.925 | 3.6

## Cp-Ct-Cf-TSR Curves
Wind speed 1 m/s
Power Coefficient [-] | [20 empty] | Torque Coefficient [-] | [20 empty] | Thrust Coefficient [-]
TSR\Pitch [deg] | -4 | -3.6 | -3.2 | -2.8 | -2.4 | -2 | -1.6 | -1.2 | -0.8 | -0.4 | 0 | 1 | 2 | 3 | 4 | 5 | 10 | 20 | 30 | 50 | TSR\Pitch [deg] | -4 | -3.6 | -3.2 | -2.8 | -2.4 | -2 | -1.6 | -1.2 | -0.8 | -0.4 | 0 | 1 | 2 | 3 | 4 | 5 | 10 | 20 | 30 | 50 | TSR\Pitch [deg] | -4 | -3.6 | -3.2 | -2.8 | -2.4 | -2 | -1.6 | -1.2 | -0.8 | -0.4 | 0 | 1 | 2 | 3 | 4 | 5 | 10 | 20 | 30 | 50
3 | 0.026322 | 0.028397 | 0.030467 | 0.032533 | 0.034596 | 0.036658 | 0.038719 | 0.040779 | 0.042837 | 0.044897 | 0.046958 | 0.052041 | 0.057257 | 0.062618 | 0.067841 | 0.073254 | 0.099274 | 0.093222 | 0.0074175 | -0.13488 | 3 | 0.008774 | 0.0094655 | 0.010156 | 0.010844 | 0.011532 | 0.012219 | 0.012906 | 0.013593 | 0.014279 | 0.014966 | 0.015653 | 0.017347 | 0.019086 | 0.020873 | 0.022614 | 0.024418 | 0.033091 | 0.031074 | 0.0024725 | -0.044959 | 3 | 8.1593 | 8.1593 | 8.1592 | 8.1592 | 8.1592 | 8.1592 | 8.1592 | 8.1593 | 8.1593 | 8.1594 | 8.1595 | 8.1598 | 8.1603 | 8.1612 | 8.1619 | 8.163 | 8.1667 | 8.1338 | 8.04 | 7.96
4 | 0.064304 | 0.068454 | 0.072631 | 0.076964 | 0.081357 | 0.085685 | 0.089945 | 0.094103 | 0.098177 | 0.10236 | 0.10671 | 0.1187 | 0.13186 | 0.1433 | 0.15245 | 0.16025 | 0.18183 | 0.076574 | -0.10111 | -0.29646 | 4 | 0.016076 | 0.017114 | 0.018158 | 0.019241 | 0.020339 | 0.021421 | 0.022486 | 0.023526 | 0.024544 | 0.025589 | 0.026677 | 0.029675 | 0.032964 | 0.035825 | 0.038112 | 0.040064 | 0.045457 | 0.019143 | -0.025278 | -0.074115 | 4 | 8.2384 | 8.2388 | 8.2393 | 8.24 | 8.2409 | 8.2416 | 8.2424 | 8.2431 | 8.2438 | 8.2446 | 8.2457 | 8.2492 | 8.2531 | 8.2551 | 8.2558 | 8.2558 | 8.2482 | 8.114 | 7.9505 | 7.9246
5 | 0.12213 | 0.1293 | 0.13665 | 0.14413 | 0.15242 | 0.16133 | 0.17044 | 0.17966 | 0.18858 | 0.1967 | 0.20419 | 0.22092 | 0.23561 | 0.2502 | 0.26309 | 0.27203 | 0.23388 | 0.0089075 | -0.2698 | -0.57547 | 5 | 0.024426 | 0.025861 | 0.027329 | 0.028826 | 0.030483 | 0.032266 | 0.034087 | 0.035932 | 0.037716 | 0.039341 | 0.040839 | 0.044184 | 0.047122 | 0.050041 | 0.052619 | 0.054406 | 0.046776 | 0.0017815 | -0.053961 | -0.11509 | 5 | 8.3484 | 8.3498 | 8.3516 | 8.3536 | 8.356 | 8.3588 | 8.3614 | 8.3641 | 8.3662 | 8.3677 | 8.3688 | 8.3709 | 8.3723 | 8.3761 | 8.3793 | 8.3787 | 8.3033 | 8.0462 | 7.8442 | 7.877
6 | 0.20375 | 0.21846 | 0.23261 | 0.24597 | 0.25864 | 0.27067 | 0.28236 | 0.29419 | 0.30833 | 0.32093 | 0.33115 | 0.35348 | 0.36864 | 0.37254 | 0.36634 | 0.35359 | 0.24447 | -0.10688 | -0.50592 | -1.0003 | 6 | 0.033958 | 0.03641 | 0.038768 | 0.040995 | 0.043106 | 0.045112 | 0.047059 | 0.049032 | 0.051388 | 0.053489 | 0.055191 | 0.058913 | 0.061441 | 0.06209 | 0.061056 | 0.058932 | 0.040745 | -0.017813 | -0.08432 | -0.16671 | 6 | 8.4956 | 8.4997 | 8.503 | 8.5058 | 8.5082 | 8.5105 | 8.5128 | 8.5157 | 8.5216 | 8.5275 | 8.5315 | 8.5382 | 8.5381 | 8.5272 | 8.5066 | 8.4808 | 8.3193 | 7.9391 | 7.7281 | 7.8193
7 | 0.32242 | 0.34436 | 0.36102 | 0.37486 | 0.38763 | 0.40327 | 0.42035 | 0.42896 | 0.4351 | 0.43952 | 0.44343 | 0.44594 | 0.43922 | 0.42701 | 0.40957 | 0.38797 | 0.23422 | -0.27208 | -0.81908 | -1.6006 | 7 | 0.04606 | 0.049194 | 0.051574 | 0.053552 | 0.055376 | 0.057609 | 0.06005 | 0.06128 | 0.062157 | 0.062789 | 0.063347 | 0.063706 | 0.062745 | 0.061001 | 0.058509 | 0.055424 | 0.03346 | -0.038868 | -0.11701 | -0.22866 | 7 | 8.6987 | 8.7089 | 8.7134 | 8.716 | 8.718 | 8.7238 | 8.7308 | 8.7291 | 8.7254 | 8.7197 | 8.7132 | 8.6892 | 8.6575 | 8.6218 | 8.5823 | 8.5403 | 8.3117 | 7.8062 | 7.603 | 7.7514
7.5 | 0.37546 | 0.395 | 0.41268 | 0.42636 | 0.43441 | 0.44088 | 0.44695 | 0.45356 | 0.45837 | 0.46193 | 0.46395 | 0.46313 | 0.45568 | 0.44211 | 0.42307 | 0.39948 | 0.22303 | -0.37358 | -1.0071 | -1.9758 | 7.5 | 0.050061 | 0.052667 | 0.055025 | 0.056848 | 0.057922 | 0.058784 | 0.059594 | 0.060475 | 0.061116 | 0.061591 | 0.06186 | 0.061751 | 0.060757 | 0.058948 | 0.05641 | 0.053263 | 0.029737 | -0.049811 | -0.13429 | -0.26344 | 7.5 | 8.8212 | 8.8293 | 8.8348 | 8.835 | 8.8293 | 8.8229 | 8.8153 | 8.8079 | 8.7977 | 8.7866 | 8.7749 | 8.7405 | 8.7011 | 8.6582 | 8.6121 | 8.564 | 8.3015 | 7.7339 | 7.5379 | 7.7134
8 | 0.40902 | 0.41849 | 0.42645 | 0.43436 | 0.44311 | 0.45112 | 0.45733 | 0.46135 | 0.46453 | 0.46738 | 0.46992 | 0.47174 | 0.46621 | 0.45306 | 0.4331 | 0.40743 | 0.20776 | -0.48817 | -1.2166 | -2.4057 | 8 | 0.051128 | 0.052311 | 0.053307 | 0.054295 | 0.055388 | 0.05639 | 0.057166 | 0.057669 | 0.058067 | 0.058422 | 0.058741 | 0.058967 | 0.058277 | 0.056632 | 0.054138 | 0.050928 | 0.02597 | -0.061021 | -0.15208 | -0.30072 | 8 | 8.9431 | 8.935 | 8.9259 | 8.9168 | 8.9077 | 8.8973 | 8.8846 | 8.8702 | 8.8552 | 8.8402 | 8.8254 | 8.7845 | 8.7396 | 8.6905 | 8.6382 | 8.5836 | 8.2874 | 7.6589 | 7.472 | 7.6728
8.5 | 0.40379 | 0.4152 | 0.42608 | 0.43464 | 0.4412 | 0.44707 | 0.45239 | 0.45735 | 0.46168 | 0.46586 | 0.4692 | 0.47434 | 0.47165 | 0.46004 | 0.43982 | 0.41254 | 0.18881 | -0.61686 | -1.4486 | -2.8943 | 8.5 | 0.047504 | 0.048847 | 0.050127 | 0.051134 | 0.051905 | 0.052597 | 0.053222 | 0.053806 | 0.054315 | 0.054808 | 0.0552 | 0.055805 | 0.055488 | 0.054122 | 0.051744 | 0.048534 | 0.022213 | -0.072572 | -0.17043 | -0.34051 | 8.5 | 9.0283 | 9.0182 | 9.0063 | 8.9917 | 8.9759 | 8.9591 | 8.9418 | 8.9244 | 8.9063 | 8.8888 | 8.8706 | 8.8241 | 8.7737 | 8.7193 | 8.6612 | 8.6005 | 8.2701 | 7.5815 | 7.4053 | 7.6296
9 | 0.39328 | 0.4032 | 0.41232 | 0.42088 | 0.42871 | 0.43626 | 0.44293 | 0.44896 | 0.45436 | 0.45915 | 0.46367 | 0.4714 | 0.4722 | 0.46318 | 0.44393 | 0.41534 | 0.16599 | -0.76089 | -1.7039 | -3.4451 | 9 | 0.043698 | 0.044801 | 0.045813 | 0.046765 | 0.047634 | 0.048473 | 0.049214 | 0.049884 | 0.050485 | 0.051017 | 0.051519 | 0.052378 | 0.052467 | 0.051464 | 0.049325 | 0.046149 | 0.018443 | -0.084543 | -0.18933 | -0.38279 | 9 | 9.1102 | 9.0927 | 9.0742 | 9.0552 | 9.0354 | 9.016 | 8.9956 | 8.9748 | 8.9538 | 8.9327 | 8.912 | 8.8592 | 8.8041 | 8.7451 | 8.6821 | 8.6153 | 8.2494 | 7.5015 | 7.3383 | 7.5838
9.5 | 0.36871 | 0.38061 | 0.39176 | 0.40235 | 0.41192 | 0.42075 | 0.42889 | 0.43631 | 0.44301 | 0.44909 | 0.45437 | 0.46463 | 0.46917 | 0.46326 | 0.44533 | 0.41597 | 0.13926 | -0.92174 | -1.9848 | -4.0616 | 9.5 | 0.038812 | 0.040065 | 0.041238 | 0.042352 | 0.04336 | 0.044289 | 0.045147 | 0.045928 | 0.046632 | 0.047273 | 0.047829 | 0.048908 | 0.049386 | 0.048765 | 0.046877 | 0.043787 | 0.014659 | -0.097025 | -0.20892 | -0.42754 | 9.5 | 9.1805 | 9.1592 | 9.1374 | 9.1154 | 9.0926 | 9.0692 | 9.0457 | 9.0221 | 8.9984 | 8.9747 | 8.9509 | 8.8919 | 8.8324 | 8.7691 | 8.7009 | 8.6284 | 8.2257 | 7.4188 | 7.27 | 7.5354
10 | 0.33866 | 0.35266 | 0.36605 | 0.37837 | 0.39012 | 0.40082 | 0.41072 | 0.41978 | 0.42805 | 0.43549 | 0.44231 | 0.4551 | 0.46259 | 0.46027 | 0.44429 | 0.41441 | 0.10849 | -1.1009 | -2.2942 | -4.7474 | 10 | 0.033866 | 0.035266 | 0.036605 | 0.037837 | 0.039012 | 0.040082 | 0.041072 | 0.041978 | 0.042805 | 0.043549 | 0.044231 | 0.04551 | 0.046259 | 0.046027 | 0.044429 | 0.041441 | 0.010849 | -0.11009 | -0.22942 | -0.47474 | 10 | 9.2485 | 9.2236 | 9.1985 | 9.1726 | 9.1468 | 9.1206 | 9.0943 | 9.0678 | 9.0414 | 9.015 | 8.989 | 8.9235 | 8.8586 | 8.791 | 8.7181 | 8.6398 | 8.199 | 7.333 | 7.1995 | 7.4845
10.5 | 0.30319 | 0.31975 | 0.33559 | 0.35033 | 0.36416 | 0.37703 | 0.38897 | 0.39996 | 0.40998 | 0.41901 | 0.42719 | 0.44338 | 0.45349 | 0.45456 | 0.44075 | 0.41055 | 0.073499 | -1.2992 | -2.6348 | -5.5061 | 10.5 | 0.028875 | 0.030452 | 0.031961 | 0.033365 | 0.034682 | 0.035908 | 0.037045 | 0.038091 | 0.039046 | 0.039906 | 0.040685 | 0.042226 | 0.043189 | 0.043292 | 0.041977 | 0.0391 | 0.0069999 | -0.12373 | -0.25093 | -0.52439 | 10.5 | 9.3154 | 9.287 | 9.2586 | 9.2297 | 9.2007 | 9.1714 | 9.1422 | 9.1131 | 9.084 | 9.0549 | 9.026 | 8.9545 | 8.8837 | 8.8115 | 8.7337 | 8.6496 | 8.1693 | 7.2441 | 7.1262 | 7.4309
11 | 0.26182 | 0.28126 | 0.29992 | 0.31758 | 0.33399 | 0.34934 | 0.3636 | 0.37686 | 0.38886 | 0.39975 | 0.40953 | 0.42934 | 0.4422 | 0.44609 | 0.43479 | 0.40448 | 0.034354 | -1.5175 | -3.0085 | -6.3411 | 11 | 0.023802 | 0.025569 | 0.027265 | 0.028871 | 0.030363 | 0.031758 | 0.033054 | 0.03426 | 0.035351 | 0.03634 | 0.03723 | 0.039031 | 0.0402 | 0.040554 | 0.039526 | 0.036771 | 0.0031231 | -0.13796 | -0.2735 | -0.57646 | 11 | 9.3807 | 9.3493 | 9.3178 | 9.2861 | 9.254 | 9.222 | 9.19 | 9.1581 | 9.1262 | 9.0945 | 9.0628 | 8.9848 | 8.9077 | 8.8302 | 8.7477 | 8.6578 | 8.137 | 7.1519 | 7.0498 | 7.3748
11.5 | 0.21626 | 0.23853 | 0.25998 | 0.28057 | 0.29983 | 0.31787 | 0.33467 | 0.35021 | 0.36458 | 0.37756 | 0.38924 | 0.41305 | 0.429 | 0.43563 | 0.42625 | 0.39633 | -0.0093282 | -1.7568 | -3.4168 | -7.2559 | 11.5 | 0.018806 | 0.020742 | 0.022607 | 0.024397 | 0.026072 | 0.027641 | 0.029102 | 0.030453 | 0.031703 | 0.032831 | 0.033847 | 0.035918 | 0.037305 | 0.03788 | 0.037065 | 0.034464 | -0.00081114 | -0.15277 | -0.29712 | -0.63095 | 11.5 | 9.4458 | 9.4118 | 9.3771 | 9.3425 | 9.3075 | 9.2726 | 9.2376 | 9.2028 | 9.1683 | 9.1338 | 9.0994 | 9.0145 | 8.9312 | 8.8481 | 8.7603 | 8.6646 | 8.1017 | 7.0561 | 6.9702 | 7.3161
12 | 0.21374 | 0.19245 | 0.21609 | 0.2393 | 0.26152 | 0.28262 | 0.3022 | 0.3204 | 0.33713 | 0.35241 | 0.36626 | 0.39472 | 0.41381 | 0.42282 | 0.41547 | 0.38598 | -0.057572 | -2.0185 | -3.8617 | -8.2541 | 12 | 0.017812 | 0.016037 | 0.018008 | 0.019941 | 0.021793 | 0.023552 | 0.025184 | 0.0267 | 0.028094 | 0.029367 | 0.030521 | 0.032893 | 0.034484 | 0.035235 | 0.034623 | 0.032165 | -0.0047977 | -0.16821 | -0.32181 | -0.68784 | 12 | 9.5277 | 9.4723 | 9.436 | 9.3987 | 9.3609 | 9.3232 | 9.2854 | 9.2477 | 9.2102 | 9.1728 | 9.1357 | 9.0441 | 8.9539 | 8.8647 | 8.7715 | 8.67 | 8.0637 | 6.9556 | 6.8873 | 7.2549
Wind speed 7 m/s
Power Coefficient [-] | [20 empty] | Torque Coefficient [-] | [20 empty] | Thrust Coefficient [-]
TSR\Pitch [deg] | -4 | -3.6 | -3.2 | -2.8 | -2.4 | -2 | -1.6 | -1.2 | -0.8 | -0.4 | 0 | 1 | 2 | 3 | 4 | 5 | 10 | 20 | 30 | 50 | TSR\Pitch [deg] | -4 | -3.6 | -3.2 | -2.8 | -2.4 | -2 | -1.6 | -1.2 | -0.8 | -0.4 | 0 | 1 | 2 | 3 | 4 | 5 | 10 | 20 | 30 | 50 | TSR\Pitch [deg] | -4 | -3.6 | -3.2 | -2.8 | -2.4 | -2 | -1.6 | -1.2 | -0.8 | -0.4 | 0 | 1 | 2 | 3 | 4 | 5 | 10 | 20 | 30 | 50
3 | 0.026684 | 0.028749 | 0.03081 | 0.032867 | 0.03492 | 0.036971 | 0.039021 | 0.041069 | 0.043115 | 0.045162 | 0.047211 | 0.052277 | 0.057439 | 0.062784 | 0.067995 | 0.07333 | 0.099629 | 0.09336 | 0.0066345 | -0.13423 | 3 | 0.0088946 | 0.0095831 | 0.01027 | 0.010956 | 0.01164 | 0.012324 | 0.013007 | 0.01369 | 0.014372 | 0.015054 | 0.015737 | 0.017426 | 0.019146 | 0.020928 | 0.022665 | 0.024443 | 0.03321 | 0.03112 | 0.0022115 | -0.044743 | 3 | 0.3028 | 0.30272 | 0.30264 | 0.30258 | 0.30254 | 0.30251 | 0.30251 | 0.30251 | 0.30253 | 0.30257 | 0.30262 | 0.30278 | 0.30321 | 0.30394 | 0.30459 | 0.30554 | 0.30902 | 0.27438 | 0.1785 | 0.096737
4 | 0.064744 | 0.068869 | 0.072968 | 0.077226 | 0.08157 | 0.085884 | 0.090128 | 0.094279 | 0.098343 | 0.10244 | 0.10671 | 0.11819 | 0.13113 | 0.14334 | 0.15288 | 0.16094 | 0.18328 | 0.074619 | -0.10197 | -0.29446 | 4 | 0.016186 | 0.017217 | 0.018242 | 0.019306 | 0.020393 | 0.021471 | 0.022532 | 0.02357 | 0.024586 | 0.025609 | 0.026677 | 0.029546 | 0.032783 | 0.035834 | 0.03822 | 0.040236 | 0.045819 | 0.018655 | -0.025492 | -0.073616 | 4 | 0.38246 | 0.38285 | 0.38325 | 0.38388 | 0.38467 | 0.38544 | 0.38617 | 0.38685 | 0.38748 | 0.38819 | 0.38917 | 0.39234 | 0.39613 | 0.39874 | 0.39959 | 0.39963 | 0.39159 | 0.25226 | 0.089273 | 0.061291
5 | 0.12212 | 0.12918 | 0.13635 | 0.14358 | 0.15115 | 0.15961 | 0.16849 | 0.1775 | 0.18671 | 0.19547 | 0.20367 | 0.22129 | 0.237 | 0.25232 | 0.26562 | 0.27501 | 0.23454 | 0.0019644 | -0.26894 | -0.5705 | 5 | 0.024424 | 0.025836 | 0.02727 | 0.028717 | 0.03023 | 0.031923 | 0.033698 | 0.0355 | 0.037341 | 0.039094 | 0.040735 | 0.044258 | 0.047401 | 0.050464 | 0.053124 | 0.055002 | 0.046908 | 0.00039289 | -0.053788 | -0.1141 | 5 | 0.49336 | 0.49464 | 0.4962 | 0.49801 | 0.50008 | 0.5026 | 0.5053 | 0.50792 | 0.51064 | 0.51257 | 0.51406 | 0.51653 | 0.51855 | 0.52252 | 0.52578 | 0.52528 | 0.44567 | 0.17974 | -0.016131 | 0.013577
6 | 0.19943 | 0.21382 | 0.22853 | 0.24288 | 0.2566 | 0.26942 | 0.28157 | 0.29393 | 0.30859 | 0.3228 | 0.33372 | 0.3574 | 0.37339 | 0.37733 | 0.37071 | 0.35716 | 0.24186 | -0.12348 | -0.4995 | -0.98916 | 6 | 0.033238 | 0.035636 | 0.038088 | 0.04048 | 0.042766 | 0.044903 | 0.046928 | 0.048988 | 0.051432 | 0.053801 | 0.05562 | 0.059567 | 0.062232 | 0.062889 | 0.061785 | 0.059526 | 0.04031 | -0.02058 | -0.08325 | -0.16486 | 6 | 0.64034 | 0.64472 | 0.64919 | 0.65261 | 0.65558 | 0.65829 | 0.66083 | 0.6641 | 0.67026 | 0.67723 | 0.68152 | 0.68899 | 0.6891 | 0.67746 | 0.65567 | 0.62811 | 0.45762 | 0.066295 | -0.13119 | -0.044261
7 | 0.31837 | 0.34093 | 0.35897 | 0.37447 | 0.38841 | 0.40709 | 0.42329 | 0.43274 | 0.43942 | 0.44429 | 0.44855 | 0.45185 | 0.44475 | 0.43197 | 0.41341 | 0.39032 | 0.22548 | -0.29845 | -0.80138 | -1.5781 | 7 | 0.045481 | 0.048704 | 0.051282 | 0.053496 | 0.055487 | 0.058156 | 0.06047 | 0.06182 | 0.062774 | 0.06347 | 0.064079 | 0.06455 | 0.063536 | 0.06171 | 0.059058 | 0.055761 | 0.032211 | -0.042635 | -0.11448 | -0.22544 | 7 | 0.84888 | 0.8598 | 0.86584 | 0.86942 | 0.87197 | 0.88082 | 0.88639 | 0.88483 | 0.88109 | 0.8755 | 0.86887 | 0.84414 | 0.81034 | 0.77241 | 0.73032 | 0.68557 | 0.44263 | -0.067574 | -0.25568 | -0.11233
7.5 | 0.37385 | 0.39361 | 0.41358 | 0.42808 | 0.43722 | 0.44438 | 0.45095 | 0.45797 | 0.46324 | 0.4673 | 0.46925 | 0.46877 | 0.46114 | 0.44667 | 0.42616 | 0.40043 | 0.20943 | -0.40465 | -0.98181 | -1.9448 | 7.5 | 0.049846 | 0.052482 | 0.055144 | 0.057077 | 0.058296 | 0.05925 | 0.060127 | 0.061063 | 0.061765 | 0.062306 | 0.062567 | 0.062503 | 0.061485 | 0.059556 | 0.056821 | 0.053391 | 0.027924 | -0.053953 | -0.13091 | -0.2593 | 7.5 | 0.97805 | 0.98532 | 0.99321 | 0.99346 | 0.98804 | 0.98141 | 0.97392 | 0.9663 | 0.95572 | 0.94421 | 0.93146 | 0.89538 | 0.85358 | 0.80777 | 0.75852 | 0.70684 | 0.42679 | -0.13911 | -0.32167 | -0.15033
8 | 0.40874 | 0.4193 | 0.42825 | 0.4371 | 0.44647 | 0.45498 | 0.46189 | 0.46619 | 0.46967 | 0.47275 | 0.47529 | 0.47741 | 0.47146 | 0.45709 | 0.43517 | 0.40695 | 0.18775 | -0.52466 | -1.1816 | -2.3638 | 8 | 0.051092 | 0.052412 | 0.053531 | 0.054638 | 0.055809 | 0.056873 | 0.057737 | 0.058273 | 0.058709 | 0.059094 | 0.059411 | 0.059676 | 0.058932 | 0.057136 | 0.054396 | 0.050869 | 0.023469 | -0.065582 | -0.1477 | -0.29547 | 8 | 1.1045 | 1.0964 | 1.0874 | 1.0784 | 1.0691 | 1.0583 | 1.0452 | 1.03 | 1.0141 | 0.99825 | 0.98214 | 0.93895 | 0.89096 | 0.83845 | 0.78225 | 0.72359 | 0.40535 | -0.21347 | -0.3894 | -0.19096
8.5 | 0.40384 | 0.41646 | 0.42816 | 0.43752 | 0.44478 | 0.45126 | 0.45709 | 0.46243 | 0.46708 | 0.47141 | 0.47506 | 0.4803 | 0.47683 | 0.46353 | 0.44071 | 0.41002 | 0.16056 | -0.6596 | -1.4007 | -2.8384 | 8.5 | 0.047511 | 0.048996 | 0.050372 | 0.051472 | 0.052328 | 0.053089 | 0.053775 | 0.054404 | 0.05495 | 0.05546 | 0.05589 | 0.056506 | 0.056098 | 0.054533 | 0.051849 | 0.048238 | 0.01889 | -0.0776 | -0.16479 | -0.33392 | 8.5 | 1.1928 | 1.1828 | 1.1703 | 1.1552 | 1.1387 | 1.121 | 1.1027 | 1.0843 | 1.0652 | 1.0461 | 1.027 | 0.97743 | 0.92336 | 0.8648 | 0.80197 | 0.73624 | 0.37881 | -0.29062 | -0.45837 | -0.23422
9 | 0.39305 | 0.40444 | 0.41452 | 0.424 | 0.43257 | 0.44076 | 0.44794 | 0.45445 | 0.46026 | 0.46538 | 0.47014 | 0.47793 | 0.47767 | 0.46633 | 0.44351 | 0.41041 | 0.1272 | -0.81089 | -1.6395 | -3.3716 | 9 | 0.043673 | 0.044937 | 0.046058 | 0.047111 | 0.048063 | 0.048973 | 0.049772 | 0.050495 | 0.05114 | 0.051709 | 0.052238 | 0.053103 | 0.053074 | 0.051814 | 0.049279 | 0.045602 | 0.014133 | -0.090098 | -0.18217 | -0.37462 | 9 | 1.2763 | 1.2585 | 1.2391 | 1.2191 | 1.1983 | 1.1777 | 1.1561 | 1.134 | 1.1116 | 1.0892 | 1.0671 | 1.0106 | 0.95125 | 0.88734 | 0.81863 | 0.74579 | 0.3468 | -0.37056 | -0.52835 | -0.28005
9.5 | 0.3689 | 0.382 | 0.39421 | 0.40584 | 0.41618 | 0.42573 | 0.43451 | 0.4425 | 0.44964 | 0.45609 | 0.46163 | 0.47205 | 0.4754 | 0.46642 | 0.44355 | 0.40818 | 0.08717 | -0.97986 | -1.8993 | -3.9665 | 9.5 | 0.038831 | 0.040211 | 0.041496 | 0.04272 | 0.043808 | 0.044814 | 0.045738 | 0.046579 | 0.04733 | 0.048009 | 0.048592 | 0.049689 | 0.050042 | 0.049097 | 0.04669 | 0.042966 | 0.0091758 | -0.10314 | -0.19993 | -0.41753 | 9.5 | 1.3471 | 1.3248 | 1.3019 | 1.2787 | 1.2544 | 1.2296 | 1.2047 | 1.1796 | 1.1544 | 1.1291 | 1.1037 | 1.0406 | 0.97637 | 0.90724 | 0.8322 | 0.75229 | 0.30926 | -0.45341 | -0.60006 | -0.3284
10 | 0.33916 | 0.35446 | 0.3691 | 0.38246 | 0.39513 | 0.4067 | 0.41732 | 0.42701 | 0.43579 | 0.44364 | 0.4507 | 0.46366 | 0.47002 | 0.4638 | 0.44139 | 0.40301 | 0.039975 | -1.1678 | -2.1816 | -4.6259 | 10 | 0.033916 | 0.035446 | 0.03691 | 0.038246 | 0.039513 | 0.04067 | 0.041732 | 0.042701 | 0.043579 | 0.044364 | 0.04507 | 0.046366 | 0.047002 | 0.04638 | 0.044139 | 0.040301 | 0.0039975 | -0.11678 | -0.21816 | -0.46259 | 10 | 1.4141 | 1.388 | 1.3614 | 1.3341 | 1.3067 | 1.2789 | 1.2508 | 1.2226 | 1.1944 | 1.1663 | 1.1384 | 1.0683 | 0.9984 | 0.92412 | 0.84307 | 0.75549 | 0.26599 | -0.53957 | -0.67429 | -0.37929
10.5 | 0.30442 | 0.3225 | 0.33963 | 0.35557 | 0.37048 | 0.38433 | 0.39711 | 0.4088 | 0.41935 | 0.42879 | 0.43722 | 0.45346 | 0.46251 | 0.45899 | 0.43653 | 0.39518 | -0.015356 | -1.3752 | -2.4881 | -5.3527 | 10.5 | 0.028992 | 0.030714 | 0.032346 | 0.033864 | 0.035284 | 0.036602 | 0.03782 | 0.038933 | 0.039938 | 0.040837 | 0.04164 | 0.043186 | 0.044049 | 0.043713 | 0.041574 | 0.037637 | -0.0014625 | -0.13098 | -0.23696 | -0.50978 | 10.5 | 1.4786 | 1.4487 | 1.4188 | 1.3882 | 1.3573 | 1.3263 | 1.2953 | 1.2642 | 1.233 | 1.2019 | 1.171 | 1.0942 | 1.018 | 0.93846 | 0.85082 | 0.7555 | 0.21659 | -0.62859 | -0.75171 | -0.43268
11 | 0.2645 | 0.28553 | 0.30568 | 0.32471 | 0.34236 | 0.35881 | 0.37398 | 0.38799 | 0.40057 | 0.41185 | 0.42185 | 0.44155 | 0.45312 | 0.45192 | 0.42943 | 0.38461 | -0.079456 | -1.603 | -2.8198 | -6.1496 | 11 | 0.024045 | 0.025958 | 0.027789 | 0.029519 | 0.031124 | 0.032619 | 0.033999 | 0.035272 | 0.036415 | 0.037441 | 0.03835 | 0.040141 | 0.041193 | 0.041084 | 0.039039 | 0.034964 | -0.0072233 | -0.14573 | -0.25634 | -0.55906 | 11 | 1.5403 | 1.5073 | 1.474 | 1.4404 | 1.4064 | 1.3723 | 1.3382 | 1.3042 | 1.2701 | 1.236 | 1.2021 | 1.1182 | 1.0352 | 0.9498 | 0.85578 | 0.75216 | 0.16091 | -0.72067 | -0.83262 | -0.48854
11.5 | 0.2211 | 0.2452 | 0.26837 | 0.29054 | 0.31119 | 0.33044 | 0.34823 | 0.36457 | 0.37952 | 0.39284 | 0.4047 | 0.42806 | 0.44231 | 0.44301 | 0.42008 | 0.37124 | -0.15367 | -1.8518 | -3.1773 | -7.0195 | 11.5 | 0.019226 | 0.021321 | 0.023337 | 0.025264 | 0.02706 | 0.028734 | 0.030281 | 0.031702 | 0.033002 | 0.03416 | 0.035192 | 0.037223 | 0.038462 | 0.038523 | 0.036529 | 0.032281 | -0.013363 | -0.16103 | -0.27628 | -0.61039 | 11.5 | 1.6006 | 1.5646 | 1.5281 | 1.4913 | 1.4542 | 1.417 | 1.3798 | 1.3426 | 1.3055 | 1.2685 | 1.2315 | 1.1401 | 1.0503 | 0.95879 | 0.85775 | 0.74547 | 0.098294 | -0.81607 | -0.91723 | -0.54683
12 | 0.19827 | 0.20199 | 0.22796 | 0.25314 | 0.277 | 0.29944 | 0.32012 | 0.33911 | 0.35638 | 0.37198 | 0.38591 | 0.41334 | 0.43001 | 0.43224 | 0.40858 | 0.35471 | -0.23906 | -2.123 | -3.561 | -7.965 | 12 | 0.016523 | 0.016832 | 0.018997 | 0.021095 | 0.023083 | 0.024953 | 0.026677 | 0.028259 | 0.029699 | 0.030999 | 0.032159 | 0.034445 | 0.035834 | 0.03602 | 0.034048 | 0.029559 | -0.019921 | -0.17692 | -0.29675 | -0.66375 | 12 | 1.6668 | 1.6196 | 1.5807 | 1.5408 | 1.5006 | 1.4605 | 1.42 | 1.3796 | 1.3393 | 1.2991 | 1.2591 | 1.1602 | 1.063 | 0.96492 | 0.85668 | 0.73504 | 0.028452 | -0.91595 | -1.0056 | -0.60753
Wind speed 13 m/s
Power Coefficient [-] | [20 empty] | Torque Coefficient [-] | [20 empty] | Thrust Coefficient [-]
TSR\Pitch [deg] | -4 | -3.6 | -3.2 | -2.8 | -2.4 | -2 | -1.6 | -1.2 | -0.8 | -0.4 | 0 | 1 | 2 | 3 | 4 | 5 | 10 | 20 | 30 | 50 | TSR\Pitch [deg] | -4 | -3.6 | -3.2 | -2.8 | -2.4 | -2 | -1.6 | -1.2 | -0.8 | -0.4 | 0 | 1 | 2 | 3 | 4 | 5 | 10 | 20 | 30 | 50 | TSR\Pitch [deg] | -4 | -3.6 | -3.2 | -2.8 | -2.4 | -2 | -1.6 | -1.2 | -0.8 | -0.4 | 0 | 1 | 2 | 3 | 4 | 5 | 10 | 20 | 30 | 50
3 | 0.027671 | 0.029707 | 0.031736 | 0.033761 | 0.035781 | 0.037798 | 0.039813 | 0.041824 | 0.043833 | 0.045843 | 0.047854 | 0.052845 | 0.057885 | 0.063157 | 0.068315 | 0.073518 | 0.1002 | 0.093132 | 0.0041843 | -0.13345 | 3 | 0.0092237 | 0.0099022 | 0.010579 | 0.011254 | 0.011927 | 0.012599 | 0.013271 | 0.013941 | 0.014611 | 0.015281 | 0.015951 | 0.017615 | 0.019295 | 0.021052 | 0.022772 | 0.024506 | 0.033401 | 0.031044 | 0.0013948 | -0.044482 | 3 | 0.18729 | 0.1872 | 0.18714 | 0.18708 | 0.18703 | 0.18701 | 0.187 | 0.18701 | 0.18703 | 0.18706 | 0.18711 | 0.18727 | 0.18763 | 0.18834 | 0.189 | 0.18984 | 0.19388 | 0.15791 | 0.06013 | -0.019884
4 | 0.066356 | 0.070382 | 0.074369 | 0.078456 | 0.082664 | 0.086899 | 0.091061 | 0.095145 | 0.099147 | 0.10317 | 0.10727 | 0.11803 | 0.1304 | 0.14303 | 0.15363 | 0.16211 | 0.18547 | 0.069001 | -0.10453 | -0.29056 | 4 | 0.016589 | 0.017596 | 0.018592 | 0.019614 | 0.020666 | 0.021725 | 0.022765 | 0.023786 | 0.024787 | 0.025793 | 0.026819 | 0.029507 | 0.032599 | 0.035758 | 0.038407 | 0.040528 | 0.046368 | 0.01725 | -0.026134 | -0.072641 | 4 | 0.268 | 0.26837 | 0.26873 | 0.26925 | 0.26996 | 0.27074 | 0.27145 | 0.27212 | 0.27275 | 0.27343 | 0.27426 | 0.27704 | 0.28069 | 0.28404 | 0.28549 | 0.28583 | 0.27821 | 0.13016 | -0.028277 | -0.055543
5 | 0.12421 | 0.13112 | 0.13801 | 0.14496 | 0.15197 | 0.15963 | 0.16797 | 0.17662 | 0.18552 | 0.19451 | 0.20349 | 0.2227 | 0.23945 | 0.25531 | 0.26902 | 0.27875 | 0.23306 | -0.018278 | -0.26795 | -0.55939 | 5 | 0.024843 | 0.026224 | 0.027602 | 0.028993 | 0.030395 | 0.031926 | 0.033594 | 0.035325 | 0.037105 | 0.038902 | 0.040699 | 0.044539 | 0.04789 | 0.051063 | 0.053803 | 0.05575 | 0.046612 | -0.0036555 | -0.053589 | -0.11188 | 5 | 0.37974 | 0.38101 | 0.38236 | 0.38397 | 0.38576 | 0.38791 | 0.39038 | 0.39297 | 0.39565 | 0.3983 | 0.40037 | 0.40374 | 0.40673 | 0.41131 | 0.41489 | 0.4146 | 0.32799 | 0.044446 | -0.13164 | -0.1033
6 | 0.20127 | 0.21516 | 0.22938 | 0.244 | 0.25868 | 0.27207 | 0.28485 | 0.29895 | 0.31283 | 0.32598 | 0.33718 | 0.36252 | 0.37597 | 0.37821 | 0.37018 | 0.35573 | 0.23087 | -0.15898 | -0.48737 | -0.9633 | 6 | 0.033545 | 0.03586 | 0.038231 | 0.040667 | 0.043113 | 0.045345 | 0.047475 | 0.049825 | 0.052138 | 0.054329 | 0.056197 | 0.06042 | 0.062661 | 0.063036 | 0.061697 | 0.059288 | 0.038478 | -0.026497 | -0.081228 | -0.16055 | 6 | 0.52596 | 0.53027 | 0.53474 | 0.53886 | 0.54235 | 0.54543 | 0.54872 | 0.55412 | 0.55996 | 0.56606 | 0.57098 | 0.58035 | 0.57794 | 0.56404 | 0.5404 | 0.51126 | 0.32837 | -0.073733 | -0.24325 | -0.16101
7 | 0.32771 | 0.34687 | 0.3632 | 0.37829 | 0.39824 | 0.41223 | 0.42257 | 0.43071 | 0.4369 | 0.44145 | 0.44442 | 0.44485 | 0.43774 | 0.42463 | 0.40549 | 0.38138 | 0.1938 | -0.34427 | -0.76841 | -1.5254 | 7 | 0.046816 | 0.049552 | 0.051886 | 0.054042 | 0.056891 | 0.058891 | 0.060367 | 0.06153 | 0.062415 | 0.063065 | 0.063488 | 0.063549 | 0.062535 | 0.060661 | 0.057928 | 0.054483 | 0.027686 | -0.049182 | -0.10977 | -0.21791 | 7 | 0.73788 | 0.74564 | 0.7502 | 0.75464 | 0.76548 | 0.76957 | 0.76942 | 0.76696 | 0.76241 | 0.75587 | 0.7472 | 0.71979 | 0.68544 | 0.64667 | 0.60341 | 0.55705 | 0.28927 | -0.20351 | -0.36463 | -0.22846
7.5 | 0.3837 | 0.39998 | 0.41275 | 0.42294 | 0.4315 | 0.43975 | 0.44619 | 0.45169 | 0.45509 | 0.45738 | 0.45892 | 0.45844 | 0.45049 | 0.43543 | 0.41398 | 0.38607 | 0.16007 | -0.45723 | -0.93349 | -1.8726 | 7.5 | 0.05116 | 0.05333 | 0.055033 | 0.056392 | 0.057533 | 0.058633 | 0.059492 | 0.060225 | 0.060678 | 0.060984 | 0.06119 | 0.061125 | 0.060066 | 0.058057 | 0.055197 | 0.051476 | 0.021342 | -0.060964 | -0.12447 | -0.24968 | 7.5 | 0.86704 | 0.87072 | 0.8702 | 0.86696 | 0.86157 | 0.85579 | 0.8467 | 0.8367 | 0.82479 | 0.81219 | 0.7991 | 0.76279 | 0.72069 | 0.67401 | 0.62356 | 0.56905 | 0.25388 | -0.27395 | -0.42916 | -0.26585
8 | 0.40013 | 0.411 | 0.42119 | 0.43024 | 0.43752 | 0.44365 | 0.44888 | 0.45338 | 0.45724 | 0.46085 | 0.46339 | 0.46492 | 0.45811 | 0.44222 | 0.41834 | 0.38589 | 0.1134 | -0.585 | -1.1146 | -2.2673 | 8 | 0.050016 | 0.051375 | 0.052649 | 0.05378 | 0.05469 | 0.055456 | 0.05611 | 0.056672 | 0.057155 | 0.057606 | 0.057923 | 0.058115 | 0.057263 | 0.055277 | 0.052292 | 0.048237 | 0.014175 | -0.073125 | -0.13932 | -0.28341 | 8 | 0.96602 | 0.95918 | 0.95062 | 0.93989 | 0.92767 | 0.91504 | 0.90102 | 0.88632 | 0.87101 | 0.85602 | 0.84005 | 0.79734 | 0.74934 | 0.6956 | 0.63741 | 0.57399 | 0.20622 | -0.34736 | -0.49582 | -0.30563
8.5 | 0.39462 | 0.4043 | 0.41336 | 0.42152 | 0.42909 | 0.43624 | 0.44278 | 0.44891 | 0.45411 | 0.45872 | 0.46265 | 0.46711 | 0.46181 | 0.44531 | 0.4179 | 0.38038 | 0.051081 | -0.72864 | -1.3111 | -2.7119 | 8.5 | 0.046426 | 0.047565 | 0.048631 | 0.04959 | 0.050481 | 0.051322 | 0.052092 | 0.052813 | 0.053424 | 0.053967 | 0.054429 | 0.054955 | 0.05433 | 0.052389 | 0.049165 | 0.044751 | 0.0060096 | -0.085723 | -0.15424 | -0.31905 | 8.5 | 1.0382 | 1.024 | 1.0095 | 0.99419 | 0.97803 | 0.96188 | 0.94499 | 0.92807 | 0.91024 | 0.89231 | 0.87438 | 0.82606 | 0.77197 | 0.71117 | 0.64395 | 0.57126 | 0.14502 | -0.4234 | -0.56415 | -0.34772
9 | 0.37594 | 0.38711 | 0.3976 | 0.40747 | 0.41671 | 0.42549 | 0.4336 | 0.4409 | 0.44749 | 0.45347 | 0.45831 | 0.46589 | 0.46197 | 0.4447 | 0.41353 | 0.36873 | -0.030486 | -0.88932 | -1.5229 | -3.2089 | 9 | 0.041772 | 0.043012 | 0.044178 | 0.045275 | 0.046301 | 0.047276 | 0.048178 | 0.048988 | 0.049721 | 0.050386 | 0.050923 | 0.051766 | 0.05133 | 0.049411 | 0.045948 | 0.040969 | -0.0033873 | -0.098813 | -0.16921 | -0.35654 | 9 | 1.0934 | 1.0762 | 1.0585 | 1.0404 | 1.0218 | 1.003 | 0.98379 | 0.964 | 0.94388 | 0.92371 | 0.90281 | 0.84912 | 0.78853 | 0.72038 | 0.64407 | 0.56014 | 0.068733 | -0.502 | -0.6338 | -0.39206
9.5 | 0.35308 | 0.36605 | 0.37862 | 0.39052 | 0.40172 | 0.41201 | 0.42155 | 0.43034 | 0.43832 | 0.44558 | 0.45172 | 0.462 | 0.46001 | 0.44086 | 0.40396 | 0.34998 | -0.13557 | -1.0681 | -1.7504 | -3.7606 | 9.5 | 0.037167 | 0.038532 | 0.039855 | 0.041108 | 0.042287 | 0.043369 | 0.044374 | 0.045299 | 0.046139 | 0.046903 | 0.047549 | 0.048631 | 0.048422 | 0.046406 | 0.042522 | 0.03684 | -0.014271 | -0.11243 | -0.18425 | -0.39585 | 9.5 | 1.1423 | 1.1223 | 1.1021 | 1.0816 | 1.0607 | 1.0391 | 1.0172 | 0.99503 | 0.97251 | 0.9499 | 0.92672 | 0.86678 | 0.80026 | 0.72348 | 0.63617 | 0.53944 | -0.022488 | -0.58328 | -0.705 | -0.43857
10 | 0.32663 | 0.34202 | 0.35692 | 0.37081 | 0.38409 | 0.39633 | 0.40768 | 0.41809 | 0.42756 | 0.43607 | 0.44377 | 0.45673 | 0.45587 | 0.43333 | 0.38825 | 0.3211 | -0.2598 | -1.2659 | -1.9948 | -4.3693 | 10 | 0.032663 | 0.034202 | 0.035692 | 0.037081 | 0.038409 | 0.039633 | 0.040768 | 0.041809 | 0.042756 | 0.043607 | 0.044377 | 0.045673 | 0.045587 | 0.043333 | 0.038825 | 0.03211 | -0.02598 | -0.12659 | -0.19948 | -0.43693 | 10 | 1.1866 | 1.1642 | 1.1417 | 1.1185 | 1.0951 | 1.0712 | 1.0468 | 1.0222 | 0.99719 | 0.97182 | 0.9464 | 0.87994 | 0.80629 | 0.71926 | 0.61886 | 0.50617 | -0.12116 | -0.66744 | -0.77803 | -0.48721
10.5 | 0.29793 | 0.31606 | 0.33351 | 0.34988 | 0.36527 | 0.37962 | 0.39292 | 0.40513 | 0.41622 | 0.42615 | 0.43501 | 0.45059 | 0.44972 | 0.42093 | 0.3634 | 0.27769 | -0.39232 | -1.4828 | -2.2562 | -5.0373 | 10.5 | 0.028375 | 0.030101 | 0.031763 | 0.033322 | 0.034787 | 0.036154 | 0.037421 | 0.038584 | 0.03964 | 0.040585 | 0.041429 | 0.042913 | 0.042831 | 0.040088 | 0.03461 | 0.026447 | -0.037364 | -0.14122 | -0.21487 | -0.47974 | 10.5 | 1.2282 | 1.2034 | 1.1784 | 1.1528 | 1.1268 | 1.1003 | 1.0734 | 1.046 | 1.0182 | 0.99006 | 0.96162 | 0.88797 | 0.8058 | 0.70615 | 0.58896 | 0.45623 | -0.21454 | -0.75374 | -0.85363 | -0.53789
11 | 0.26699 | 0.28817 | 0.30852 | 0.32776 | 0.34567 | 0.36239 | 0.37785 | 0.39215 | 0.40497 | 0.41643 | 0.42643 | 0.44407 | 0.44051 | 0.40126 | 0.32519 | 0.21231 | -0.53119 | -1.7201 | -2.5259 | -5.7668 | 11 | 0.024271 | 0.026198 | 0.028047 | 0.029797 | 0.031425 | 0.032945 | 0.03435 | 0.03565 | 0.036815 | 0.037857 | 0.038766 | 0.04037 | 0.040046 | 0.036478 | 0.029563 | 0.019301 | -0.04829 | -0.15637 | -0.22963 | -0.52425 | 11 | 1.2667 | 1.2395 | 1.2121 | 1.1841 | 1.1554 | 1.1262 | 1.0964 | 1.0663 | 1.0354 | 1.004 | 0.97219 | 0.89029 | 0.79729 | 0.68098 | 0.54221 | 0.38384 | -0.30266 | -0.84258 | -0.93243 | -0.59057
11.5 | 0.23552 | 0.26004 | 0.28336 | 0.30559 | 0.32627 | 0.34552 | 0.36331 | 0.37958 | 0.39432 | 0.4072 | 0.41843 | 0.43693 | 0.42664 | 0.37009 | 0.26507 | 0.1141 | -0.6817 | -1.947 | -2.8769 | -6.5601 | 11.5 | 0.02048 | 0.022612 | 0.02464 | 0.026573 | 0.028371 | 0.030045 | 0.031592 | 0.033007 | 0.034289 | 0.035409 | 0.036385 | 0.037994 | 0.037099 | 0.032181 | 0.023049 | 0.0099218 | -0.059278 | -0.1693 | -0.25016 | -0.57044 | 11.5 | 1.3034 | 1.2737 | 1.2434 | 1.2126 | 1.1809 | 1.1486 | 1.1156 | 1.0819 | 1.0477 | 1.0127 | 0.9773 | 0.88573 | 0.77804 | 0.63937 | 0.47124 | 0.2822 | -0.39083 | -0.93372 | -1.0198 | -0.64519
12 | 0.20368 | 0.23189 | 0.2587 | 0.28399 | 0.3077 | 0.32987 | 0.3501 | 0.36841 | 0.38475 | 0.39901 | 0.41093 | 0.42854 | 0.40398 | 0.31823 | 0.1686 | -0.03063 | -0.84508 | -2.201 | -3.1177 | -7.4194 | 12 | 0.016974 | 0.019324 | 0.021558 | 0.023666 | 0.025641 | 0.027489 | 0.029175 | 0.030701 | 0.032062 | 0.033251 | 0.034244 | 0.035712 | 0.033665 | 0.026519 | 0.01405 | -0.0025525 | -0.070423 | -0.18342 | -0.25981 | -0.61828 | 12 | 1.3377 | 1.3051 | 1.2717 | 1.2375 | 1.2025 | 1.1668 | 1.1301 | 1.0925 | 1.0541 | 1.0149 | 0.9751 | 0.87255 | 0.74326 | 0.57228 | 0.36568 | 0.1465 | -0.48061 | -1.04 | -1.1019 | -0.7017
Wind speed 7 m/s
Power Coefficient [-] | [20 empty] | Torque Coefficient [-] | [20 empty] | Thrust Coefficient [-]
TSR\Pitch [deg] | -4 | -3.6 | -3.2 | -2.8 | -2.4 | -2 | -1.6 | -1.2 | -0.8 | -0.4 | 0 | 1 | 2 | 3 | 4 | 5 | 10 | 20 | 30 | 50 | TSR\Pitch [deg] | -4 | -3.6 | -3.2 | -2.8 | -2.4 | -2 | -1.6 | -1.2 | -0.8 | -0.4 | 0 | 1 | 2 | 3 | 4 | 5 | 10 | 20 | 30 | 50 | TSR\Pitch [deg] | -4 | -3.6 | -3.2 | -2.8 | -2.4 | -2 | -1.6 | -1.2 | -0.8 | -0.4 | 0 | 1 | 2 | 3 | 4 | 5 | 10 | 20 | 30 | 50
3 | 0.02669 | 0.028756 | 0.030817 | 0.032873 | 0.034926 | 0.036977 | 0.039026 | 0.041074 | 0.04312 | 0.045166 | 0.047215 | 0.05228 | 0.057441 | 0.062786 | 0.067997 | 0.07333 | 0.099632 | 0.093358 | 0.0066252 | -0.13423 | 3 | 0.0088968 | 0.0095853 | 0.010272 | 0.010958 | 0.011642 | 0.012326 | 0.013009 | 0.013691 | 0.014373 | 0.015055 | 0.015738 | 0.017427 | 0.019147 | 0.020929 | 0.022666 | 0.024443 | 0.033211 | 0.031119 | 0.0022084 | -0.044742 | 3 | 0.32613 | 0.32604 | 0.32597 | 0.32591 | 0.32586 | 0.32584 | 0.32583 | 0.32584 | 0.32586 | 0.32589 | 0.32595 | 0.32611 | 0.32654 | 0.32726 | 0.32792 | 0.32887 | 0.33237 | 0.2977 | 0.20168 | 0.11976
4 | 0.064749 | 0.068873 | 0.072971 | 0.077227 | 0.08157 | 0.085884 | 0.090127 | 0.094279 | 0.098341 | 0.10243 | 0.1067 | 0.11817 | 0.13112 | 0.14333 | 0.15288 | 0.16094 | 0.18328 | 0.074695 | -0.10197 | -0.29442 | 4 | 0.016187 | 0.017218 | 0.018243 | 0.019307 | 0.020393 | 0.021471 | 0.022532 | 0.02357 | 0.024585 | 0.025608 | 0.026676 | 0.029544 | 0.032779 | 0.035833 | 0.03822 | 0.040236 | 0.045821 | 0.018674 | -0.025493 | -0.073605 | 4 | 0.40591 | 0.4063 | 0.4067 | 0.40733 | 0.40811 | 0.40889 | 0.40961 | 0.41029 | 0.41093 | 0.41164 | 0.41262 | 0.41578 | 0.41958 | 0.42221 | 0.42306 | 0.42311 | 0.41508 | 0.27567 | 0.11232 | 0.084259
5 | 0.12211 | 0.12916 | 0.13633 | 0.14356 | 0.15112 | 0.15958 | 0.16845 | 0.17745 | 0.18666 | 0.19543 | 0.20364 | 0.22127 | 0.237 | 0.25232 | 0.26563 | 0.27503 | 0.23452 | 0.0018285 | -0.26889 | -0.57037 | 5 | 0.024422 | 0.025833 | 0.027266 | 0.028713 | 0.030224 | 0.031915 | 0.03369 | 0.03549 | 0.037331 | 0.039085 | 0.040729 | 0.044254 | 0.0474 | 0.050465 | 0.053126 | 0.055005 | 0.046904 | 0.00036569 | -0.053778 | -0.11407 | 5 | 0.51696 | 0.51825 | 0.51981 | 0.52162 | 0.52369 | 0.52621 | 0.52891 | 0.53152 | 0.53424 | 0.53619 | 0.53769 | 0.54019 | 0.54223 | 0.5462 | 0.54946 | 0.54897 | 0.46925 | 0.20284 | 0.0067678 | 0.036469
6 | 0.19933 | 0.2137 | 0.22841 | 0.24277 | 0.25651 | 0.26934 | 0.2815 | 0.29387 | 0.30855 | 0.32278 | 0.33371 | 0.35741 | 0.37343 | 0.37738 | 0.37076 | 0.35718 | 0.24173 | -0.12374 | -0.4993 | -0.98886 | 6 | 0.033221 | 0.035617 | 0.038069 | 0.040462 | 0.042751 | 0.04489 | 0.046917 | 0.048979 | 0.051425 | 0.053797 | 0.055619 | 0.059568 | 0.062238 | 0.062897 | 0.061793 | 0.05953 | 0.040289 | -0.020624 | -0.083217 | -0.16481 | 6 | 0.66412 | 0.6685 | 0.67298 | 0.67643 | 0.67941 | 0.68214 | 0.6847 | 0.68798 | 0.69416 | 0.70114 | 0.70545 | 0.71293 | 0.71309 | 0.70146 | 0.67964 | 0.65201 | 0.4811 | 0.089164 | -0.10845 | -0.021466
7 | 0.31653 | 0.34072 | 0.35869 | 0.37438 | 0.38834 | 0.4052 | 0.42328 | 0.43276 | 0.43946 | 0.44433 | 0.4486 | 0.45193 | 0.44482 | 0.43201 | 0.41341 | 0.39028 | 0.22516 | -0.29878 | -0.80089 | -1.5775 | 7 | 0.045219 | 0.048675 | 0.051242 | 0.053482 | 0.055477 | 0.057885 | 0.060469 | 0.061823 | 0.06278 | 0.063476 | 0.064086 | 0.064561 | 0.063546 | 0.061716 | 0.059059 | 0.055754 | 0.032166 | -0.042682 | -0.11441 | -0.22536 | 7 | 0.87049 | 0.88387 | 0.88974 | 0.89361 | 0.89617 | 0.90284 | 0.91071 | 0.90917 | 0.90545 | 0.89984 | 0.89322 | 0.86847 | 0.83458 | 0.79655 | 0.75434 | 0.70945 | 0.46588 | -0.044909 | -0.23313 | -0.089657
7.5 | 0.37248 | 0.39324 | 0.4133 | 0.42803 | 0.43724 | 0.44413 | 0.45097 | 0.45801 | 0.4633 | 0.46737 | 0.46934 | 0.46886 | 0.4612 | 0.4467 | 0.42612 | 0.40033 | 0.20898 | -0.405 | -0.98112 | -1.9439 | 7.5 | 0.049665 | 0.052432 | 0.055107 | 0.057071 | 0.058299 | 0.059217 | 0.060129 | 0.061068 | 0.061773 | 0.062316 | 0.062579 | 0.062515 | 0.061494 | 0.059559 | 0.056816 | 0.053378 | 0.027864 | -0.054 | -0.13082 | -0.25919 | 7.5 | 1.0007 | 1.0092 | 1.0173 | 1.018 | 1.0126 | 1.0055 | 0.99844 | 0.99084 | 0.98027 | 0.96874 | 0.95597 | 0.91978 | 0.87786 | 0.83191 | 0.7825 | 0.73066 | 0.44987 | -0.11654 | -0.29925 | -0.12772
8 | 0.40865 | 0.41928 | 0.42826 | 0.43711 | 0.44648 | 0.45502 | 0.46196 | 0.46628 | 0.46977 | 0.47285 | 0.47539 | 0.4775 | 0.47152 | 0.45708 | 0.43509 | 0.40679 | 0.18713 | -0.52502 | -1.1807 | -2.3626 | 8 | 0.051081 | 0.05241 | 0.053532 | 0.054639 | 0.05581 | 0.056878 | 0.057745 | 0.058285 | 0.058721 | 0.059106 | 0.059424 | 0.059688 | 0.05894 | 0.057136 | 0.054387 | 0.050849 | 0.023391 | -0.065628 | -0.14758 | -0.29533 | 8 | 1.1292 | 1.1211 | 1.1121 | 1.1031 | 1.0939 | 1.083 | 1.0699 | 1.0547 | 1.0388 | 1.0229 | 1.0067 | 0.96339 | 0.91524 | 0.86255 | 0.80616 | 0.74732 | 0.42822 | -0.191 | -0.36714 | -0.16843
8.5 | 0.40381 | 0.41644 | 0.42817 | 0.43758 | 0.44487 | 0.45135 | 0.45718 | 0.46254 | 0.46719 | 0.47152 | 0.47518 | 0.48041 | 0.47689 | 0.4635 | 0.44059 | 0.40979 | 0.15972 | -0.65997 | -1.3995 | -2.8368 | 8.5 | 0.047507 | 0.048993 | 0.050373 | 0.05148 | 0.052338 | 0.0531 | 0.053786 | 0.054416 | 0.054964 | 0.055473 | 0.055904 | 0.056519 | 0.056105 | 0.05453 | 0.051834 | 0.04821 | 0.018791 | -0.077644 | -0.16464 | -0.33374 | 8.5 | 1.2177 | 1.2078 | 1.1952 | 1.1802 | 1.1637 | 1.1459 | 1.1276 | 1.1091 | 1.0899 | 1.0708 | 1.0516 | 1.0019 | 0.94761 | 0.88883 | 0.82579 | 0.75984 | 0.40141 | -0.26824 | -0.43631 | -0.21177
9 | 0.39308 | 0.4044 | 0.41459 | 0.42408 | 0.43267 | 0.44087 | 0.44806 | 0.45458 | 0.4604 | 0.46552 | 0.47028 | 0.47806 | 0.47774 | 0.46629 | 0.44333 | 0.41009 | 0.12608 | -0.81126 | -1.6379 | -3.3696 | 9 | 0.043675 | 0.044933 | 0.046066 | 0.04712 | 0.048075 | 0.048985 | 0.049785 | 0.050509 | 0.051155 | 0.051725 | 0.052254 | 0.053118 | 0.053082 | 0.05181 | 0.049259 | 0.045565 | 0.014009 | -0.090139 | -0.18199 | -0.3744 | 9 | 1.3016 | 1.2835 | 1.2642 | 1.2442 | 1.2233 | 1.2027 | 1.1809 | 1.1588 | 1.1363 | 1.1138 | 1.0917 | 1.035 | 0.97544 | 0.91128 | 0.84231 | 0.76921 | 0.36908 | -0.34829 | -0.50654 | -0.25768
9.5 | 0.36894 | 0.38207 | 0.3943 | 0.40594 | 0.4163 | 0.42587 | 0.43467 | 0.44267 | 0.44981 | 0.45627 | 0.46181 | 0.47221 | 0.47549 | 0.46638 | 0.44332 | 0.40773 | 0.085723 | -0.9802 | -1.8972 | -3.9639 | 9.5 | 0.038835 | 0.040218 | 0.041506 | 0.042731 | 0.043821 | 0.044829 | 0.045755 | 0.046596 | 0.047349 | 0.048028 | 0.048611 | 0.049706 | 0.050051 | 0.049092 | 0.046665 | 0.042919 | 0.0090235 | -0.10318 | -0.1997 | -0.41725 | 9.5 | 1.3724 | 1.3501 | 1.327 | 1.3039 | 1.2794 | 1.2546 | 1.2296 | 1.2044 | 1.179 | 1.1537 | 1.1282 | 1.0649 | 1.0005 | 0.93106 | 0.85571 | 0.7755 | 0.33117 | -0.43124 | -0.57848 | -0.30613
10 | 0.33923 | 0.35456 | 0.36922 | 0.38261 | 0.3953 | 0.40689 | 0.41753 | 0.42723 | 0.43602 | 0.44386 | 0.45093 | 0.46386 | 0.47014 | 0.46375 | 0.44109 | 0.40244 | 0.038122 | -1.168 | -2.1788 | -4.6226 | 10 | 0.033923 | 0.035456 | 0.036922 | 0.038261 | 0.03953 | 0.040689 | 0.041753 | 0.042723 | 0.043602 | 0.044386 | 0.045093 | 0.046386 | 0.047014 | 0.046375 | 0.044109 | 0.040244 | 0.0038122 | -0.1168 | -0.21788 | -0.46226 | 10 | 1.4395 | 1.4133 | 1.3866 | 1.3592 | 1.3318 | 1.3038 | 1.2756 | 1.2473 | 1.2191 | 1.1908 | 1.1629 | 1.0925 | 1.0224 | 0.94777 | 0.86638 | 0.77844 | 0.28746 | -0.51751 | -0.65296 | -0.35711
10.5 | 0.30453 | 0.32264 | 0.33962 | 0.35578 | 0.37072 | 0.38459 | 0.39738 | 0.40909 | 0.41964 | 0.42908 | 0.4375 | 0.4537 | 0.46268 | 0.45894 | 0.43615 | 0.39445 | -0.017714 | -1.3754 | -2.4844 | -5.3485 | 10.5 | 0.029003 | 0.030727 | 0.032345 | 0.033884 | 0.035307 | 0.036627 | 0.037846 | 0.038961 | 0.039966 | 0.040864 | 0.041667 | 0.043209 | 0.044064 | 0.043709 | 0.041538 | 0.037567 | -0.001687 | -0.13099 | -0.23661 | -0.50938 | 10.5 | 1.504 | 1.4741 | 1.4438 | 1.4133 | 1.3823 | 1.3512 | 1.32 | 1.2888 | 1.2576 | 1.2263 | 1.1953 | 1.1183 | 1.0418 | 0.96192 | 0.87387 | 0.77813 | 0.23754 | -0.60664 | -0.73064 | -0.41062
11 | 0.26467 | 0.28575 | 0.30594 | 0.32501 | 0.34269 | 0.35917 | 0.37436 | 0.38837 | 0.40095 | 0.41223 | 0.42221 | 0.44186 | 0.45333 | 0.45189 | 0.42896 | 0.38369 | -0.082416 | -1.6031 | -2.8151 | -6.1445 | 11 | 0.024061 | 0.025977 | 0.027813 | 0.029546 | 0.031154 | 0.032652 | 0.034033 | 0.035306 | 0.03645 | 0.037475 | 0.038383 | 0.040169 | 0.041212 | 0.041081 | 0.038997 | 0.034881 | -0.0074923 | -0.14574 | -0.25592 | -0.55859 | 11 | 1.5658 | 1.5326 | 1.4991 | 1.4654 | 1.4313 | 1.3971 | 1.3629 | 1.3288 | 1.2945 | 1.2603 | 1.2262 | 1.142 | 1.0588 | 0.97302 | 0.87853 | 0.77441 | 0.18128 | -0.69883 | -0.81183 | -0.4666
11.5 | 0.22136 | 0.24552 | 0.26875 | 0.29096 | 0.31165 | 0.33092 | 0.34873 | 0.36508 | 0.38002 | 0.39332 | 0.40516 | 0.42845 | 0.44259 | 0.44299 | 0.41951 | 0.37007 | -0.15736 | -1.8517 | -3.1714 | -7.0132 | 11.5 | 0.019248 | 0.021349 | 0.02337 | 0.025301 | 0.0271 | 0.028776 | 0.030325 | 0.031746 | 0.033045 | 0.034202 | 0.035232 | 0.037256 | 0.038486 | 0.038521 | 0.036479 | 0.03218 | -0.013684 | -0.16102 | -0.27578 | -0.60984 | 11.5 | 1.626 | 1.5899 | 1.5532 | 1.5163 | 1.479 | 1.4417 | 1.4043 | 1.3669 | 1.3297 | 1.2925 | 1.2555 | 1.1637 | 1.0736 | 0.98173 | 0.88013 | 0.76727 | 0.11799 | -0.79435 | -0.89673 | -0.52501
12 | 0.19858 | 0.20242 | 0.22848 | 0.25371 | 0.27762 | 0.30009 | 0.32078 | 0.33976 | 0.35702 | 0.3726 | 0.3865 | 0.41383 | 0.43035 | 0.43224 | 0.40789 | 0.35326 | -0.24363 | -2.1227 | -3.5538 | -7.9573 | 12 | 0.016549 | 0.016869 | 0.01904 | 0.021143 | 0.023135 | 0.025007 | 0.026732 | 0.028313 | 0.029752 | 0.03105 | 0.032209 | 0.034485 | 0.035863 | 0.03602 | 0.033991 | 0.029438 | -0.020302 | -0.17689 | -0.29615 | -0.6631 | 12 | 1.6922 | 1.6448 | 1.6057 | 1.5656 | 1.5253 | 1.4849 | 1.4443 | 1.4038 | 1.3633 | 1.3229 | 1.2827 | 1.1835 | 1.086 | 0.98753 | 0.87864 | 0.7563 | 0.047393 | -0.89434 | -0.98538 | -0.58584
Wind speed 9 m/s
Power Coefficient [-] | [20 empty] | Torque Coefficient [-] | [20 empty] | Thrust Coefficient [-]
TSR\Pitch [deg] | -4 | -3.6 | -3.2 | -2.8 | -2.4 | -2 | -1.6 | -1.2 | -0.8 | -0.4 | 0 | 1 | 2 | 3 | 4 | 5 | 10 | 20 | 30 | 50 | TSR\Pitch [deg] | -4 | -3.6 | -3.2 | -2.8 | -2.4 | -2 | -1.6 | -1.2 | -0.8 | -0.4 | 0 | 1 | 2 | 3 | 4 | 5 | 10 | 20 | 30 | 50 | TSR\Pitch [deg] | -4 | -3.6 | -3.2 | -2.8 | -2.4 | -2 | -1.6 | -1.2 | -0.8 | -0.4 | 0 | 1 | 2 | 3 | 4 | 5 | 10 | 20 | 30 | 50
3 | 0.026946 | 0.029004 | 0.031056 | 0.033103 | 0.035148 | 0.037189 | 0.039229 | 0.041267 | 0.043303 | 0.045339 | 0.047378 | 0.052424 | 0.057548 | 0.062875 | 0.068073 | 0.073363 | 0.099795 | 0.093315 | 0.0059501 | -0.13401 | 3 | 0.008982 | 0.0096679 | 0.010352 | 0.011034 | 0.011716 | 0.012396 | 0.013076 | 0.013756 | 0.014434 | 0.015113 | 0.015793 | 0.017475 | 0.019183 | 0.020958 | 0.022691 | 0.024454 | 0.033265 | 0.031105 | 0.0019834 | -0.044671 | 3 | 0.25255 | 0.25246 | 0.25239 | 0.25233 | 0.25228 | 0.25226 | 0.25225 | 0.25226 | 0.25228 | 0.25231 | 0.25236 | 0.25253 | 0.25293 | 0.25365 | 0.25431 | 0.25522 | 0.2589 | 0.22384 | 0.12727 | 0.045816
4 | 0.065116 | 0.069217 | 0.073275 | 0.077481 | 0.081784 | 0.086082 | 0.090307 | 0.094444 | 0.098495 | 0.10256 | 0.10677 | 0.11798 | 0.13076 | 0.14325 | 0.15309 | 0.16129 | 0.18403 | 0.073109 | -0.1027 | -0.29335 | 4 | 0.016279 | 0.017304 | 0.018319 | 0.01937 | 0.020446 | 0.02152 | 0.022577 | 0.023611 | 0.024624 | 0.02564 | 0.026692 | 0.029495 | 0.03269 | 0.035812 | 0.038272 | 0.040322 | 0.046007 | 0.018277 | -0.025675 | -0.073338 | 4 | 0.33268 | 0.33306 | 0.33344 | 0.33404 | 0.3348 | 0.33558 | 0.33631 | 0.33699 | 0.33762 | 0.33831 | 0.33923 | 0.34227 | 0.34605 | 0.34898 | 0.35001 | 0.35017 | 0.34224 | 0.20018 | 0.038125 | 0.010251
5 | 0.1224 | 0.12942 | 0.13647 | 0.14363 | 0.15089 | 0.15907 | 0.16777 | 0.17665 | 0.18577 | 0.19471 | 0.20336 | 0.22154 | 0.23768 | 0.2534 | 0.26688 | 0.27648 | 0.23446 | -0.0033793 | -0.26857 | -0.56732 | 5 | 0.024481 | 0.025883 | 0.027295 | 0.028726 | 0.030179 | 0.031813 | 0.033554 | 0.035329 | 0.037153 | 0.038942 | 0.040672 | 0.044308 | 0.047536 | 0.050679 | 0.053377 | 0.055295 | 0.046891 | -0.00067586 | -0.053713 | -0.11346 | 5 | 0.44412 | 0.44539 | 0.44685 | 0.4486 | 0.45053 | 0.45292 | 0.45559 | 0.4582 | 0.46095 | 0.46328 | 0.465 | 0.46782 | 0.47019 | 0.47441 | 0.47775 | 0.47738 | 0.39544 | 0.12407 | -0.06686 | -0.037584
6 | 0.19842 | 0.21255 | 0.22716 | 0.24162 | 0.25602 | 0.2692 | 0.28163 | 0.2943 | 0.30988 | 0.32355 | 0.33438 | 0.35927 | 0.37506 | 0.37902 | 0.37203 | 0.35809 | 0.23926 | -0.13449 | -0.4955 | -0.98169 | 6 | 0.03307 | 0.035425 | 0.03786 | 0.040269 | 0.042669 | 0.044866 | 0.046939 | 0.049049 | 0.051646 | 0.053925 | 0.055731 | 0.059878 | 0.06251 | 0.06317 | 0.062005 | 0.059681 | 0.039877 | -0.022415 | -0.082583 | -0.16361 | 6 | 0.59112 | 0.59547 | 0.60011 | 0.60401 | 0.6073 | 0.61023 | 0.613 | 0.61655 | 0.62389 | 0.62998 | 0.63409 | 0.6427 | 0.64252 | 0.63061 | 0.60812 | 0.57978 | 0.40435 | 0.0075511 | -0.18113 | -0.09555
7 | 0.31708 | 0.34081 | 0.35879 | 0.37462 | 0.38898 | 0.40953 | 0.4239 | 0.43359 | 0.44014 | 0.44532 | 0.44956 | 0.45255 | 0.4453 | 0.43226 | 0.41322 | 0.38944 | 0.21775 | -0.31351 | -0.79045 | -1.5627 | 7 | 0.045298 | 0.048687 | 0.051256 | 0.053517 | 0.055569 | 0.058504 | 0.060558 | 0.061941 | 0.062877 | 0.063617 | 0.064222 | 0.064649 | 0.063614 | 0.061751 | 0.059032 | 0.055635 | 0.031107 | -0.044787 | -0.11292 | -0.22324 | 7 | 0.79981 | 0.81259 | 0.81878 | 0.82273 | 0.82577 | 0.83668 | 0.84034 | 0.83905 | 0.83499 | 0.82952 | 0.82268 | 0.79705 | 0.76247 | 0.72364 | 0.68049 | 0.6345 | 0.38327 | -0.12561 | -0.30514 | -0.16369
7.5 | 0.37362 | 0.39335 | 0.41381 | 0.42792 | 0.43676 | 0.44428 | 0.45152 | 0.45839 | 0.46355 | 0.46746 | 0.46909 | 0.46867 | 0.46093 | 0.44609 | 0.42491 | 0.39822 | 0.19763 | -0.4219 | -0.96552 | -1.9235 | 7.5 | 0.049816 | 0.052447 | 0.055174 | 0.057055 | 0.058234 | 0.059238 | 0.060202 | 0.061119 | 0.061806 | 0.062328 | 0.062545 | 0.062489 | 0.061457 | 0.059479 | 0.056655 | 0.053097 | 0.02635 | -0.056253 | -0.12874 | -0.25646 | 7.5 | 0.93132 | 0.93849 | 0.94694 | 0.94696 | 0.94124 | 0.93479 | 0.92775 | 0.91959 | 0.90854 | 0.89677 | 0.88354 | 0.84675 | 0.80411 | 0.75727 | 0.70673 | 0.65352 | 0.36274 | -0.1967 | -0.37117 | -0.20167
8 | 0.4074 | 0.41774 | 0.42712 | 0.43676 | 0.44626 | 0.45461 | 0.46095 | 0.46523 | 0.46892 | 0.47209 | 0.47473 | 0.47682 | 0.47057 | 0.45559 | 0.43269 | 0.40308 | 0.17047 | -0.54452 | -1.1587 | -2.335 | 8 | 0.050925 | 0.052217 | 0.05339 | 0.054596 | 0.055782 | 0.056827 | 0.057619 | 0.058154 | 0.058615 | 0.059011 | 0.059342 | 0.059603 | 0.058821 | 0.056949 | 0.054086 | 0.050386 | 0.021308 | -0.068065 | -0.14484 | -0.29188 | 8 | 1.0565 | 1.0482 | 1.0395 | 1.0311 | 1.0213 | 1.0099 | 0.99615 | 0.98066 | 0.96473 | 0.94862 | 0.93229 | 0.88837 | 0.83943 | 0.78568 | 0.72787 | 0.66727 | 0.33523 | -0.27092 | -0.43907 | -0.24225
8.5 | 0.40242 | 0.41538 | 0.42683 | 0.43527 | 0.44282 | 0.44956 | 0.45557 | 0.4612 | 0.46611 | 0.47059 | 0.47435 | 0.4794 | 0.47551 | 0.46113 | 0.43683 | 0.40409 | 0.13593 | -0.68247 | -1.3696 | -2.8003 | 8.5 | 0.047343 | 0.048868 | 0.050216 | 0.051209 | 0.052096 | 0.052889 | 0.053596 | 0.054258 | 0.054836 | 0.055363 | 0.055806 | 0.0564 | 0.055942 | 0.054251 | 0.051391 | 0.04754 | 0.015992 | -0.08029 | -0.16113 | -0.32944 | 8.5 | 1.1435 | 1.1328 | 1.1194 | 1.1035 | 1.0869 | 1.0692 | 1.0507 | 1.0323 | 1.0131 | 0.99394 | 0.97467 | 0.92422 | 0.86931 | 0.80915 | 0.7443 | 0.67604 | 0.30087 | -0.34797 | -0.5086 | -0.28538
9 | 0.3897 | 0.40134 | 0.41178 | 0.42146 | 0.43037 | 0.43885 | 0.44635 | 0.45311 | 0.45918 | 0.46454 | 0.46951 | 0.47736 | 0.47618 | 0.46316 | 0.43799 | 0.40192 | 0.092886 | -0.83703 | -1.598 | -3.322 | 9 | 0.0433 | 0.044593 | 0.045753 | 0.046829 | 0.047819 | 0.048762 | 0.049595 | 0.050345 | 0.05102 | 0.051616 | 0.052168 | 0.05304 | 0.052909 | 0.051463 | 0.048666 | 0.044658 | 0.010321 | -0.093003 | -0.17755 | -0.36911 | 9 | 1.2206 | 1.2026 | 1.1833 | 1.1632 | 1.1425 | 1.1221 | 1.1005 | 1.0784 | 1.0562 | 1.0338 | 1.0117 | 0.9548 | 0.89416 | 0.82823 | 0.7568 | 0.68065 | 0.25902 | -0.42779 | -0.57953 | -0.33102
9.5 | 0.36573 | 0.37909 | 0.39158 | 0.40348 | 0.41412 | 0.42401 | 0.43309 | 0.44137 | 0.44878 | 0.45549 | 0.46124 | 0.47185 | 0.47414 | 0.46268 | 0.43622 | 0.39637 | 0.040415 | -1.0094 | -1.8446 | -3.9029 | 9.5 | 0.038498 | 0.039904 | 0.041219 | 0.042472 | 0.043592 | 0.044632 | 0.045589 | 0.046459 | 0.047239 | 0.047947 | 0.048551 | 0.049668 | 0.049909 | 0.048704 | 0.045918 | 0.041724 | 0.0042542 | -0.10626 | -0.19417 | -0.41083 | 9.5 | 1.2857 | 1.2637 | 1.241 | 1.2181 | 1.194 | 1.1695 | 1.1449 | 1.12 | 1.0949 | 1.0698 | 1.0445 | 0.9812 | 0.9157 | 0.84394 | 0.76525 | 0.68098 | 0.20936 | -0.51049 | -0.65217 | -0.37912
10 | 0.33666 | 0.3523 | 0.36706 | 0.38074 | 0.39374 | 0.40562 | 0.41655 | 0.42654 | 0.43559 | 0.44365 | 0.45088 | 0.46412 | 0.46937 | 0.45961 | 0.43182 | 0.38717 | -0.023094 | -1.2009 | -2.1109 | -4.5455 | 10 | 0.033666 | 0.03523 | 0.036706 | 0.038074 | 0.039374 | 0.040562 | 0.041655 | 0.042654 | 0.043559 | 0.044365 | 0.045088 | 0.046412 | 0.046937 | 0.045961 | 0.043182 | 0.038717 | -0.0023094 | -0.12009 | -0.21109 | -0.45455 | 10 | 1.3465 | 1.3206 | 1.2945 | 1.2678 | 1.241 | 1.2136 | 1.186 | 1.1582 | 1.1303 | 1.1024 | 1.0747 | 1.0046 | 0.93344 | 0.85585 | 0.76984 | 0.67651 | 0.15118 | -0.59639 | -0.72712 | -0.42965
10.5 | 0.30332 | 0.3215 | 0.33892 | 0.35517 | 0.37038 | 0.38454 | 0.39761 | 0.40952 | 0.42028 | 0.42988 | 0.43845 | 0.45482 | 0.4627 | 0.45456 | 0.42423 | 0.37428 | -0.099253 | -1.4118 | -2.3982 | -5.2524 | 10.5 | 0.028888 | 0.030619 | 0.032279 | 0.033826 | 0.035274 | 0.036623 | 0.037868 | 0.039002 | 0.040026 | 0.040941 | 0.041757 | 0.043316 | 0.044067 | 0.043291 | 0.040403 | 0.035646 | -0.0094526 | -0.13446 | -0.2284 | -0.50023 | 10.5 | 1.4035 | 1.3746 | 1.3454 | 1.3156 | 1.2855 | 1.2552 | 1.2248 | 1.1942 | 1.1635 | 1.1326 | 1.1019 | 1.0252 | 0.94783 | 0.86422 | 0.76994 | 0.66714 | 0.08374 | -0.68497 | -0.80509 | -0.48256
11 | 0.26542 | 0.28673 | 0.30714 | 0.32644 | 0.34438 | 0.36104 | 0.3764 | 0.39058 | 0.40329 | 0.41466 | 0.42469 | 0.44426 | 0.45448 | 0.44705 | 0.41379 | 0.35699 | -0.18993 | -1.6429 | -2.7075 | -6.0261 | 11 | 0.024129 | 0.026066 | 0.027922 | 0.029677 | 0.031307 | 0.032822 | 0.034218 | 0.035507 | 0.036663 | 0.037696 | 0.038608 | 0.040387 | 0.041317 | 0.040641 | 0.037617 | 0.032454 | -0.017266 | -0.14935 | -0.24614 | -0.54783 | 11 | 1.4574 | 1.4254 | 1.3932 | 1.3607 | 1.3278 | 1.2946 | 1.2612 | 1.2279 | 1.1942 | 1.1605 | 1.1268 | 1.0429 | 0.95888 | 0.86843 | 0.76559 | 0.65218 | 0.006514 | -0.77644 | -0.88639 | -0.53781
11.5 | 0.22488 | 0.24946 | 0.27294 | 0.29534 | 0.31616 | 0.33555 | 0.35347 | 0.36985 | 0.38479 | 0.39809 | 0.40998 | 0.43254 | 0.44507 | 0.43776 | 0.40017 | 0.33497 | -0.29791 | -1.8946 | -3.0397 | -6.8691 | 11.5 | 0.019555 | 0.021692 | 0.023734 | 0.025681 | 0.027493 | 0.029178 | 0.030736 | 0.032161 | 0.03346 | 0.034616 | 0.03565 | 0.037612 | 0.038702 | 0.038066 | 0.034798 | 0.029128 | -0.025906 | -0.16475 | -0.26432 | -0.59732 | 11.5 | 1.5094 | 1.4746 | 1.4394 | 1.4039 | 1.368 | 1.3319 | 1.2955 | 1.2589 | 1.2224 | 1.1857 | 1.1491 | 1.0574 | 0.96649 | 0.86892 | 0.7563 | 0.63126 | -0.081391 | -0.87099 | -0.97116 | -0.59535
12 | 0.18223 | 0.20971 | 0.23649 | 0.262 | 0.28599 | 0.30849 | 0.32912 | 0.348 | 0.36517 | 0.38059 | 0.39415 | 0.42033 | 0.43425 | 0.42627 | 0.38268 | 0.30678 | -0.42665 | -2.1683 | -3.3952 | -7.7838 | 12 | 0.015186 | 0.017475 | 0.019707 | 0.021833 | 0.023833 | 0.025708 | 0.027427 | 0.029 | 0.030431 | 0.031716 | 0.032846 | 0.035027 | 0.036187 | 0.035522 | 0.03189 | 0.025565 | -0.035554 | -0.18069 | -0.28293 | -0.64865 | 12 | 1.5585 | 1.5215 | 1.4835 | 1.4449 | 1.406 | 1.3669 | 1.3274 | 1.2877 | 1.2479 | 1.208 | 1.1682 | 1.0689 | 0.97036 | 0.86488 | 0.74137 | 0.60309 | -0.18 | -0.96971 | -1.0594 | -0.65511
Wind speed 11 m/s
Power Coefficient [-] | [20 empty] | Torque Coefficient [-] | [20 empty] | Thrust Coefficient [-]
TSR\Pitch [deg] | -4 | -3.6 | -3.2 | -2.8 | -2.4 | -2 | -1.6 | -1.2 | -0.8 | -0.4 | 0 | 1 | 2 | 3 | 4 | 5 | 10 | 20 | 30 | 50 | TSR\Pitch [deg] | -4 | -3.6 | -3.2 | -2.8 | -2.4 | -2 | -1.6 | -1.2 | -0.8 | -0.4 | 0 | 1 | 2 | 3 | 4 | 5 | 10 | 20 | 30 | 50 | TSR\Pitch [deg] | -4 | -3.6 | -3.2 | -2.8 | -2.4 | -2 | -1.6 | -1.2 | -0.8 | -0.4 | 0 | 1 | 2 | 3 | 4 | 5 | 10 | 20 | 30 | 50
3 | 0.027278 | 0.029326 | 0.031367 | 0.033404 | 0.035437 | 0.037467 | 0.039495 | 0.04152 | 0.043543 | 0.045567 | 0.047592 | 0.052614 | 0.057695 | 0.062998 | 0.068178 | 0.073423 | 0.099988 | 0.093238 | 0.0051196 | -0.13375 | 3 | 0.0090928 | 0.0097752 | 0.010456 | 0.011135 | 0.011812 | 0.012489 | 0.013165 | 0.01384 | 0.014514 | 0.015189 | 0.015864 | 0.017538 | 0.019232 | 0.020999 | 0.022726 | 0.024474 | 0.033329 | 0.031079 | 0.0017065 | -0.044582 | 3 | 0.21544 | 0.21536 | 0.21528 | 0.21522 | 0.21518 | 0.21516 | 0.21515 | 0.21515 | 0.21517 | 0.21521 | 0.21526 | 0.21542 | 0.2158 | 0.21652 | 0.21717 | 0.21804 | 0.22192 | 0.18641 | 0.089189 | 0.0083245
4 | 0.065647 | 0.069715 | 0.073738 | 0.077882 | 0.082136 | 0.086408 | 0.090605 | 0.094721 | 0.098751 | 0.10279 | 0.10694 | 0.1179 | 0.13048 | 0.14309 | 0.15332 | 0.16166 | 0.1848 | 0.071206 | -0.10357 | -0.29201 | 4 | 0.016412 | 0.017429 | 0.018435 | 0.01947 | 0.020534 | 0.021602 | 0.022651 | 0.02368 | 0.024688 | 0.025698 | 0.026735 | 0.029475 | 0.03262 | 0.035774 | 0.03833 | 0.040416 | 0.0462 | 0.017802 | -0.025892 | -0.073002 | 4 | 0.29593 | 0.29631 | 0.29668 | 0.29723 | 0.29797 | 0.29875 | 0.29947 | 0.30016 | 0.30078 | 0.30147 | 0.30233 | 0.30523 | 0.30896 | 0.31215 | 0.3134 | 0.31365 | 0.30588 | 0.16083 | 0.00032022 | -0.027317
5 | 0.12306 | 0.13002 | 0.13698 | 0.14404 | 0.15114 | 0.159 | 0.1675 | 0.17625 | 0.18525 | 0.1943 | 0.20317 | 0.22197 | 0.23845 | 0.25442 | 0.26808 | 0.2778 | 0.23399 | -0.01023 | -0.2682 | -0.5635 | 5 | 0.024612 | 0.026004 | 0.027397 | 0.028809 | 0.030229 | 0.031801 | 0.0335 | 0.035251 | 0.037051 | 0.038859 | 0.040633 | 0.044394 | 0.047689 | 0.050884 | 0.053617 | 0.055561 | 0.046798 | -0.002046 | -0.053639 | -0.1127 | 5 | 0.40768 | 0.40895 | 0.41034 | 0.41201 | 0.41386 | 0.41611 | 0.41868 | 0.42129 | 0.42401 | 0.42663 | 0.42854 | 0.43171 | 0.4344 | 0.43885 | 0.44232 | 0.44202 | 0.35763 | 0.080236 | -0.10397 | -0.075178
6 | 0.19888 | 0.21283 | 0.22721 | 0.24171 | 0.25645 | 0.26991 | 0.28256 | 0.29573 | 0.31116 | 0.32475 | 0.33566 | 0.36098 | 0.3762 | 0.37955 | 0.37207 | 0.35779 | 0.23556 | -0.147 | -0.49125 | -0.97278 | 6 | 0.033147 | 0.035472 | 0.037868 | 0.040285 | 0.042742 | 0.044986 | 0.047093 | 0.049288 | 0.051859 | 0.054125 | 0.055944 | 0.060164 | 0.062699 | 0.063258 | 0.062012 | 0.059631 | 0.039259 | -0.0245 | -0.081875 | -0.16213 | 6 | 0.55444 | 0.55877 | 0.56333 | 0.56752 | 0.57104 | 0.57413 | 0.5771 | 0.58126 | 0.58864 | 0.59466 | 0.59898 | 0.60798 | 0.60731 | 0.59456 | 0.5714 | 0.54246 | 0.36259 | -0.038384 | -0.21703 | -0.13312
7 | 0.32108 | 0.34292 | 0.36016 | 0.37584 | 0.392 | 0.41186 | 0.42417 | 0.43302 | 0.43941 | 0.44468 | 0.44829 | 0.4503 | 0.44315 | 0.42997 | 0.41071 | 0.38668 | 0.20717 | -0.32908 | -0.77899 | -1.5445 | 7 | 0.045869 | 0.048989 | 0.051451 | 0.053691 | 0.056001 | 0.058838 | 0.060596 | 0.06186 | 0.062772 | 0.063526 | 0.064041 | 0.064329 | 0.063307 | 0.061425 | 0.058672 | 0.05524 | 0.029595 | -0.047011 | -0.11128 | -0.22064 | 7 | 0.76564 | 0.77648 | 0.78206 | 0.78593 | 0.79164 | 0.80192 | 0.80364 | 0.80157 | 0.79725 | 0.79172 | 0.78377 | 0.75722 | 0.72257 | 0.68337 | 0.63973 | 0.59335 | 0.33345 | -0.16959 | -0.34004 | -0.20108
7.5 | 0.37759 | 0.39787 | 0.4142 | 0.42632 | 0.43462 | 0.44284 | 0.45033 | 0.45646 | 0.46135 | 0.46419 | 0.46576 | 0.46534 | 0.45748 | 0.4423 | 0.42089 | 0.39344 | 0.1813 | -0.43977 | -0.94868 | -1.8985 | 7.5 | 0.050345 | 0.053049 | 0.055226 | 0.056842 | 0.057949 | 0.059046 | 0.060043 | 0.060862 | 0.061514 | 0.061892 | 0.062101 | 0.062045 | 0.060997 | 0.058973 | 0.056119 | 0.052458 | 0.024173 | -0.058637 | -0.12649 | -0.25313 | 7.5 | 0.89673 | 0.90513 | 0.90823 | 0.90656 | 0.90046 | 0.8948 | 0.8877 | 0.87809 | 0.86692 | 0.85442 | 0.84112 | 0.80418 | 0.76137 | 0.71395 | 0.66315 | 0.60892 | 0.30652 | -0.24039 | -0.40546 | -0.23887
8 | 0.40446 | 0.41464 | 0.42481 | 0.43499 | 0.44362 | 0.45138 | 0.45648 | 0.46098 | 0.46479 | 0.46824 | 0.47082 | 0.47271 | 0.46614 | 0.45051 | 0.42698 | 0.39599 | 0.14608 | -0.56502 | -1.1353 | -2.3016 | 8 | 0.050557 | 0.05183 | 0.053101 | 0.054374 | 0.055453 | 0.056422 | 0.05706 | 0.057623 | 0.058099 | 0.05853 | 0.058853 | 0.059089 | 0.058268 | 0.056314 | 0.053372 | 0.049499 | 0.01826 | -0.070627 | -0.14191 | -0.2877 | 8 | 1.0117 | 1.0037 | 0.99592 | 0.98742 | 0.97582 | 0.96404 | 0.94944 | 0.93425 | 0.91852 | 0.90287 | 0.88636 | 0.84257 | 0.79356 | 0.73918 | 0.68075 | 0.6186 | 0.27043 | -0.31432 | -0.47308 | -0.27916
8.5 | 0.40012 | 0.41211 | 0.42159 | 0.42981 | 0.43753 | 0.44442 | 0.45064 | 0.45659 | 0.46175 | 0.46629 | 0.47015 | 0.47503 | 0.47046 | 0.45497 | 0.42913 | 0.39423 | 0.10042 | -0.70586 | -1.3383 | -2.7564 | 8.5 | 0.047073 | 0.048483 | 0.049599 | 0.050566 | 0.051474 | 0.052284 | 0.053017 | 0.053717 | 0.054323 | 0.054858 | 0.055311 | 0.055886 | 0.055348 | 0.053526 | 0.050486 | 0.04638 | 0.011814 | -0.083042 | -0.15744 | -0.32428 | 8.5 | 1.0945 | 1.0816 | 1.0668 | 1.0508 | 1.0346 | 1.017 | 0.99906 | 0.98121 | 0.96254 | 0.94368 | 0.92482 | 0.87495 | 0.81995 | 0.75902 | 0.6927 | 0.62226 | 0.22482 | -0.39099 | -0.54231 | -0.32192
9 | 0.38396 | 0.39548 | 0.40592 | 0.41576 | 0.42484 | 0.43362 | 0.44134 | 0.44839 | 0.45473 | 0.46037 | 0.46551 | 0.47331 | 0.47086 | 0.45581 | 0.42789 | 0.38803 | 0.042234 | -0.86354 | -1.5573 | -3.2655 | 9 | 0.042662 | 0.043942 | 0.045102 | 0.046196 | 0.047205 | 0.04818 | 0.049038 | 0.049821 | 0.050526 | 0.051152 | 0.051723 | 0.05259 | 0.052318 | 0.050645 | 0.047544 | 0.043115 | 0.0046927 | -0.095949 | -0.17303 | -0.36283 | 9 | 1.1602 | 1.1422 | 1.1233 | 1.1039 | 1.0841 | 1.0644 | 1.0434 | 1.0222 | 1.0008 | 0.97912 | 0.95769 | 0.90178 | 0.84077 | 0.77343 | 0.6996 | 0.61992 | 0.16861 | -0.47034 | -0.61292 | -0.36706
9.5 | 0.36021 | 0.37356 | 0.38618 | 0.39817 | 0.40904 | 0.41916 | 0.4285 | 0.43704 | 0.44474 | 0.45174 | 0.45774 | 0.46838 | 0.46887 | 0.45407 | 0.42311 | 0.37733 | -0.030717 | -1.0392 | -1.793 | -3.8312 | 9.5 | 0.037917 | 0.039323 | 0.040651 | 0.041913 | 0.043057 | 0.044122 | 0.045105 | 0.046004 | 0.046815 | 0.047551 | 0.048184 | 0.049303 | 0.049355 | 0.047797 | 0.044538 | 0.039719 | -0.0032333 | -0.10939 | -0.18873 | -0.40329 | 9.5 | 1.2167 | 1.1957 | 1.1739 | 1.1519 | 1.129 | 1.1057 | 1.0822 | 1.0584 | 1.0343 | 1.0102 | 0.98572 | 0.92372 | 0.85756 | 0.78347 | 0.70091 | 0.61141 | 0.10086 | -0.55248 | -0.6852 | -0.41455
10 | 0.33247 | 0.34789 | 0.36277 | 0.37661 | 0.38979 | 0.40188 | 0.41305 | 0.42329 | 0.43255 | 0.44081 | 0.44827 | 0.46167 | 0.46473 | 0.44966 | 0.41452 | 0.36116 | -0.12129 | -1.2339 | -2.0463 | -4.4561 | 10 | 0.033247 | 0.034789 | 0.036277 | 0.037661 | 0.038979 | 0.040188 | 0.041305 | 0.042329 | 0.043255 | 0.044081 | 0.044827 | 0.046167 | 0.046473 | 0.044966 | 0.041452 | 0.036116 | -0.012129 | -0.12339 | -0.20463 | -0.44561 | 10 | 1.2689 | 1.2445 | 1.2199 | 1.1947 | 1.1693 | 1.1434 | 1.1172 | 1.0907 | 1.0641 | 1.0372 | 1.0104 | 0.94194 | 0.86991 | 0.78842 | 0.69643 | 0.59556 | 0.020614 | -0.6377 | -0.75953 | -0.46431
10.5 | 0.30106 | 0.31926 | 0.33674 | 0.35308 | 0.36843 | 0.38275 | 0.39593 | 0.40799 | 0.41891 | 0.42868 | 0.43738 | 0.45383 | 0.45887 | 0.44258 | 0.40135 | 0.33833 | -0.23367 | -1.4479 | -2.3192 | -5.1424 | 10.5 | 0.028672 | 0.030406 | 0.032071 | 0.033627 | 0.035089 | 0.036452 | 0.037708 | 0.038856 | 0.039896 | 0.040826 | 0.041655 | 0.043222 | 0.043701 | 0.04215 | 0.038224 | 0.032222 | -0.022254 | -0.1379 | -0.22088 | -0.48976 | 10.5 | 1.3175 | 1.2904 | 1.263 | 1.2351 | 1.2069 | 1.1783 | 1.1494 | 1.1203 | 1.0909 | 1.0612 | 1.0315 | 0.95641 | 0.87776 | 0.78806 | 0.68486 | 0.57128 | -0.072472 | -0.72534 | -0.83668 | -0.5163
11 | 0.26639 | 0.28766 | 0.30808 | 0.32741 | 0.34534 | 0.36202 | 0.37744 | 0.39169 | 0.40444 | 0.41584 | 0.42591 | 0.44496 | 0.45165 | 0.43208 | 0.38285 | 0.30694 | -0.36651 | -1.6819 | -2.6124 | -5.8926 | 11 | 0.024217 | 0.026151 | 0.028008 | 0.029764 | 0.031395 | 0.032911 | 0.034313 | 0.035608 | 0.036767 | 0.037803 | 0.038719 | 0.040451 | 0.04106 | 0.03928 | 0.034804 | 0.027903 | -0.033319 | -0.1529 | -0.23749 | -0.53569 | 11 | 1.3627 | 1.3329 | 1.303 | 1.2726 | 1.2417 | 1.2104 | 1.1787 | 1.1468 | 1.1145 | 1.082 | 1.0492 | 0.96654 | 0.88079 | 0.78123 | 0.66541 | 0.53666 | -0.17511 | -0.81565 | -0.91685 | -0.57045
11.5 | 0.23008 | 0.25469 | 0.27811 | 0.3004 | 0.32115 | 0.34047 | 0.35829 | 0.37458 | 0.38946 | 0.40264 | 0.41426 | 0.43576 | 0.44283 | 0.41788 | 0.35721 | 0.26407 | -0.51251 | -1.9365 | -2.9269 | -6.7088 | 11.5 | 0.020007 | 0.022147 | 0.024183 | 0.026121 | 0.027926 | 0.029606 | 0.031155 | 0.032572 | 0.033866 | 0.035012 | 0.036023 | 0.037892 | 0.038507 | 0.036337 | 0.031062 | 0.022963 | -0.044566 | -0.16839 | -0.25451 | -0.58338 | 11.5 | 1.4061 | 1.3737 | 1.3408 | 1.3077 | 1.2739 | 1.2396 | 1.205 | 1.17 | 1.1347 | 1.099 | 1.0631 | 0.97227 | 0.87852 | 0.76722 | 0.63619 | 0.48941 | -0.2769 | -0.90887 | -1.0003 | -0.62672
12 | 0.19214 | 0.22026 | 0.2471 | 0.2725 | 0.29631 | 0.31856 | 0.33897 | 0.35765 | 0.37447 | 0.38937 | 0.40237 | 0.42613 | 0.43219 | 0.39818 | 0.32145 | 0.20523 | -0.66831 | -2.2135 | -3.2627 | -7.5935 | 12 | 0.016012 | 0.018355 | 0.020592 | 0.022708 | 0.024692 | 0.026547 | 0.028248 | 0.029804 | 0.031206 | 0.032447 | 0.033531 | 0.035511 | 0.036016 | 0.033181 | 0.026787 | 0.017103 | -0.055693 | -0.18446 | -0.27189 | -0.63279 | 12 | 1.447 | 1.412 | 1.3763 | 1.34 | 1.3031 | 1.2659 | 1.228 | 1.1897 | 1.1509 | 1.1117 | 1.0723 | 0.97299 | 0.86999 | 0.74405 | 0.59439 | 0.4262 | -0.3752 | -1.0061 | -1.0869 | -0.68503
Wind speed 13 m/s
Power Coefficient [-] | [20 empty] | Torque Coefficient [-] | [20 empty] | Thrust Coefficient [-]
TSR\Pitch [deg] | -4 | -3.6 | -3.2 | -2.8 | -2.4 | -2 | -1.6 | -1.2 | -0.8 | -0.4 | 0 | 1 | 2 | 3 | 4 | 5 | 10 | 20 | 30 | 50 | TSR\Pitch [deg] | -4 | -3.6 | -3.2 | -2.8 | -2.4 | -2 | -1.6 | -1.2 | -0.8 | -0.4 | 0 | 1 | 2 | 3 | 4 | 5 | 10 | 20 | 30 | 50 | TSR\Pitch [deg] | -4 | -3.6 | -3.2 | -2.8 | -2.4 | -2 | -1.6 | -1.2 | -0.8 | -0.4 | 0 | 1 | 2 | 3 | 4 | 5 | 10 | 20 | 30 | 50
3 | 0.027694 | 0.029728 | 0.031757 | 0.03378 | 0.0358 | 0.037816 | 0.039829 | 0.04184 | 0.043848 | 0.045856 | 0.047866 | 0.052855 | 0.057892 | 0.063162 | 0.068317 | 0.073517 | 0.1002 | 0.093111 | 0.0041371 | -0.13342 | 3 | 0.0092313 | 0.0099094 | 0.010586 | 0.01126 | 0.011933 | 0.012605 | 0.013276 | 0.013947 | 0.014616 | 0.015285 | 0.015955 | 0.017618 | 0.019297 | 0.021054 | 0.022772 | 0.024506 | 0.033402 | 0.031037 | 0.001379 | -0.044474 | 3 | 0.19422 | 0.19414 | 0.19407 | 0.19401 | 0.19396 | 0.19394 | 0.19393 | 0.19394 | 0.19396 | 0.19399 | 0.19404 | 0.1942 | 0.19456 | 0.19527 | 0.19592 | 0.19676 | 0.20082 | 0.16479 | 0.066864 | -0.013302
4 | 0.066374 | 0.070397 | 0.07438 | 0.078463 | 0.082666 | 0.086899 | 0.09106 | 0.095142 | 0.099142 | 0.10316 | 0.10726 | 0.118 | 0.13035 | 0.14299 | 0.1536 | 0.1621 | 0.18549 | 0.068816 | -0.10454 | -0.2904 | 4 | 0.016593 | 0.017599 | 0.018595 | 0.019616 | 0.020666 | 0.021725 | 0.022765 | 0.023785 | 0.024786 | 0.025791 | 0.026815 | 0.0295 | 0.032588 | 0.035746 | 0.038401 | 0.040524 | 0.046373 | 0.017204 | -0.026135 | -0.072599 | 4 | 0.27506 | 0.27543 | 0.27579 | 0.27631 | 0.27702 | 0.27779 | 0.27851 | 0.27918 | 0.2798 | 0.28049 | 0.28131 | 0.28409 | 0.28773 | 0.29109 | 0.29257 | 0.29293 | 0.28531 | 0.13686 | -0.021652 | -0.049029
5 | 0.12418 | 0.13108 | 0.13796 | 0.14491 | 0.15191 | 0.15954 | 0.16786 | 0.1765 | 0.18538 | 0.19437 | 0.20335 | 0.22262 | 0.23942 | 0.25534 | 0.26906 | 0.27881 | 0.23294 | -0.018772 | -0.2678 | -0.55892 | 5 | 0.024836 | 0.026217 | 0.027593 | 0.028982 | 0.030382 | 0.031908 | 0.033572 | 0.035299 | 0.037076 | 0.038873 | 0.04067 | 0.044524 | 0.047884 | 0.051068 | 0.053813 | 0.055762 | 0.046587 | -0.0037543 | -0.053559 | -0.11178 | 5 | 0.38696 | 0.38823 | 0.38958 | 0.39118 | 0.39297 | 0.3951 | 0.39757 | 0.40015 | 0.40283 | 0.40549 | 0.40759 | 0.41101 | 0.41406 | 0.41865 | 0.42224 | 0.42196 | 0.33502 | 0.050774 | -0.12513 | -0.096883
6 | 0.20104 | 0.21489 | 0.22909 | 0.24368 | 0.25836 | 0.27182 | 0.28466 | 0.2992 | 0.31265 | 0.32591 | 0.33716 | 0.36243 | 0.37604 | 0.37831 | 0.37025 | 0.35574 | 0.23034 | -0.15956 | -0.48684 | -0.96222 | 6 | 0.033506 | 0.035815 | 0.038181 | 0.040613 | 0.04306 | 0.045304 | 0.047443 | 0.049867 | 0.052108 | 0.054319 | 0.056193 | 0.060404 | 0.062673 | 0.063052 | 0.061709 | 0.05929 | 0.03839 | -0.026593 | -0.08114 | -0.16037 | 6 | 0.5333 | 0.53761 | 0.54207 | 0.54624 | 0.54977 | 0.55289 | 0.55622 | 0.56216 | 0.56747 | 0.57364 | 0.57859 | 0.58785 | 0.58564 | 0.57173 | 0.54798 | 0.51869 | 0.33491 | -0.067509 | -0.23684 | -0.15471
7 | 0.32683 | 0.34643 | 0.36285 | 0.37807 | 0.39803 | 0.41207 | 0.42275 | 0.43066 | 0.43691 | 0.44148 | 0.44448 | 0.44494 | 0.43781 | 0.42463 | 0.40538 | 0.38112 | 0.19242 | -0.34487 | -0.76722 | -1.5232 | 7 | 0.046689 | 0.049489 | 0.051836 | 0.05401 | 0.056862 | 0.058867 | 0.060393 | 0.061523 | 0.062416 | 0.063069 | 0.063497 | 0.063563 | 0.062545 | 0.060661 | 0.057912 | 0.054446 | 0.027489 | -0.049267 | -0.1096 | -0.2176 | 7 | 0.74491 | 0.75336 | 0.75802 | 0.76251 | 0.77336 | 0.77749 | 0.77779 | 0.77496 | 0.77045 | 0.76393 | 0.75524 | 0.72773 | 0.69322 | 0.65423 | 0.61072 | 0.56408 | 0.29482 | -0.19742 | -0.35836 | -0.22234
7.5 | 0.38329 | 0.3996 | 0.41247 | 0.42275 | 0.4312 | 0.43969 | 0.44618 | 0.45174 | 0.45516 | 0.45746 | 0.45901 | 0.45852 | 0.45052 | 0.43533 | 0.41371 | 0.38559 | 0.15799 | -0.45781 | -0.93189 | -1.8696 | 7.5 | 0.051106 | 0.05328 | 0.054996 | 0.056367 | 0.057494 | 0.058625 | 0.059491 | 0.060231 | 0.060688 | 0.060995 | 0.061202 | 0.061136 | 0.060069 | 0.058045 | 0.055162 | 0.051412 | 0.021065 | -0.061042 | -0.12425 | -0.24928 | 7.5 | 0.87502 | 0.87868 | 0.87829 | 0.8751 | 0.86942 | 0.86398 | 0.85491 | 0.84491 | 0.83296 | 0.82031 | 0.80717 | 0.77066 | 0.72833 | 0.68137 | 0.63059 | 0.57573 | 0.25866 | -0.26792 | -0.42301 | -0.25982
8 | 0.39979 | 0.41072 | 0.42101 | 0.43014 | 0.43752 | 0.44368 | 0.44894 | 0.45346 | 0.45734 | 0.46096 | 0.4635 | 0.465 | 0.45808 | 0.44201 | 0.41788 | 0.38511 | 0.11039 | -0.58555 | -1.1126 | -2.2632 | 8 | 0.049973 | 0.05134 | 0.052626 | 0.053767 | 0.05469 | 0.05546 | 0.056118 | 0.056683 | 0.057168 | 0.05762 | 0.057938 | 0.058124 | 0.05726 | 0.055251 | 0.052235 | 0.048138 | 0.013798 | -0.073193 | -0.13907 | -0.2829 | 8 | 0.9743 | 0.96745 | 0.95896 | 0.94824 | 0.93602 | 0.92334 | 0.90927 | 0.89452 | 0.87914 | 0.86407 | 0.84802 | 0.80507 | 0.75675 | 0.70266 | 0.64405 | 0.58015 | 0.21003 | -0.3414 | -0.48984 | -0.29971
8.5 | 0.3944 | 0.40418 | 0.41331 | 0.42153 | 0.4293 | 0.43632 | 0.44289 | 0.44904 | 0.45426 | 0.45889 | 0.46282 | 0.46721 | 0.46173 | 0.44495 | 0.41717 | 0.37915 | 0.046813 | -0.72911 | -1.3085 | -2.7066 | 8.5 | 0.0464 | 0.047551 | 0.048625 | 0.049591 | 0.050506 | 0.051332 | 0.052105 | 0.052828 | 0.053442 | 0.053987 | 0.054449 | 0.054966 | 0.054321 | 0.052347 | 0.049078 | 0.044606 | 0.0055074 | -0.085778 | -0.15395 | -0.31842 | 8.5 | 1.0467 | 1.0324 | 1.0179 | 1.0025 | 0.98672 | 0.97011 | 0.95315 | 0.93616 | 0.91824 | 0.90022 | 0.88218 | 0.83356 | 0.77908 | 0.71781 | 0.65002 | 0.5767 | 0.14766 | -0.4175 | -0.55837 | -0.34193
9 | 0.37584 | 0.3871 | 0.39764 | 0.40756 | 0.41684 | 0.42565 | 0.4338 | 0.44112 | 0.44773 | 0.45372 | 0.45856 | 0.46604 | 0.46185 | 0.44414 | 0.4124 | 0.36684 | -0.036302 | -0.88963 | -1.5197 | -3.202 | 9 | 0.04176 | 0.043011 | 0.044183 | 0.045285 | 0.046316 | 0.047294 | 0.0482 | 0.049013 | 0.049748 | 0.050414 | 0.050951 | 0.051782 | 0.051317 | 0.049349 | 0.045822 | 0.04076 | -0.0040336 | -0.098847 | -0.16886 | -0.35578 | 9 | 1.1018 | 1.0845 | 1.0668 | 1.0487 | 1.0299 | 1.011 | 0.99177 | 0.97188 | 0.95166 | 0.93138 | 0.91037 | 0.8563 | 0.79522 | 0.72643 | 0.64936 | 0.56457 | 0.070091 | -0.49615 | -0.62827 | -0.38641
9.5 | 0.35311 | 0.36616 | 0.37878 | 0.39073 | 0.40197 | 0.4123 | 0.42188 | 0.43069 | 0.43869 | 0.44595 | 0.45208 | 0.46223 | 0.45983 | 0.44001 | 0.4022 | 0.3471 | -0.14293 | -1.0684 | -1.7464 | -3.7518 | 9.5 | 0.03717 | 0.038543 | 0.039871 | 0.04113 | 0.042313 | 0.0434 | 0.044408 | 0.045336 | 0.046178 | 0.046942 | 0.047588 | 0.048656 | 0.048403 | 0.046317 | 0.042337 | 0.036536 | -0.015045 | -0.11246 | -0.18383 | -0.39493 | 9.5 | 1.1506 | 1.1305 | 1.1102 | 1.0896 | 1.0686 | 1.047 | 1.0249 | 1.0026 | 0.97999 | 0.95725 | 0.93393 | 0.87356 | 0.80638 | 0.72872 | 0.64037 | 0.54245 | -0.022052 | -0.57752 | -0.69972 | -0.43307
10 | 0.32683 | 0.34229 | 0.35725 | 0.3712 | 0.38453 | 0.39682 | 0.40819 | 0.41862 | 0.42811 | 0.43662 | 0.4443 | 0.45708 | 0.45559 | 0.43199 | 0.38554 | 0.31666 | -0.26732 | -1.2662 | -1.9914 | -4.3582 | 10 | 0.032683 | 0.034229 | 0.035725 | 0.03712 | 0.038453 | 0.039682 | 0.040819 | 0.041862 | 0.042811 | 0.043662 | 0.04443 | 0.045708 | 0.045559 | 0.043199 | 0.038554 | 0.031666 | -0.026732 | -0.12662 | -0.19914 | -0.43582 | 10 | 1.1946 | 1.1722 | 1.1496 | 1.1262 | 1.1028 | 1.0787 | 1.0542 | 1.0294 | 1.0043 | 0.97873 | 0.95315 | 0.88617 | 0.81163 | 0.72338 | 0.62152 | 0.5072 | -0.11992 | -0.6618 | -0.77311 | -0.48188
10.5 | 0.29837 | 0.31657 | 0.33409 | 0.35053 | 0.36597 | 0.38037 | 0.39369 | 0.40592 | 0.41701 | 0.42692 | 0.43575 | 0.45107 | 0.4492 | 0.41877 | 0.35911 | 0.2708 | -0.3996 | -1.4832 | -2.2555 | -5.0233 | 10.5 | 0.028416 | 0.03015 | 0.031818 | 0.033384 | 0.034854 | 0.036225 | 0.037495 | 0.038659 | 0.039715 | 0.040659 | 0.0415 | 0.042959 | 0.04278 | 0.039882 | 0.034201 | 0.025791 | -0.038057 | -0.14126 | -0.21481 | -0.47841 | 10.5 | 1.236 | 1.2111 | 1.186 | 1.1602 | 1.1341 | 1.1074 | 1.0803 | 1.0528 | 1.0248 | 0.99641 | 0.96776 | 0.89347 | 0.81006 | 0.70865 | 0.58939 | 0.45443 | -0.21253 | -0.74824 | -0.8493 | -0.53277
11 | 0.26775 | 0.28903 | 0.30946 | 0.32878 | 0.34675 | 0.3635 | 0.37898 | 0.39328 | 0.40608 | 0.4175 | 0.42743 | 0.44467 | 0.43943 | 0.39763 | 0.31818 | 0.20148 | -0.53885 | -1.5673 | -2.1113 | -5.7495 | 11 | 0.024341 | 0.026275 | 0.028132 | 0.029889 | 0.031522 | 0.033046 | 0.034453 | 0.035753 | 0.036917 | 0.037955 | 0.038857 | 0.040424 | 0.039948 | 0.036148 | 0.028926 | 0.018316 | -0.048986 | -0.14248 | -0.19194 | -0.52268 | 11 | 1.2741 | 1.2468 | 1.2192 | 1.1911 | 1.1622 | 1.1327 | 1.1027 | 1.0724 | 1.0413 | 1.0096 | 0.97751 | 0.8948 | 0.79997 | 0.6811 | 0.53928 | 0.37807 | -0.30051 | -0.78262 | -0.81891 | -0.58567
11.5 | 0.23674 | 0.26137 | 0.28479 | 0.3071 | 0.32783 | 0.34711 | 0.36491 | 0.38115 | 0.39584 | 0.40863 | 0.41975 | 0.43751 | 0.42445 | 0.3638 | 0.25338 | 0.097501 | -0.69008 | -1.6476 | -2.0525 | -6.5388 | 11.5 | 0.020586 | 0.022728 | 0.024764 | 0.026704 | 0.028507 | 0.030184 | 0.031731 | 0.033144 | 0.034421 | 0.035533 | 0.0365 | 0.038044 | 0.036908 | 0.031635 | 0.022033 | 0.0084783 | -0.060007 | -0.14327 | -0.17848 | -0.56859 | 11.5 | 1.3104 | 1.2805 | 1.2499 | 1.2189 | 1.187 | 1.1545 | 1.1212 | 1.0872 | 1.0527 | 1.0173 | 0.98154 | 0.88891 | 0.77834 | 0.63582 | 0.46338 | 0.27162 | -0.38879 | -0.81146 | -0.80097 | -0.64053
12 | 0.20552 | 0.23386 | 0.26077 | 0.28614 | 0.3099 | 0.33209 | 0.35229 | 0.37054 | 0.38677 | 0.40086 | 0.41254 | 0.42866 | 0.39944 | 0.30692 | 0.1495 | -0.054715 | -0.85631 | -1.7179 | -1.4396 | -7.3934 | 12 | 0.017127 | 0.019488 | 0.021731 | 0.023845 | 0.025825 | 0.027674 | 0.029358 | 0.030878 | 0.032231 | 0.033405 | 0.034378 | 0.035722 | 0.033286 | 0.025577 | 0.012458 | -0.0045596 | -0.071359 | -0.14316 | -0.11997 | -0.61611 | 12 | 1.3441 | 1.3112 | 1.2776 | 1.2431 | 1.2078 | 1.1718 | 1.1347 | 1.0967 | 1.0578 | 1.0182 | 0.97792 | 0.87367 | 0.73978 | 0.56294 | 0.35131 | 0.13165 | -0.47933 | -0.83577 | -0.61078 | -0.69732

## BladeExternalGeometry
Eta | Chord | Twist | Pitch Axis | Airfoil Thickness | PreBend | Sweep | AC Axis | LE | TE | Abs thickness
[-] | [mm] | [deg] | (% chord) | [%] | [mm] | [mm] | [%] | [mm] | [mm] | [mm]
0 | 2600 | 20 | 50 | 100 | 0 | 0 | 50 | -1300 | 1300 | 2600
0.01 | 2600 | 19.872 | 49.6519 | 100 | 0 | 0 | 50 | -1290.95 | 1309.05 | 2600
0.02 | 2600 | 19.7257 | 49.3038 | 100 | 0 | 0 | 50 | -1281.9 | 1318.1 | 2600
0.03 | 2620.62 | 19.5646 | 48.5706 | 99.1217 | 0 | 0 | 49.4842 | -1272.85 | 1347.77 | 2597.6033
0.04 | 2680.0668 | 19.3896 | 47.1555 | 96.6787 | 0 | 0 | 48.0613 | -1263.8 | 1416.2668 | 2591.0529
0.05 | 2776.6556 | 19.1977 | 45.1893 | 92.9587 | 0 | 0 | 45.9182 | -1254.75 | 1521.9056 | 2581.1416
0.06 | 2910.5917 | 18.9878 | 42.7989 | 88.2494 | 0 | 0 | 43.2418 | -1245.7 | 1664.8917 | 2568.5805
0.07 | 3032.4361 | 18.7586 | 40.7807 | 82.8388 | 0 | 0 | 40.2187 | -1236.65 | 1795.7861 | 2512.0322
0.08 | 3155.3701 | 18.5087 | 38.9051 | 77.0144 | 0 | 0 | 37.0359 | -1227.6 | 1927.7701 | 2430.0892
0.1 | 3400 | 17.9417 | 35.5735 | 65.2757 | 0 | 0 | 30.9383 | -1209.5 | 2190.5 | 2219.374
0.12 | 3618.0139 | 17.0675 | 32.9297 | 55.3355 | 1.2513 | 0 | 26.4438 | -1191.4 | 2426.6139 | 2002.0454
0.14 | 3803.9226 | 15.8086 | 30.8445 | 49.4379 | 5.456 | 0 | 25 | -1173.3 | 2630.6226 | 1880.5802
0.16 | 3958.6764 | 14.3676 | 29.1815 | 45.9423 | 10.8502 | 0 | 25 | -1155.2 | 2803.4764 | 1818.7072
0.18 | 4083.2253 | 12.9472 | 27.8481 | 43.115 | 17.4659 | 0 | 25 | -1137.1 | 2946.1253 | 1760.4816
0.2 | 4178.5194 | 11.7498 | 26.7798 | 40.9574 | 25.314 | 0 | 25 | -1119 | 3059.5194 | 1711.4137
0.22 | 4245.5088 | 10.7294 | 25.9309 | 39.4364 | 34.4304 | 0 | 25 | -1100.9 | 3144.6088 | 1674.2749
0.24 | 4285.1437 | 9.713 | 25.2687 | 38.2315 | 44.8807 | 0 | 25 | -1082.8 | 3202.3437 | 1638.2748
0.26 | 4298.3943 | 8.7129 | 24.7697 | 37.2277 | 56.7133 | 0 | 25 | -1064.7 | 3233.6943 | 1600.1929
0.28 | 4286.6982 | 7.7417 | 24.4151 | 36.3787 | 69.9493 | 0 | 25 | -1046.6 | 3240.0982 | 1559.4463
0.3 | 4251.9598 | 6.8115 | 24.1888 | 35.6384 | 84.6264 | 0 | 25 | -1028.5 | 3223.4598 | 1515.3304
0.32 | 4196.1038 | 5.9348 | 24.0795 | 34.9606 | 100.822 | 0 | 25 | -1010.4 | 3185.7038 | 1466.9833
0.34 | 4121.0551 | 5.124 | 24.0788 | 34.3407 | 118.6633 | 0 | 25 | -992.3 | 3128.7551 | 1415.201
0.36 | 4028.7384 | 4.3914 | 24.1813 | 33.7883 | 138.0985 | 0 | 25 | -974.2 | 3054.5384 | 1361.2412
0.38 | 3921.0784 | 3.7495 | 24.3836 | 33.2891 | 159.2622 | 0 | 25 | -956.1 | 2964.9784 | 1305.2908
0.4 | 3800 | 3.2106 | 24.6842 | 32.829 | 182.2607 | 0 | 25 | -938 | 2862 | 1247.5028
0.42 | 3667.7423 | 2.7625 | 25.0808 | 32.394 | 207.0292 | 0 | 25 | -919.9 | 2747.8423 | 1188.128
0.44 | 3527.8021 | 2.3793 | 25.5627 | 31.9699 | 233.901 | 0 | 25 | -901.8 | 2626.0021 | 1127.8332
0.46 | 3383.9908 | 2.0521 | 26.1141 | 31.5425 | 262.7016 | 0 | 25 | -883.7 | 2500.2908 | 1067.3951
0.48 | 3240.1197 | 1.7722 | 26.7151 | 31.0978 | 293.7286 | 0 | 25 | -865.6 | 2374.5197 | 1007.6054
0.5 | 3100 | 1.5308 | 27.3387 | 30.6216 | 326.9413 | 0 | 25 | -847.5 | 2252.5 | 949.2697
0.52 | 2966.8089 | 1.3192 | 27.956 | 30.0998 | 362.5452 | 0 | 25 | -829.4 | 2137.4089 | 893.0043
0.54 | 2841.1873 | 1.1286 | 28.555 | 29.5129 | 400.6055 | 0 | 25 | -811.3 | 2029.8873 | 838.5157
0.56 | 2723.142 | 0.95035 | 29.1281 | 28.8582 | 441.2656 | 0 | 25 | -793.2 | 1929.942 | 785.8507
0.58 | 2612.6796 | 0.77564 | 29.6669 | 28.1615 | 484.6779 | 0 | 25 | -775.1 | 1837.5796 | 735.7689
0.6 | 2509.8069 | 0.59572 | 30.1617 | 27.4486 | 530.9433 | 0 | 25 | -757 | 1752.8069 | 688.9063
0.62 | 2414.5307 | 0.42234 | 30.6022 | 26.7456 | 580.2983 | 0 | 25 | -738.9 | 1675.6307 | 645.7801
0.64 | 2326.8577 | 0.26994 | 30.9774 | 26.0785 | 632.8034 | 0 | 25 | -720.8 | 1606.0577 | 606.809
0.66 | 2246.7947 | 0.13385 | 31.2757 | 25.4733 | 688.8004 | 0 | 25 | -702.7 | 1544.0947 | 572.3326
0.68 | 2174.3484 | 0.0094005 | 31.4853 | 24.9554 | 748.2852 | 0 | 25 | -684.6 | 1489.7484 | 542.6179
0.7 | 2109.5256 | -0.10809 | 31.5948 | 24.467 | 811.7616 | 0 | 25 | -666.5 | 1443.0256 | 516.1375
0.72 | 2052.333 | -0.22329 | 31.7922 | 23.9656 | 879.0982 | 0 | 25 | -652.4818 | 1399.8513 | 491.8542
0.74 | 2002.7774 | -0.34088 | 31.7279 | 23.4642 | 951.0694 | 0 | 25 | -635.4398 | 1367.3376 | 469.9355
0.76 | 1960.8656 | -0.46553 | 31.5734 | 22.9757 | 1027.4081 | 0 | 25 | -619.1124 | 1341.7532 | 450.5217
0.78 | 1926.6042 | -0.60191 | 31.261 | 22.5129 | 1109.0095 | 0 | 25 | -602.2761 | 1324.3281 | 433.7347
0.8 | 1900 | -0.75471 | 30.799 | 22.0889 | 1195.8227 | 0 | 25 | -585.1803 | 1314.8197 | 419.6889
0.82 | 1879.2032 | -0.91217 | 30.2115 | 21.7165 | 1288.386 | 0 | 25 | -567.7346 | 1311.4686 | 408.0971
0.84 | 1854.9376 | -1.0697 | 29.5616 | 21.4087 | 1387.4351 | 0 | 25 | -548.3495 | 1306.5881 | 397.1172
0.86 | 1816.0704 | -1.2429 | 28.8736 | 21.1783 | 1493.076 | 0 | 25 | -524.3651 | 1291.7054 | 384.6125
0.88 | 1751.4688 | -1.4471 | 28.2364 | 21.0383 | 1606.2222 | 0 | 25 | -494.5509 | 1256.9179 | 368.4792
0.9 | 1650 | -1.6978 | 27.6742 | 21 | 1727.7789 | 0 | 25 | -456.625 | 1193.375 | 346.5
0.92 | 1500.5312 | -2.0507 | 27.2485 | 21 | 1858.252 | 0 | 25 | -408.8718 | 1091.6594 | 315.1115
0.94 | 1291.9296 | -2.5385 | 26.9167 | 21 | 1998.713 | 0 | 25 | -347.7445 | 944.185 | 271.3052
0.96 | 1013.0624 | -3.1419 | 26.7129 | 21 | 2150.4601 | 0 | 25 | -270.618 | 742.4444 | 212.7431
0.98 | 652.7968 | -3.8416 | 26.4385 | 21 | 2315.0825 | 0 | 25 | -172.5898 | 480.207 | 137.0873
1 | 200 | -4.6185 | 25 | 21 | 2500 | 0 | 25 | -50 | 150 | 42

## Airfoils
Airfoil Name | Span Positioning | Thickness | Reynolds | Aerodynamic Center Position |  | Airfoil Name | Span Positioning | Thickness | Reynolds | Aerodynamic Center Position |  | Airfoil Name | Span Positioning | Thickness | Reynolds | Aerodynamic Center Position |  | Airfoil Name | Span Positioning | Thickness | Reynolds | Aerodynamic Center Position |  | Airfoil Name | Span Positioning | Thickness | Reynolds | Aerodynamic Center Position |  | Airfoil Name | Span Positioning | Thickness | Reynolds | Aerodynamic Center Position |  | Airfoil Name | Span Positioning | Thickness | Reynolds | Aerodynamic Center Position |  | Airfoil Name | Span Positioning | Thickness | Reynolds | Aerodynamic Center Position |  | Airfoil Name | Span Positioning | Thickness | Reynolds | Aerodynamic Center Position
[-] | [%] | [%] | [-] | [%] |  | [-] | [%] | [%] | [-] | [%] |  | [-] | [%] | [%] | [-] | [%] |  | [-] | [%] | [%] | [-] | [%] |  | [-] | [%] | [%] | [-] | [%] |  | [-] | [%] | [%] | [-] | [%] |  | [-] | [%] | [%] | [-] | [%] |  | [-] | [%] | [%] | [-] | [%] |  | [-] | [%] | [%] | [-] | [%]
circle | 0 | 100 | 6000000 | 50 |  | circle | 2 | 100 | 6000000 | 50 |  | FX77-W-500 | 13.7101 | 50 | 3000000 | 25 |  | FX77-W-400 | 21.1789 | 40 | 3000000 | 25 |  | DU00-W2-350 | 31.8808 | 35 | 3000000 | 25 |  | DU97-W-300 | 52.3599 | 30 | 3000000 | 25 |  | DU91-W2-250 | 67.8129 | 25 | 3000000 | 25 |  | DU08-W-210 | 89.6653 | 21 | 6000000 | 25 |  | DU08-W-210 | 100 | 21 | 6000000 | 25
Coordinate X | Coordinate Y | Angle of Attack | Cl | Cd | Cm | Coordinate X | Coordinate Y | Angle of Attack | Cl | Cd | Cm | Coordinate X | Coordinate Y | Angle of Attack | Cl | Cd | Cm | Coordinate X | Coordinate Y | Angle of Attack | Cl | Cd | Cm | Coordinate X | Coordinate Y | Angle of Attack | Cl | Cd | Cm | Coordinate X | Coordinate Y | Angle of Attack | Cl | Cd | Cm | Coordinate X | Coordinate Y | Angle of Attack | Cl | Cd | Cm | Coordinate X | Coordinate Y | Angle of Attack | Cl | Cd | Cm | Coordinate X | Coordinate Y | Angle of Attack | Cl | Cd | Cm
[m] | [m] | [deg] | [-] | [-] | [-] | [m] | [m] | [deg] | [-] | [-] | [-] | [m] | [m] | [deg] | [-] | [-] | [-] | [m] | [m] | [deg] | [-] | [-] | [-] | [m] | [m] | [deg] | [-] | [-] | [-] | [m] | [m] | [deg] | [-] | [-] | [-] | [m] | [m] | [deg] | [-] | [-] | [-] | [m] | [m] | [deg] | [-] | [-] | [-] | [m] | [m] | [deg] | [-] | [-] | [-]
1 | 0 | -180 | 0 | 0.6 | 0 | 1 | 0 | -180 | 0 | 0.6 | 0 | 1 | -0.05944 | -180 | 0 | 0.1546 | 0 | 1 | -0.046552 | -180 | 0 | 0.01 | 0 | 1 | 0.005 | -180 | 0 | 0 | 0 | 1 | 0.0087 | -180 | 0 | 0 | 0 | 1 | 0.0033 | -180 | 0 | 0 | 0 | 1 | 0.001393 | -180 | 0 | 0 | 0 | 1 | 0.001393 | -180 | 0 | 0 | 0
0.9999 | 0.0087 | -175 | 0 | 0.6 | 0 | 0.9999 | 0.0087 | -175 | 0 | 0.6 | 0 | 0.995 | -0.0044404 | -175 | 0.22 | 0.17285 | 0.2 | 0.995 | -0.0015523 | -175 | 0.24645 | 0.01 | 0.2 | 0.9893 | 0.0082 | -175 | 0.21663 | 0.053548 | 0.2 | 0.9935 | 0.0105 | -175 | 0.18301 | 0.046744 | 0.2 | 0.99 | 0.0061 | -175 | 0.18148 | 0.056205 | 0.2 | 0.99 | 0.004032 | -175 | 0.25026 | 0.037696 | 0.2 | 0.99 | 0.004032 | -175 | 0.25026 | 0.037696 | 0.2
0.9997 | 0.0174 | -170 | 0 | 0.6 | 0 | 0.9997 | 0.0174 | -170 | 0 | 0.6 | 0 | 0.99 | 0.05556 | -170 | 0.44 | 0.1911 | 0.4 | 0.98 | 0.017064 | -170 | 0.4929 | 0.01 | 0.4 | 0.9731 | 0.013 | -170 | 0.43326 | 0.1071 | 0.4 | 0.9848 | 0.0129 | -170 | 0.36602 | 0.093488 | 0.4 | 0.98 | 0.0089 | -170 | 0.36295 | 0.11241 | 0.4 | 0.98 | 0.006562 | -170 | 0.50052 | 0.075392 | 0.4 | 0.98 | 0.006562 | -170 | 0.50052 | 0.075392 | 0.4
0.9993 | 0.0262 | -165 | 0 | 0.6 | 0 | 0.9993 | 0.0262 | -165 | 0 | 0.6 | 0 | 0.982 | 0.10556 | -165 | 0.54655 | 0.24365 | 0.3584 | 0.96473 | 0.025483 | -165 | 0.6031 | 0.0521 | 0.35275 | 0.9526 | 0.019 | -165 | 0.61988 | 0.16312 | 0.21212 | 0.9739 | 0.0158 | -165 | 0.54903 | 0.14023 | 0.19412 | 0.97 | 0.0116 | -165 | 0.54443 | 0.16861 | 0.19827 | 0.97 | 0.00907 | -165 | 0.65457 | 0.12387 | 0.15025 | 0.97 | 0.00907 | -165 | 0.65457 | 0.12387 | 0.15025
0.9988 | 0.0349 | -160 | 0 | 0.6 | 0 | 0.9988 | 0.0349 | -160 | 0 | 0.6 | 0 | 0.96035 | 0.11293 | -160 | 0.6531 | 0.2962 | 0.3168 | 0.93533 | 0.034378 | -160 | 0.7133 | 0.0942 | 0.3055 | 0.9305 | 0.0254 | -160 | 0.80649 | 0.21914 | 0.024234 | 0.9613 | 0.0191 | -160 | 0.73204 | 0.18698 | -0.011767 | 0.96 | 0.0142 | -160 | 0.7259 | 0.22482 | -0.0034565 | 0.96 | 0.011554 | -160 | 0.80862 | 0.17235 | -0.099498 | 0.96 | 0.011554 | -160 | 0.80862 | 0.17235 | -0.099498
0.9981 | 0.0436 | -155 | 0 | 0.6 | 0 | 0.9981 | 0.0436 | -155 | 0 | 0.6 | 0 | 0.91484 | 0.12825 | -155 | 0.62745 | 0.3763 | 0.30045 | 0.90441 | 0.044355 | -155 | 0.67505 | 0.1822 | 0.2823 | 0.908 | 0.032 | -155 | 0.76278 | 0.31386 | 0.048277 | 0.9477 | 0.0226 | -155 | 0.7212 | 0.27895 | -0.0084324 | 0.95 | 0.0168 | -155 | 0.73125 | 0.31385 | -0.01941 | 0.95 | 0.014 | -155 | 0.76446 | 0.2689 | -0.06607 | 0.95 | 0.014 | -155 | 0.76446 | 0.2689 | -0.06607
0.9973 | 0.0523 | -150 | 0 | 0.6 | 0 | 0.9973 | 0.0523 | -150 | 0 | 0.6 | 0 | 0.86853 | 0.14443 | -150 | 0.6018 | 0.4564 | 0.2841 | 0.87209 | 0.054738 | -150 | 0.6368 | 0.2702 | 0.2591 | 0.8854 | 0.0387 | -150 | 0.71907 | 0.40857 | 0.072319 | 0.9332 | 0.0262 | -150 | 0.71036 | 0.37093 | -0.0050977 | 0.94 | 0.0194 | -150 | 0.7366 | 0.40288 | -0.035363 | 0.94 | 0.016435 | -150 | 0.72031 | 0.36545 | -0.032643 | 0.94 | 0.016435 | -150 | 0.72031 | 0.36545 | -0.032643
0.9963 | 0.0609 | -145 | 0 | 0.6 | 0 | 0.9963 | 0.0609 | -145 | 0 | 0.6 | 0 | 0.8216 | 0.15956 | -145 | 0.5874 | 0.5539 | 0.28905 | 0.83853 | 0.066169 | -145 | 0.61555 | 0.3785 | 0.26145 | 0.8628 | 0.0454 | -145 | 0.69475 | 0.52451 | 0.094142 | 0.9184 | 0.0298 | -145 | 0.68775 | 0.48904 | 0.02014 | 0.93 | 0.0219 | -145 | 0.70885 | 0.51915 | -0.0083056 | 0.93 | 0.018862 | -145 | 0.69574 | 0.48387 | -0.0075598 | 0.93 | 0.018862 | -145 | 0.69574 | 0.48387 | -0.0075598
0.9951 | 0.0696 | -140 | 0 | 0.6 | 0 | 0.9951 | 0.0696 | -140 | 0 | 0.6 | 0 | 0.77427 | 0.17553 | -140 | 0.573 | 0.6514 | 0.294 | 0.80388 | 0.07782 | -140 | 0.5943 | 0.4868 | 0.2638 | 0.84 | 0.0522 | -140 | 0.67043 | 0.64045 | 0.11596 | 0.9033 | 0.0335 | -140 | 0.66513 | 0.60715 | 0.045378 | 0.92 | 0.0245 | -140 | 0.6811 | 0.63541 | 0.018752 | 0.92 | 0.021282 | -140 | 0.67118 | 0.6023 | 0.017523 | 0.92 | 0.021282 | -140 | 0.67118 | 0.6023 | 0.017523
0.9938 | 0.0782 | -135 | 0 | 0.6 | 0 | 0.9938 | 0.0782 | -135 | 0 | 0.6 | 0 | 0.72674 | 0.19027 | -135 | 0.54675 | 0.7539 | 0.3047 | 0.76828 | 0.090343 | -135 | 0.56365 | 0.6025 | 0.2746 | 0.8169 | 0.0592 | -135 | 0.63573 | 0.76338 | 0.13951 | 0.8882 | 0.0372 | -135 | 0.63152 | 0.73276 | 0.071232 | 0.91 | 0.027 | -135 | 0.64422 | 0.75875 | 0.045476 | 0.91 | 0.023695 | -135 | 0.63633 | 0.72831 | 0.043217 | 0.91 | 0.023695 | -135 | 0.63633 | 0.72831 | 0.043217
0.9924 | 0.0868 | -130 | 0 | 0.6 | 0 | 0.9924 | 0.0868 | -130 | 0 | 0.6 | 0 | 0.67922 | 0.20536 | -130 | 0.5205 | 0.8564 | 0.3154 | 0.73187 | 0.1026 | -130 | 0.533 | 0.7182 | 0.2854 | 0.7937 | 0.0662 | -130 | 0.60104 | 0.88632 | 0.16306 | 0.873 | 0.0409 | -130 | 0.5979 | 0.85838 | 0.097086 | 0.9 | 0.0295 | -130 | 0.60734 | 0.88209 | 0.072199 | 0.9 | 0.026103 | -130 | 0.60148 | 0.85431 | 0.068911 | 0.9 | 0.026103 | -130 | 0.60148 | 0.85431 | 0.068911
0.9908 | 0.0954 | -125 | 0 | 0.6 | 0 | 0.9908 | 0.0954 | -125 | 0 | 0.6 | 0 | 0.63189 | 0.21893 | -125 | 0.47605 | 0.9506 | 0.32595 | 0.69483 | 0.11554 | -125 | 0.48565 | 0.82775 | 0.29825 | 0.7707 | 0.0731 | -125 | 0.54755 | 1.0011 | 0.18718 | 0.8579 | 0.0446 | -125 | 0.54514 | 0.9763 | 0.12363 | 0.875 | 0.0358 | -125 | 0.55239 | 0.99738 | 0.099328 | 0.875 | 0.032092 | -125 | 0.54789 | 0.97269 | 0.09538 | 0.875 | 0.032092 | -125 | 0.54789 | 0.97269 | 0.09538
0.9891 | 0.104 | -120 | 0 | 0.6 | 0 | 0.9891 | 0.104 | -120 | 0 | 0.6 | 0 | 0.58496 | 0.23219 | -120 | 0.4316 | 1.0448 | 0.3365 | 0.65728 | 0.12765 | -120 | 0.4383 | 0.9373 | 0.3111 | 0.7479 | 0.0799 | -120 | 0.49406 | 1.1159 | 0.2113 | 0.8427 | 0.0482 | -120 | 0.49238 | 1.0942 | 0.15018 | 0.85 | 0.042 | -120 | 0.49743 | 1.1127 | 0.12646 | 0.85 | 0.038014 | -120 | 0.4943 | 1.0911 | 0.12185 | 0.85 | 0.038014 | -120 | 0.4943 | 1.0911 | 0.12185
0.9872 | 0.1125 | -115 | 0 | 0.6 | 0 | 0.9872 | 0.1125 | -115 | 0 | 0.6 | 0 | 0.53865 | 0.24262 | -115 | 0.36965 | 1.1184 | 0.34335 | 0.61942 | 0.14042 | -115 | 0.37445 | 1.0279 | 0.3219 | 0.7252 | 0.0866 | -115 | 0.42204 | 1.2085 | 0.23353 | 0.8277 | 0.0519 | -115 | 0.42084 | 1.1902 | 0.17537 | 0.825 | 0.0482 | -115 | 0.42446 | 1.2057 | 0.15214 | 0.825 | 0.043863 | -115 | 0.42221 | 1.1875 | 0.14706 | 0.825 | 0.043863 | -115 | 0.42221 | 1.1875 | 0.14706
0.9851 | 0.121 | -110 | 0 | 0.6 | 0 | 0.9851 | 0.121 | -110 | 0 | 0.6 | 0 | 0.49314 | 0.24976 | -110 | 0.3077 | 1.192 | 0.3502 | 0.5814 | 0.15222 | -110 | 0.3106 | 1.1185 | 0.3327 | 0.7029 | 0.0932 | -110 | 0.35003 | 1.301 | 0.25576 | 0.8126 | 0.0554 | -110 | 0.3493 | 1.2861 | 0.20056 | 0.8 | 0.0543 | -110 | 0.35148 | 1.2987 | 0.17782 | 0.8 | 0.04965 | -110 | 0.35013 | 1.2839 | 0.17226 | 0.8 | 0.04965 | -110 | 0.35013 | 1.2839 | 0.17226
0.983 | 0.1294 | -105 | 0 | 0.6 | 0 | 0.983 | 0.1294 | -105 | 0 | 0.6 | 0 | 0.44863 | 0.25169 | -105 | 0.2332 | 1.2349 | 0.351 | 0.54337 | 0.16428 | -105 | 0.235 | 1.1796 | 0.3385 | 0.6809 | 0.0996 | -105 | 0.26483 | 1.3597 | 0.27333 | 0.7976 | 0.059 | -105 | 0.26438 | 1.3484 | 0.22163 | 0.775 | 0.0603 | -105 | 0.26573 | 1.358 | 0.19935 | 0.775 | 0.055353 | -105 | 0.26489 | 1.3468 | 0.19344 | 0.775 | 0.055353 | -105 | 0.26489 | 1.3468 | 0.19344
0.9806 | 0.1378 | -100 | 0 | 0.6 | 0 | 0.9806 | 0.1378 | -100 | 0 | 0.6 | 0 | 0.40532 | 0.25063 | -100 | 0.1587 | 1.2779 | 0.3518 | 0.50551 | 0.17515 | -100 | 0.1594 | 1.2406 | 0.3443 | 0.659 | 0.1058 | -100 | 0.17963 | 1.4183 | 0.2909 | 0.7826 | 0.0625 | -100 | 0.17945 | 1.4108 | 0.24271 | 0.75 | 0.0662 | -100 | 0.17999 | 1.4172 | 0.22089 | 0.75 | 0.060949 | -100 | 0.17965 | 1.4097 | 0.21462 | 0.75 | 0.060949 | -100 | 0.17965 | 1.4097 | 0.21462
0.9782 | 0.1462 | -95 | 0 | 0.6 | 0 | 0.9782 | 0.1462 | -95 | 0 | 0.6 | 0 | 0.36337 | 0.2452 | -95 | 0.07935 | 1.2839 | 0.3453 | 0.46797 | 0.18575 | -95 | 0.0797 | 1.2653 | 0.34305 | 0.6376 | 0.1118 | -95 | 0.089815 | 1.4357 | 0.30132 | 0.7677 | 0.066 | -95 | 0.089725 | 1.4319 | 0.25701 | 0.725 | 0.072 | -95 | 0.089994 | 1.4351 | 0.2356 | 0.725 | 0.066436 | -95 | 0.089827 | 1.4314 | 0.22908 | 0.725 | 0.066436 | -95 | 0.089827 | 1.4314 | 0.22908
0.9755 | 0.1545 | -90 | 0 | 0.6 | 0 | 0.9755 | 0.1545 | -90 | 0 | 0.6 | 0 | 0.32298 | 0.23726 | -90 | 0 | 1.29 | 0.3388 | 0.43092 | 0.1941 | -90 | 0 | 1.29 | 0.3418 | 0.6165 | 0.1175 | -90 | 0 | 1.4531 | 0.31174 | 0.7528 | 0.0694 | -90 | 0 | 1.4531 | 0.27131 | 0.7 | 0.0777 | -90 | 0 | 1.4531 | 0.25032 | 0.7 | 0.071826 | -90 | 0 | 1.4531 | 0.24354 | 0.7 | 0.071826 | -90 | 0 | 1.4531 | 0.24354
0.9728 | 0.1628 | -85 | 0 | 0.6 | 0 | 0.9728 | 0.1628 | -85 | 0 | 0.6 | 0 | 0.28433 | 0.22556 | -85 | -0.07935 | 1.2839 | 0.33125 | 0.39451 | 0.19981 | -85 | -0.0797 | 1.2653 | 0.3304 | 0.5957 | 0.123 | -85 | -0.089815 | 1.4357 | 0.3159 | 0.7379 | 0.0728 | -85 | -0.089725 | 1.4319 | 0.27748 | 0.675 | 0.0833 | -85 | -0.089994 | 1.4351 | 0.25849 | 0.675 | 0.077113 | -85 | -0.089827 | 1.4314 | 0.24961 | 0.675 | 0.077113 | -85 | -0.089827 | 1.4314 | 0.24961
0.9698 | 0.171 | -80 | 0 | 0.6 | 0 | 0.9698 | 0.171 | -80 | 0 | 0.6 | 0 | 0.24757 | 0.21222 | -80 | -0.1587 | 1.2779 | 0.3237 | 0.35891 | 0.20135 | -80 | -0.1594 | 1.2406 | 0.319 | 0.5752 | 0.1282 | -80 | -0.17963 | 1.4183 | 0.32005 | 0.723 | 0.0761 | -80 | -0.17945 | 1.4108 | 0.28364 | 0.65 | 0.0887 | -80 | -0.17999 | 1.4172 | 0.26667 | 0.65 | 0.082275 | -80 | -0.17965 | 1.4097 | 0.25567 | 0.65 | 0.082275 | -80 | -0.17965 | 1.4097 | 0.25567
0.9668 | 0.1792 | -75 | 0 | 0.6 | 0 | 0.9668 | 0.1792 | -75 | 0 | 0.6 | 0 | 0.21286 | 0.19578 | -75 | -0.2332 | 1.2349 | 0.30935 | 0.32426 | 0.20051 | -75 | -0.235 | 1.1796 | 0.30175 | 0.5549 | 0.1331 | -75 | -0.26483 | 1.3597 | 0.31618 | 0.7082 | 0.0794 | -75 | -0.26438 | 1.3484 | 0.28159 | 0.625 | 0.094 | -75 | -0.26573 | 1.358 | 0.26663 | 0.625 | 0.087285 | -75 | -0.26489 | 1.3468 | 0.25355 | 0.625 | 0.087285 | -75 | -0.26489 | 1.3468 | 0.25355
0.9636 | 0.1873 | -70 | 0 | 0.6 | 0 | 0.9636 | 0.1873 | -70 | 0 | 0.6 | 0 | 0.18035 | 0.17844 | -70 | -0.3077 | 1.192 | 0.295 | 0.2907 | 0.19616 | -70 | -0.3106 | 1.1185 | 0.2845 | 0.535 | 0.1377 | -70 | -0.35003 | 1.301 | 0.31232 | 0.6934 | 0.0826 | -70 | -0.3493 | 1.2861 | 0.27954 | 0.6 | 0.099 | -70 | -0.35148 | 1.2987 | 0.26659 | 0.6 | 0.092116 | -70 | -0.35013 | 1.2839 | 0.25143 | 0.6 | 0.092116 | -70 | -0.35013 | 1.2839 | 0.25143
0.9603 | 0.1954 | -65 | 0 | 0.6 | 0 | 0.9603 | 0.1954 | -65 | 0 | 0.6 | 0 | 0.15017 | 0.15823 | -65 | -0.36965 | 1.1184 | 0.27565 | 0.25838 | 0.18981 | -65 | -0.37445 | 1.0279 | 0.2637 | 0.5155 | 0.142 | -65 | -0.42204 | 1.2085 | 0.30236 | 0.6786 | 0.0858 | -65 | -0.42084 | 1.1902 | 0.27118 | 0.575 | 0.1037 | -65 | -0.42446 | 1.2057 | 0.2602 | 0.575 | 0.096748 | -65 | -0.42221 | 1.1875 | 0.24308 | 0.575 | 0.096748 | -65 | -0.42221 | 1.1875 | 0.24308
0.9568 | 0.2034 | -60 | 0 | 0.6 | 0 | 0.9568 | 0.2034 | -60 | 0 | 0.6 | 0 | 0.12249 | 0.138 | -60 | -0.4316 | 1.0448 | 0.2563 | 0.22747 | 0.18045 | -60 | -0.4383 | 0.9373 | 0.2429 | 0.4963 | 0.146 | -60 | -0.49406 | 1.1159 | 0.2924 | 0.6639 | 0.0889 | -60 | -0.49238 | 1.0942 | 0.26282 | 0.55 | 0.1082 | -60 | -0.49743 | 1.1127 | 0.2538 | 0.55 | 0.10115 | -60 | -0.4943 | 1.0911 | 0.23472 | 0.55 | 0.10115 | -60 | -0.4943 | 1.0911 | 0.23472
0.9532 | 0.2113 | -55 | 0 | 0.6 | 0 | 0.9532 | 0.2113 | -55 | 0 | 0.6 | 0 | 0.097369 | 0.11549 | -55 | -0.47605 | 0.9506 | 0.23435 | 0.19806 | 0.16977 | -55 | -0.48565 | 0.82775 | 0.22125 | 0.4773 | 0.1496 | -55 | -0.54755 | 1.0011 | 0.27948 | 0.6492 | 0.092 | -55 | -0.54514 | 0.9763 | 0.25138 | 0.525 | 0.1124 | -55 | -0.55239 | 0.99738 | 0.24438 | 0.525 | 0.10529 | -55 | -0.54789 | 0.97269 | 0.22345 | 0.525 | 0.10529 | -55 | -0.54789 | 0.97269 | 0.22345
0.9494 | 0.2192 | -50 | 0 | 0.6 | 0 | 0.9494 | 0.2192 | -50 | 0 | 0.6 | 0 | 0.074942 | 0.093757 | -50 | -0.5205 | 0.8564 | 0.2124 | 0.17029 | 0.15662 | -50 | -0.533 | 0.7182 | 0.1996 | 0.4585 | 0.1529 | -50 | -0.60104 | 0.88632 | 0.26655 | 0.6346 | 0.0949 | -50 | -0.5979 | 0.85838 | 0.23995 | 0.5 | 0.1162 | -50 | -0.60734 | 0.88209 | 0.23496 | 0.5 | 0.10912 | -50 | -0.60148 | 0.85431 | 0.21218 | 0.5 | 0.10912 | -50 | -0.60148 | 0.85431 | 0.21218
0.9455 | 0.227 | -45 | 0 | 0.6 | 0 | 0.9455 | 0.227 | -45 | 0 | 0.6 | 0 | 0.05532 | 0.070254 | -45 | -0.54675 | 0.7539 | 0.18985 | 0.14428 | 0.14275 | -45 | -0.56365 | 0.6025 | 0.17925 | 0.44 | 0.1559 | -45 | -0.63992 | 0.76352 | 0.25402 | 0.62 | 0.0978 | -45 | -0.63582 | 0.73279 | 0.22906 | 0.475 | 0.1197 | -45 | -0.64818 | 0.75887 | 0.2263 | 0.475 | 0.11259 | -45 | -0.6405 | 0.72831 | 0.20162 | 0.475 | 0.11259 | -45 | -0.6405 | 0.72831 | 0.20162
0.9415 | 0.2347 | -40 | 0 | 0.6 | 0 | 0.9415 | 0.2347 | -40 | 0 | 0.6 | 0 | 0.038561 | 0.048917 | -40 | -0.573 | 0.6514 | 0.1673 | 0.12014 | 0.12659 | -40 | -0.5943 | 0.4868 | 0.1589 | 0.4216 | 0.1585 | -40 | -0.67043 | 0.64045 | 0.24362 | 0.6054 | 0.1007 | -40 | -0.66513 | 0.60715 | 0.22061 | 0.45 | 0.1227 | -40 | -0.6811 | 0.63541 | 0.22044 | 0.45 | 0.11567 | -40 | -0.67118 | 0.6023 | 0.19369 | 0.45 | 0.11567 | -40 | -0.67118 | 0.6023 | 0.19369
0.9373 | 0.2424 | -38 | 0 | 0.6 | 0 | 0.9373 | 0.2424 | -38 | 0 | 0.6 | 0 | 0.024767 | 0.026257 | -38 | -0.57876 | 0.6124 | 0.15848 | 0.097988 | 0.1104 | -38 | -0.6028 | 0.44348 | 0.15168 | 0.4036 | 0.1608 | -38 | -0.68082 | 0.59199 | 0.24047 | 0.5909 | 0.1034 | -38 | -0.67497 | 0.55774 | 0.2184 | 0.44 | 0.1237 | -38 | -0.69261 | 0.58681 | 0.21943 | 0.44 | 0.11677 | -38 | -0.68165 | 0.55275 | 0.19174 | 0.44 | 0.11677 | -38 | -0.68165 | 0.55275 | 0.19174
0.933 | 0.25 | -36 | 0 | 0.6 | 0 | 0.933 | 0.25 | -36 | 0 | 0.6 | 0 | 0.013968 | 0.0069404 | -36 | -0.58452 | 0.5734 | 0.14966 | 0.077895 | 0.09239 | -36 | -0.6113 | 0.40016 | 0.14446 | 0.3858 | 0.1627 | -36 | -0.69053 | 0.54435 | 0.23813 | 0.5765 | 0.1061 | -36 | -0.68406 | 0.50918 | 0.21712 | 0.43 | 0.1247 | -36 | -0.70354 | 0.53903 | 0.21949 | 0.43 | 0.11779 | -36 | -0.69144 | 0.50406 | 0.19077 | 0.43 | 0.11779 | -36 | -0.69144 | 0.50406 | 0.19077
0.9286 | 0.2575 | -34 | 0 | 0.6 | 0 | 0.9286 | 0.2575 | -34 | 0 | 0.6 | 0 | 0.0062209 | -0.014746 | -34 | -0.59028 | 0.5344 | 0.14084 | 0.059953 | 0.075006 | -34 | -0.6198 | 0.35684 | 0.13724 | 0.3684 | 0.1642 | -34 | -0.69986 | 0.49774 | 0.23679 | 0.5621 | 0.1087 | -34 | -0.69272 | 0.4617 | 0.21701 | 0.42 | 0.1256 | -34 | -0.71422 | 0.49229 | 0.22088 | 0.42 | 0.11873 | -34 | -0.70087 | 0.45646 | 0.19102 | 0.42 | 0.11873 | -34 | -0.70087 | 0.45646 | 0.19102
0.924 | 0.265 | -32 | 0 | 0.6 | 0 | 0.924 | 0.265 | -32 | 0 | 0.6 | 0 | 0.0015552 | -0.033321 | -32 | -0.59604 | 0.4954 | 0.13202 | 0.044256 | 0.056203 | -32 | -0.6283 | 0.31352 | 0.13002 | 0.3513 | 0.1654 | -32 | -0.70921 | 0.45241 | 0.2367 | 0.5477 | 0.1111 | -32 | -0.70132 | 0.41554 | 0.21835 | 0.41 | 0.1264 | -32 | -0.72506 | 0.44683 | 0.22396 | 0.41 | 0.11959 | -32 | -0.71032 | 0.41018 | 0.19279 | 0.41 | 0.11959 | -32 | -0.71032 | 0.41018 | 0.19279
0.9193 | 0.2723 | -30 | 0 | 0.6 | 0 | 0.9193 | 0.2723 | -30 | 0 | 0.6 | 0 | 0 | -0.06444 | -30 | -0.6018 | 0.4564 | 0.1232 | 0.030849 | 0.039134 | -30 | -0.6368 | 0.2702 | 0.1228 | 0.3345 | 0.1662 | -30 | -0.71907 | 0.40857 | 0.23815 | 0.5334 | 0.1135 | -30 | -0.71036 | 0.37093 | 0.22152 | 0.4 | 0.1271 | -30 | -0.7366 | 0.40288 | 0.22914 | 0.4 | 0.12036 | -30 | -0.72031 | 0.36545 | 0.19647 | 0.4 | 0.12036 | -30 | -0.72031 | 0.36545 | 0.19647
0.9145 | 0.2796 | -28 | 0 | 0.6 | 0 | 0.9145 | 0.2796 | -28 | 0 | 0.6 | 0 | 0.0015552 | -0.088045 | -28 | -0.61206 | 0.42436 | 0.11322 | 0.019814 | 0.021006 | -28 | -0.6521 | 0.235 | 0.1151 | 0.318 | 0.1666 | -28 | -0.73009 | 0.36645 | 0.24156 | 0.5191 | 0.1158 | -28 | -0.72045 | 0.32807 | 0.227 | 0.39 | 0.1277 | -28 | -0.7495 | 0.36065 | 0.23701 | 0.39 | 0.12104 | -28 | -0.73146 | 0.32249 | 0.20254 | 0.39 | 0.12104 | -28 | -0.73146 | 0.32249 | 0.20254
0.9096 | 0.2868 | -26 | 0 | 0.6 | 0 | 0.9096 | 0.2868 | -26 | 0 | 0.6 | 0 | 0.0062209 | -0.099121 | -26 | -0.62232 | 0.39232 | 0.10324 | 0.011174 | 0.0055523 | -26 | -0.6674 | 0.1998 | 0.1074 | 0.3017 | 0.1666 | -26 | -0.74308 | 0.32626 | 0.24744 | 0.5049 | 0.118 | -26 | -0.73238 | 0.28719 | 0.23545 | 0.38 | 0.1282 | -26 | -0.76461 | 0.32035 | 0.24834 | 0.38 | 0.12162 | -26 | -0.74459 | 0.2815 | 0.21171 | 0.38 | 0.12162 | -26 | -0.74459 | 0.2815 | 0.21171
0.9045 | 0.2939 | -24 | 0 | 0.6 | 0 | 0.9045 | 0.2939 | -24 | 0 | 0.6 | 0 | 0.013968 | -0.1143 | -24 | -0.63258 | 0.36028 | 0.09326 | 0.0049767 | -0.011797 | -24 | -0.6827 | 0.1646 | 0.0997 | 0.2857 | 0.1663 | -24 | -0.75909 | 0.28818 | 0.25655 | 0.4908 | 0.12 | -24 | -0.74718 | 0.24847 | 0.24777 | 0.37 | 0.1285 | -24 | -0.78307 | 0.28218 | 0.2642 | 0.37 | 0.12209 | -24 | -0.76078 | 0.24269 | 0.2249 | 0.37 | 0.12209 | -24 | -0.76078 | 0.24269 | 0.2249
0.8993 | 0.3009 | -22 | 0 | 0.6 | 0 | 0.8993 | 0.3009 | -22 | 0 | 0.6 | 0 | 0.024767 | -0.12575 | -22 | -0.64284 | 0.32824 | 0.08328 | 0.0012442 | -0.026657 | -22 | -0.698 | 0.1294 | 0.092 | 0.27 | 0.1656 | -22 | -0.77958 | 0.25242 | 0.26993 | 0.4767 | 0.122 | -22 | -0.76625 | 0.21211 | 0.26527 | 0.36 | 0.1288 | -22 | -0.81181 | 0.24608 | 0.24518 | 0.36 | 0.12245 | -22 | -0.78146 | 0.20625 | 0.24347 | 0.36 | 0.12245 | -22 | -0.78146 | 0.20625 | 0.24347
0.894 | 0.3078 | -20 | 0 | 0.6 | 0 | 0.894 | 0.3078 | -20 | 0 | 0.6 | 0 | 0.038561 | -0.13829 | -20 | -0.6531 | 0.2962 | 0.0733 | 0 | -0.051552 | -20 | -0.7133 | 0.0942 | 0.0843 | 0.2547 | 0.1645 | -20 | -0.80649 | 0.21914 | 0.28913 | 0.4627 | 0.1238 | -20 | -0.92153 | 0.19687 | 0.1962 | 0.35 | 0.1289 | -20 | -0.84743 | 0.21034 | 0.18694 | 0.35 | 0.12268 | -20 | -0.80862 | 0.17235 | 0.26946 | 0.35 | 0.12268 | -20 | -0.80862 | 0.17235 | 0.26946
0.8886 | 0.3147 | -19 | 0 | 0.6 | 0 | 0.8886 | 0.3147 | -19 | 0 | 0.6 | 0 | 0.05532 | -0.14841 | -19 | -0.62655 | 0.28357 | 0.06342 | 0.0012442 | -0.070436 | -19 | -0.68902 | 0.08822 | 0.07428 | 0.2398 | 0.1631 | -19 | -0.79145 | 0.20363 | 0.26529 | 0.4488 | 0.1255 | -19 | -0.99917 | 0.18926 | 0.16166 | 0.34 | 0.1288 | -19 | -0.86524 | 0.19248 | 0.15782 | 0.34 | 0.12277 | -19 | -0.82546 | 0.1564 | 0.28613 | 0.34 | 0.12277 | -19 | -0.82546 | 0.1564 | 0.28613
0.883 | 0.3214 | -18 | 0 | 0.6 | 0 | 0.883 | 0.3214 | -18 | 0 | 0.6 | 0 | 0.074942 | -0.16018 | -18 | -0.6 | 0.27094 | 0.05354 | 0.0049767 | -0.079297 | -18 | -0.66474 | 0.08224 | 0.06426 | 0.2252 | 0.1613 | -18 | -0.77641 | 0.18812 | 0.24144 | 0.435 | 0.1271 | -18 | -1.0768 | 0.18164 | 0.12713 | 0.33 | 0.1286 | -18 | -0.88304 | 0.17461 | 0.1287 | 0.33 | 0.1227 | -18 | -0.82 | 0.14115 | 0.28 | 0.33 | 0.1227 | -18 | -0.82 | 0.14115 | 0.28
0.8774 | 0.328 | -17 | 0 | 0.6 | 0 | 0.8774 | 0.328 | -17 | 0 | 0.6 | 0 | 0.097369 | -0.16996 | -17 | -0.57345 | 0.25831 | 0.04366 | 0.011174 | -0.091436 | -17 | -0.64046 | 0.07626 | 0.05424 | 0.211 | 0.1591 | -17 | -0.76137 | 0.17261 | 0.2176 | 0.4213 | 0.1286 | -17 | -1.1544 | 0.17402 | 0.092593 | 0.32 | 0.1282 | -17 | -0.90085 | 0.15674 | 0.099582 | 0.32 | 0.12247 | -17 | -0.81374 | 0.12796 | 0.26627 | 0.32 | 0.12247 | -17 | -0.81374 | 0.12796 | 0.26627
0.8716 | 0.3346 | -16 | 0 | 0.6 | 0 | 0.8716 | 0.3346 | -16 | 0 | 0.6 | 0 | 0.12249 | -0.18091 | -16 | -0.5469 | 0.24568 | 0.03378 | 0.019814 | -0.1006 | -16 | -0.61618 | 0.07028 | 0.04422 | 0.1971 | 0.1566 | -16 | -0.74633 | 0.15711 | 0.19375 | 0.4077 | 0.1298 | -16 | -1.2321 | 0.1664 | 0.058057 | 0.31 | 0.1277 | -16 | -0.91866 | 0.13887 | 0.070463 | 0.31 | 0.12208 | -16 | -0.78241 | 0.11477 | 0.22658 | 0.31 | 0.12208 | -16 | -0.78241 | 0.11477 | 0.22658
0.8657 | 0.341 | -15 | 0 | 0.6 | 0 | 0.8657 | 0.341 | -15 | 0 | 0.6 | 0 | 0.15017 | -0.19017 | -15 | -0.52035 | 0.23305 | 0.0239 | 0.030849 | -0.11063 | -15 | -0.5919 | 0.0643 | 0.0342 | 0.1836 | 0.1537 | -15 | -0.73129 | 0.1416 | 0.16991 | 0.3942 | 0.131 | -15 | -1.2594 | 0.15497 | 0.032234 | 0.3 | 0.127 | -15 | -0.93647 | 0.12101 | 0.041344 | 0.3 | 0.12155 | -15 | -0.75109 | 0.10158 | 0.18689 | 0.3 | 0.12155 | -15 | -0.75109 | 0.10158 | 0.18689
0.8597 | 0.3473 | -14 | 0 | 0.6 | 0 | 0.8597 | 0.3473 | -14 | 0 | 0.6 | 0 | 0.18035 | -0.20025 | -14 | -0.4938 | 0.22042 | 0.01402 | 0.044256 | -0.11873 | -14 | -0.56762 | 0.05832 | 0.02418 | 0.1704 | 0.1505 | -14 | -0.71625 | 0.12609 | 0.14607 | 0.3808 | 0.132 | -14 | -1.1936 | 0.13659 | 0.02016 | 0.29 | 0.1262 | -14 | -0.95427 | 0.10314 | 0.012225 | 0.29 | 0.12086 | -14 | -0.71976 | 0.088387 | 0.1472 | 0.29 | 0.12086 | -14 | -0.71976 | 0.088387 | 0.1472
0.8536 | 0.3536 | -13.5 | 0 | 0.6 | 0 | 0.8536 | 0.3536 | -13.5 | 0 | 0.6 | 0 | 0.21286 | -0.20861 | -13.5 | -0.48052 | 0.2141 | 0.00908 | 0.059953 | -0.12815 | -13.5 | -0.55548 | 0.05533 | 0.01917 | 0.1577 | 0.1469 | -13.5 | -0.70873 | 0.11834 | 0.13414 | 0.3676 | 0.1328 | -13.5 | -1.1517 | 0.12679 | 0.012345 | 0.28 | 0.1252 | -13.5 | -0.96318 | 0.094205 | -0.0023344 | 0.28 | 0.12002 | -13.5 | -0.70409 | 0.081791 | 0.12736 | 0.28 | 0.12002 | -13.5 | -0.70409 | 0.081791 | 0.12736
0.8473 | 0.3597 | -13 | 0 | 0.6 | 0 | 0.8473 | 0.3597 | -13 | 0 | 0.6 | 0 | 0.24757 | -0.21745 | -13 | -0.46725 | 0.20779 | 0.00414 | 0.077895 | -0.13597 | -13 | -0.54334 | 0.05234 | 0.01416 | 0.1453 | 0.1431 | -13 | -0.70121 | 0.11058 | 0.12222 | 0.3545 | 0.1335 | -13 | -1.1098 | 0.11699 | 0.0045294 | 0.27 | 0.1241 | -13 | -0.97208 | 0.085271 | -0.016894 | 0.27 | 0.11903 | -13 | -0.68843 | 0.075195 | 0.10751 | 0.27 | 0.11903 | -13 | -0.68843 | 0.075195 | 0.10751
0.841 | 0.3657 | -12.5 | 0 | 0.6 | 0 | 0.841 | 0.3657 | -12.5 | 0 | 0.6 | 0 | 0.28433 | -0.2246 | -12.5 | -0.45398 | 0.20147 | -0.0008 | 0.097988 | -0.14473 | -12.5 | -0.5312 | 0.04935 | 0.00915 | 0.1334 | 0.1389 | -12.5 | -0.69369 | 0.10283 | 0.1103 | 0.3415 | 0.1339 | -12.5 | -1.0648 | 0.10756 | -0.0039483 | 0.26 | 0.1228 | -12.5 | -0.96078 | 0.074523 | -0.024192 | 0.26 | 0.11789 | -12.5 | -0.67277 | 0.068599 | 0.08767 | 0.26 | 0.11789 | -12.5 | -0.67277 | 0.068599 | 0.08767
0.8346 | 0.3716 | -12 | 0 | 0.6 | 0 | 0.8346 | 0.3716 | -12 | 0 | 0.6 | 0 | 0.32298 | -0.2319 | -12 | -0.4407 | 0.19516 | -0.00574 | 0.12014 | -0.15213 | -12 | -0.51906 | 0.04636 | 0.00414 | 0.1219 | 0.1345 | -12 | -0.68617 | 0.095073 | 0.098377 | 0.3286 | 0.1342 | -12 | -1.0198 | 0.098133 | -0.012426 | 0.25 | 0.1214 | -12 | -0.94948 | 0.063774 | -0.03149 | 0.25 | 0.11661 | -12 | -0.6571 | 0.062003 | 0.067826 | 0.25 | 0.11661 | -12 | -0.6571 | 0.062003 | 0.067826
0.828 | 0.3774 | -11.5 | 0 | 0.6 | 0 | 0.828 | 0.3774 | -11.5 | 0 | 0.6 | 0 | 0.36337 | -0.23749 | -11.5 | -0.42742 | 0.18885 | -0.01068 | 0.14428 | -0.1602 | -11.5 | -0.50692 | 0.04337 | -0.00087 | 0.1109 | 0.1298 | -11.5 | -0.67864 | 0.087319 | 0.086455 | 0.316 | 0.1344 | -11.5 | -0.97537 | 0.090456 | -0.018779 | 0.24 | 0.1199 | -11.5 | -0.92624 | 0.054523 | -0.033152 | 0.24 | 0.11518 | -11.5 | -0.64144 | 0.055407 | 0.047982 | 0.24 | 0.11518 | -11.5 | -0.64144 | 0.055407 | 0.047982
0.8214 | 0.383 | -11 | 0 | 0.6 | 0 | 0.8214 | 0.383 | -11 | 0 | 0.6 | 0 | 0.40532 | -0.24296 | -11 | -0.41415 | 0.18253 | -0.01562 | 0.17029 | -0.16689 | -11 | -0.49478 | 0.04038 | -0.00588 | 0.1005 | 0.1249 | -11 | -0.67112 | 0.079565 | 0.074533 | 0.3035 | 0.1343 | -11 | -0.93098 | 0.08278 | -0.025132 | 0.23 | 0.1182 | -11 | -0.903 | 0.045271 | -0.034814 | 0.23 | 0.11361 | -11 | -0.62578 | 0.048811 | 0.028137 | 0.23 | 0.11361 | -11 | -0.62578 | 0.048811 | 0.028137
0.8147 | 0.3886 | -10.5 | 0 | 0.6 | 0 | 0.8147 | 0.3886 | -10.5 | 0 | 0.6 | 0 | 0.44863 | -0.24658 | -10.5 | -0.40087 | 0.17622 | -0.02056 | 0.19806 | -0.17396 | -10.5 | -0.48264 | 0.03739 | -0.01089 | 0.0907 | 0.1199 | -10.5 | -0.6636 | 0.071811 | 0.06261 | 0.2912 | 0.134 | -10.5 | -0.88426 | 0.076227 | -0.029981 | 0.22 | 0.1164 | -10.5 | -0.87112 | 0.038421 | -0.038933 | 0.22 | 0.11189 | -10.5 | -0.61011 | 0.042215 | 0.008293 | 0.22 | 0.11189 | -10.5 | -0.61011 | 0.042215 | 0.008293
0.8078 | 0.394 | -10 | 0 | 0.6 | 0 | 0.8078 | 0.394 | -10 | 0 | 0.6 | 0 | 0.49314 | -0.24988 | -10 | -0.3876 | 0.1699 | -0.0255 | 0.22747 | -0.17968 | -10 | -0.4705 | 0.0344 | -0.0159 | 0.0815 | 0.1146 | -10 | -0.65608 | 0.064057 | 0.050688 | 0.2792 | 0.1336 | -10 | -0.83753 | 0.069674 | -0.034831 | 0.21 | 0.1144 | -10 | -0.83923 | 0.03157 | -0.043053 | 0.21 | 0.11003 | -10 | -0.59445 | 0.035619 | -0.011551 | 0.21 | 0.11003 | -10 | -0.59445 | 0.035619 | -0.011551
0.8009 | 0.3993 | -9.5 | 0 | 0.6 | 0 | 0.8009 | 0.3993 | -9.5 | 0 | 0.6 | 0 | 0.53865 | -0.25111 | -9.5 | -0.36131 | 0.16352 | -0.024743 | 0.25838 | -0.18552 | -9.5 | -0.44398 | 0.033929 | -0.015871 | 0.0728 | 0.1093 | -9.5 | -0.64856 | 0.056302 | 0.038766 | 0.2674 | 0.1329 | -9.5 | -0.80147 | 0.059813 | -0.040885 | 0.2 | 0.1122 | -9.5 | -0.80604 | 0.026128 | -0.04705 | 0.2 | 0.10801 | -9.5 | -0.57879 | 0.029024 | -0.031396 | 0.2 | 0.10801 | -9.5 | -0.57879 | 0.029024 | -0.031396
0.7939 | 0.4045 | -9 | 0 | 0.6 | 0 | 0.7939 | 0.4045 | -9 | 0 | 0.6 | 0 | 0.58496 | -0.25169 | -9 | -0.33501 | 0.15714 | -0.023985 | 0.2907 | -0.18999 | -9 | -0.41746 | 0.033457 | -0.015843 | 0.0647 | 0.1038 | -9 | -0.64104 | 0.048548 | 0.026844 | 0.2559 | 0.132 | -9 | -0.7654 | 0.049952 | -0.04694 | 0.19 | 0.1099 | -9 | -0.77284 | 0.020687 | -0.051048 | 0.19 | 0.10583 | -9 | -0.56312 | 0.022428 | -0.05124 | 0.19 | 0.10583 | -9 | -0.56312 | 0.022428 | -0.05124
0.7868 | 0.4096 | -8.5 | 0 | 0.6 | 0 | 0.7868 | 0.4096 | -8.5 | 0 | 0.6 | 0 | 0.63189 | -0.24959 | -8.5 | -0.30872 | 0.15075 | -0.023228 | 0.32426 | -0.19437 | -8.5 | -0.39094 | 0.032986 | -0.015814 | 0.0571 | 0.0982 | -8.5 | -0.63352 | 0.040794 | 0.014922 | 0.2447 | 0.131 | -8.5 | -0.7513 | 0.037014 | -0.051965 | 0.18 | 0.1075 | -8.5 | -0.71749 | 0.016735 | -0.059465 | 0.18 | 0.10348 | -8.5 | -0.5355 | 0.017031 | -0.068842 | 0.18 | 0.10348 | -8.5 | -0.5355 | 0.017031 | -0.068842
0.7796 | 0.4145 | -8 | 0 | 0.6 | 0 | 0.7796 | 0.4145 | -8 | 0 | 0.6 | 0 | 0.67922 | -0.24661 | -8 | -0.28242 | 0.14437 | -0.022471 | 0.35891 | -0.19726 | -8 | -0.36441 | 0.032514 | -0.015786 | 0.0501 | 0.0926 | -8 | -0.626 | 0.03304 | 0.003 | 0.2337 | 0.1296 | -8 | -0.7372 | 0.024076 | -0.05699 | 0.17 | 0.1049 | -8 | -0.66214 | 0.012783 | -0.067882 | 0.17 | 0.10098 | -8 | -0.50788 | 0.011634 | -0.086445 | 0.17 | 0.10098 | -8 | -0.50788 | 0.011634 | -0.086445
0.7723 | 0.4193 | -7.5 | 0 | 0.6 | 0 | 0.7723 | 0.4193 | -7.5 | 0 | 0.6 | 0 | 0.72674 | -0.24132 | -7.5 | -0.25613 | 0.13799 | -0.021713 | 0.39451 | -0.1999 | -7.5 | -0.33789 | 0.032043 | -0.015757 | 0.0436 | 0.0869 | -7.5 | -0.5835 | 0.029417 | -0.001 | 0.2228 | 0.1281 | -7.5 | -0.69316 | 0.020586 | -0.05869 | 0.16 | 0.1021 | -7.5 | -0.59492 | 0.011634 | -0.07388 | 0.16 | 0.098298 | -7.5 | -0.43732 | 0.010187 | -0.095137 | 0.16 | 0.098298 | -7.5 | -0.43732 | 0.010187 | -0.095137
0.765 | 0.424 | -7 | 0 | 0.6 | 0 | 0.765 | 0.424 | -7 | 0 | 0.6 | 0 | 0.77427 | -0.23509 | -7 | -0.22984 | 0.13161 | -0.020956 | 0.43092 | -0.20089 | -7 | -0.31137 | 0.031571 | -0.015729 | 0.0376 | 0.0811 | -7 | -0.541 | 0.025795 | -0.005 | 0.2119 | 0.1263 | -7 | -0.64911 | 0.017096 | -0.060391 | 0.15 | 0.0991 | -7 | -0.5277 | 0.010484 | -0.079878 | 0.15 | 0.095445 | -7 | -0.3661 | 0.009 | -0.1025 | 0.15 | 0.095445 | -7 | -0.3661 | 0.009 | -0.1025
0.7575 | 0.4286 | -6.5 | 0 | 0.6 | 0 | 0.7575 | 0.4286 | -6.5 | 0 | 0.6 | 0 | 0.8216 | -0.22568 | -6.5 | -0.20354 | 0.12522 | -0.020199 | 0.46797 | -0.20135 | -6.5 | -0.28485 | 0.0311 | -0.0157 | 0.0321 | 0.0754 | -6.5 | -0.494 | 0.02266 | -0.0095 | 0.201 | 0.1242 | -6.5 | -0.57827 | 0.015875 | -0.064431 | 0.14 | 0.0959 | -6.5 | -0.45743 | 0.0097645 | -0.086076 | 0.14 | 0.092407 | -6.5 | -0.3035 | 0.0076 | -0.1048 | 0.14 | 0.092407 | -6.5 | -0.3035 | 0.0076 | -0.1048
0.75 | 0.433 | -6 | 0 | 0.6 | 0 | 0.75 | 0.433 | -6 | 0 | 0.6 | 0 | 0.86853 | -0.21477 | -6 | -0.17725 | 0.11884 | -0.019441 | 0.50551 | -0.19967 | -6 | -0.25833 | 0.030629 | -0.015671 | 0.0272 | 0.0697 | -6 | -0.447 | 0.019525 | -0.014 | 0.1902 | 0.1219 | -6 | -0.50742 | 0.014654 | -0.068471 | 0.13 | 0.0926 | -6 | -0.38716 | 0.0090453 | -0.092274 | 0.13 | 0.089169 | -6 | -0.2415 | 0.0072 | -0.1068 | 0.13 | 0.089169 | -6 | -0.2415 | 0.0072 | -0.1068
0.7424 | 0.4373 | -5.5 | 0 | 0.6 | 0 | 0.7424 | 0.4373 | -5.5 | 0 | 0.6 | 0 | 0.91484 | -0.20024 | -5.5 | -0.15095 | 0.11246 | -0.018684 | 0.54337 | -0.19728 | -5.5 | -0.23181 | 0.030157 | -0.015643 | 0.0228 | 0.064 | -5.5 | -0.3955 | 0.017657 | -0.0185 | 0.1793 | 0.1194 | -5.5 | -0.43819 | 0.013686 | -0.072065 | 0.12 | 0.089 | -5.5 | -0.3171 | 0.0087403 | -0.09708 | 0.12 | 0.085719 | -5.5 | -0.18 | 0.0069 | -0.1085 | 0.12 | 0.085719 | -5.5 | -0.18 | 0.0069 | -0.1085
0.7347 | 0.4415 | -5 | 0 | 0.6 | 0 | 0.7347 | 0.4415 | -5 | 0 | 0.6 | 0 | 0.96035 | -0.18605 | -5 | -0.12466 | 0.10608 | -0.017926 | 0.5814 | -0.19305 | -5 | -0.20529 | 0.029686 | -0.015614 | 0.0188 | 0.0585 | -5 | -0.344 | 0.01579 | -0.023 | 0.1686 | 0.1166 | -5 | -0.36896 | 0.012718 | -0.07566 | 0.11 | 0.0852 | -5 | -0.24704 | 0.0084354 | -0.10189 | 0.11 | 0.082041 | -5 | -0.1187 | 0.0067 | -0.1101 | 0.11 | 0.082041 | -5 | -0.1187 | 0.0067 | -0.1101
0.727 | 0.4455 | -4.5 | 0 | 0.6 | 0 | 0.727 | 0.4455 | -4.5 | 0 | 0.6 | 0 | 0.98 | -0.17336 | -4.5 | -0.098365 | 0.099694 | -0.017169 | 0.61942 | -0.18808 | -4.5 | -0.17876 | 0.029214 | -0.015586 | 0.0153 | 0.0531 | -4.5 | -0.2885 | 0.014297 | -0.028 | 0.158 | 0.1137 | -4.5 | -0.30101 | 0.012112 | -0.078906 | 0.1 | 0.0812 | -4.5 | -0.17873 | 0.0082916 | -0.10519 | 0.1 | 0.078116 | -4.5 | -0.0577 | 0.0065 | -0.1116 | 0.1 | 0.078116 | -4.5 | -0.0577 | 0.0065 | -0.1116
0.7192 | 0.4494 | -4 | 0 | 0.6 | 0 | 0.7192 | 0.4494 | -4 | 0 | 0.6 | 0 | 0.99 | -0.12444 | -4 | -0.072071 | 0.093312 | -0.016412 | 0.65728 | -0.18054 | -4 | -0.15224 | 0.028743 | -0.015557 | 0.0123 | 0.0477 | -4 | -0.233 | 0.012805 | -0.033 | 0.1475 | 0.1105 | -4 | -0.23306 | 0.011506 | -0.082153 | 0.095 | 0.0791 | -4 | -0.11042 | 0.0081479 | -0.1085 | 0.095 | 0.076051 | -4 | 0.003 | 0.0064 | -0.113 | 0.095 | 0.076051 | -4 | 0.003 | 0.0064 | -0.113
0.7113 | 0.4532 | -3.5 | 0 | 0.6 | 0 | 0.7113 | 0.4532 | -3.5 | 0 | 0.6 | 0 | 1 | -0.08444 | -3.5 | -0.045776 | 0.086929 | -0.015654 | 0.69483 | -0.17182 | -3.5 | -0.12572 | 0.028271 | -0.015529 | 0.0096 | 0.0425 | -3.5 | -0.174 | 0.012348 | -0.038 | 0.1372 | 0.1071 | -3.5 | -0.16655 | 0.011162 | -0.085077 | 0.09 | 0.0769 | -3.5 | -0.04392 | 0.0079792 | -0.11138 | 0.09 | 0.073915 | -3.5 | 0.0635 | 0.0064 | -0.1143 | 0.09 | 0.073915 | -3.5 | 0.0635 | 0.0064 | -0.1143
0.7034 | 0.4568 | -3 | 0 | 0.6 | 0 | 0.7034 | 0.4568 | -3 | 0 | 0.6 | 0 |  |  | -3 | -0.0071429 | 0.083296 | -0.01602 | 0.73187 | -0.16019 | -3 | -0.0992 | 0.0278 | -0.0155 | 0.0074 | 0.0375 | -3 | -0.115 | 0.01189 | -0.043 | 0.1271 | 0.1035 | -3 | -0.10055 | 0.010863 | -0.087918 | 0.085 | 0.0746 | -3 | 0.022845 | 0.007822 | -0.11378 | 0.085 | 0.071702 | -3 | 0.1242 | 0.0063 | -0.1155 | 0.085 | 0.071702 | -3 | 0.1242 | 0.0063 | -0.1155
0.6954 | 0.4603 | -2.5 | 0 | 0.6 | 0 | 0.6954 | 0.4603 | -2.5 | 0 | 0.6 | 0 |  |  | -2.5 | 0.05 | 0.083786 | -0.018071 | 0.76828 | -0.14884 | -2.5 | -0.0312 | 0.0278 | -0.0185 | 0.0055 | 0.0326 | -2.5 | -0.054 | 0.011298 | -0.0475 | 0.1172 | 0.0997 | -2.5 | -0.036198 | 0.01071 | -0.090492 | 0.08 | 0.0723 | -2.5 | 0.088864 | 0.0077055 | -0.11621 | 0.08 | 0.069407 | -2.5 | 0.1846 | 0.0063 | -0.1168 | 0.08 | 0.069407 | -2.5 | 0.1846 | 0.0063 | -0.1168
0.6873 | 0.4636 | -2 | 0 | 0.6 | 0 | 0.6873 | 0.4636 | -2 | 0 | 0.6 | 0 |  |  | -2 | 0.10714 | 0.084276 | -0.020122 | 0.80388 | -0.13745 | -2 | 0.0368 | 0.0278 | -0.0202 | 0.004 | 0.0277 | -2 | 0.007 | 0.010705 | -0.052 | 0.1076 | 0.0957 | -2 | 0.028028 | 0.010563 | -0.093035 | 0.075 | 0.0699 | -2 | 0.15462 | 0.0076021 | -0.11855 | 0.075 | 0.067025 | -2 | 0.2447 | 0.0063 | -0.1179 | 0.075 | 0.067025 | -2 | 0.2447 | 0.0063 | -0.1179
0.6792 | 0.4668 | -1.5 | 0 | 0.6 | 0 | 0.6792 | 0.4668 | -1.5 | 0 | 0.6 | 0 |  |  | -1.5 | 0.16429 | 0.084765 | -0.022173 | 0.83853 | -0.12731 | -1.5 | 0.1048 | 0.0278 | -0.0219 | 0.0028 | 0.0226 | -1.5 | 0.07 | 0.010518 | -0.056 | 0.0983 | 0.0916 | -1.5 | 0.091789 | 0.010439 | -0.095466 | 0.07 | 0.0673 | -1.5 | 0.21918 | 0.0075585 | -0.12049 | 0.07 | 0.064551 | -1.5 | 0.3051 | 0.0063 | -0.119 | 0.07 | 0.064551 | -1.5 | 0.3051 | 0.0063 | -0.119
0.671 | 0.4698 | -1 | 0 | 0.6 | 0 | 0.671 | 0.4698 | -1 | 0 | 0.6 | 0 |  |  | -1 | 0.22143 | 0.085255 | -0.024224 | 0.87209 | -0.1178 | -1 | 0.1728 | 0.0278 | -0.0237 | 0.0018 | 0.0173 | -1 | 0.133 | 0.01033 | -0.06 | 0.0892 | 0.0873 | -1 | 0.15563 | 0.010323 | -0.097893 | 0.065 | 0.0647 | -1 | 0.28346 | 0.0075282 | -0.1224 | 0.065 | 0.061975 | -1 | 0.3651 | 0.0063 | -0.1202 | 0.065 | 0.061975 | -1 | 0.3651 | 0.0063 | -0.1202
0.6628 | 0.4728 | -0.5 | 0 | 0.6 | 0 | 0.6628 | 0.4728 | -0.5 | 0 | 0.6 | 0 |  |  | -0.5 | 0.27857 | 0.085745 | -0.026276 | 0.90441 | -0.10965 | -0.5 | 0.2408 | 0.0279 | -0.0254 | 0.001 | 0.0122 | -0.5 | 0.197 | 0.010233 | -0.064 | 0.0805 | 0.0829 | -0.5 | 0.22128 | 0.010388 | -0.10022 | 0.06 | 0.062 | -0.5 | 0.34559 | 0.0075961 | -0.1241 | 0.06 | 0.05929 | -0.5 | 0.4251 | 0.0063 | -0.1213 | 0.06 | 0.05929 | -0.5 | 0.4251 | 0.0063 | -0.1213
0.6545 | 0.4755 | 0 | 0 | 0.6 | 0 | 0.6545 | 0.4755 | 0 | 0 | 0.6 | 0 |  |  | 0 | 0.33571 | 0.086235 | -0.028327 | 0.93533 | -0.1022 | 0 | 0.3088 | 0.0279 | -0.0271 | 0.0004 | 0.0076 | 0 | 0.261 | 0.010135 | -0.068 | 0.0722 | 0.0784 | 0 | 0.28687 | 0.010455 | -0.10253 | 0.055 | 0.0592 | 0 | 0.40775 | 0.00766 | -0.12579 | 0.055 | 0.056486 | 0 | 0.4848 | 0.0064 | -0.1224 | 0.055 | 0.056486 | 0 | 0.4848 | 0.0064 | -0.1224
0.6462 | 0.4782 | 0.5 | 0 | 0.6 | 0 | 0.6462 | 0.4782 | 0.5 | 0 | 0.6 | 0 |  |  | 0.5 | 0.39286 | 0.086724 | -0.030378 | 0.96473 | -0.096064 | 0.5 | 0.3768 | 0.0279 | -0.0288 | 0.0001 | 0.0034 | 0.5 | 0.326 | 0.010127 | -0.0715 | 0.0643 | 0.0738 | 0.5 | 0.35137 | 0.01054 | -0.10463 | 0.05 | 0.0562 | 0.5 | 0.47025 | 0.00766 | -0.12733 | 0.05 | 0.05355 | 0.5 | 0.5448 | 0.0064 | -0.1235 | 0.05 | 0.05355 | 0.5 | 0.5448 | 0.0064 | -0.1235
0.6378 | 0.4806 | 1 | 0 | 0.6 | 0 | 0.6378 | 0.4806 | 1 | 0 | 0.6 | 0 |  |  | 1 | 0.45 | 0.087214 | -0.032429 | 0.9925 | -0.090541 | 1 | 0.4448 | 0.0279 | -0.0306 | 0 | -0.0004 | 1 | 0.391 | 0.01012 | -0.075 | 0.0568 | 0.0691 | 1 | 0.41584 | 0.010619 | -0.10671 | 0.045 | 0.0531 | 1 | 0.53287 | 0.00766 | -0.12869 | 0.045 | 0.050465 | 1 | 0.6043 | 0.0064 | -0.1245 | 0.045 | 0.050465 | 1 | 0.6043 | 0.0064 | -0.1245
0.6294 | 0.483 | 1.5 | 0 | 0.6 | 0 | 0.6294 | 0.483 | 1.5 | 0 | 0.6 | 0 |  |  | 1.5 | 0.50714 | 0.087704 | -0.03448 | 1 | -0.061552 | 1.5 | 0.5128 | 0.0279 | -0.0323 | 0.0001 | -0.0042 | 1.5 | 0.4565 | 0.010292 | -0.0785 | 0.0497 | 0.0644 | 1.5 | 0.47986 | 0.01061 | -0.10858 | 0.04 | 0.0498 | 1.5 | 0.59549 | 0.00766 | -0.13005 | 0.04 | 0.047213 | 1.5 | 0.6637 | 0.0065 | -0.1254 | 0.04 | 0.047213 | 1.5 | 0.6637 | 0.0065 | -0.1254
0.621 | 0.4851 | 2 | 0 | 0.6 | 0 | 0.621 | 0.4851 | 2 | 0 | 0.6 | 0 |  |  | 2 | 0.57 | 0.087792 | -0.036685 |  |  | 2 | 0.5798 | 0.028 | -0.0342 | 0.0005 | -0.0082 | 2 | 0.522 | 0.010465 | -0.082 | 0.0432 | 0.0597 | 2 | 0.54388 | 0.010601 | -0.11045 | 0.035 | 0.0463 | 2 | 0.658 | 0.0077938 | -0.1313 | 0.035 | 0.043767 | 2 | 0.7231 | 0.0065 | -0.1264 | 0.035 | 0.043767 | 2 | 0.7231 | 0.0065 | -0.1264
0.6125 | 0.4872 | 2.5 | 0 | 0.6 | 0 | 0.6125 | 0.4872 | 2.5 | 0 | 0.6 | 0 |  |  | 2.5 | 0.63667 | 0.087613 | -0.038992 |  |  | 2.5 | 0.6462 | 0.028 | -0.0363 | 0.0012 | -0.0127 | 2.5 | 0.587 | 0.010637 | -0.0845 | 0.0371 | 0.055 | 2.5 | 0.60582 | 0.010749 | -0.11209 | 0.03 | 0.0426 | 2.5 | 0.7205 | 0.0079333 | -0.13255 | 0.03 | 0.040094 | 2.5 | 0.7823 | 0.0066 | -0.1274 | 0.03 | 0.040094 | 2.5 | 0.7823 | 0.0066 | -0.1274
0.604 | 0.4891 | 3 | 0 | 0.6 | 0 | 0.604 | 0.4891 | 3 | 0 | 0.6 | 0 |  |  | 3 | 0.70333 | 0.087433 | -0.0413 |  |  | 3 | 0.7126 | 0.028 | -0.0385 | 0.0021 | -0.0174 | 3 | 0.652 | 0.01081 | -0.087 | 0.0316 | 0.0504 | 3 | 0.66759 | 0.010911 | -0.11371 | 0.025 | 0.0387 | 3 | 0.78182 | 0.0080568 | -0.13364 | 0.025 | 0.036145 | 3 | 0.841 | 0.0067 | -0.1283 | 0.025 | 0.036145 | 3 | 0.841 | 0.0067 | -0.1283
0.5954 | 0.4908 | 3.5 | 0 | 0.6 | 0 | 0.5954 | 0.4908 | 3.5 | 0 | 0.6 | 0 |  |  | 3.5 | 0.77 | 0.087254 | -0.043608 |  |  | 3.5 | 0.779 | 0.028 | -0.0407 | 0.0032 | -0.0223 | 3.5 | 0.7155 | 0.01108 | -0.089 | 0.0267 | 0.046 | 3.5 | 0.72928 | 0.011025 | -0.11505 | 0.02 | 0.0344 | 3.5 | 0.84299 | 0.0081782 | -0.13471 | 0.02 | 0.031845 | 3.5 | 0.9001 | 0.0068 | -0.1291 | 0.02 | 0.031845 | 3.5 | 0.9001 | 0.0068 | -0.1291
0.5868 | 0.4924 | 4 | 0 | 0.6 | 0 | 0.5868 | 0.4924 | 4 | 0 | 0.6 | 0 |  |  | 4 | 0.83667 | 0.087074 | -0.045915 |  |  | 4 | 0.8454 | 0.0281 | -0.0429 | 0.0045 | -0.0272 | 4 | 0.779 | 0.01135 | -0.091 | 0.0223 | 0.0418 | 4 | 0.79096 | 0.011132 | -0.11636 | 0.0175 | 0.032 | 4 | 0.90376 | 0.0083115 | -0.13562 | 0.0175 | 0.029529 | 4 | 0.9585 | 0.0069 | -0.13 | 0.0175 | 0.029529 | 4 | 0.9585 | 0.0069 | -0.13
0.5782 | 0.4938 | 4.5 | 0 | 0.6 | 0 | 0.5782 | 0.4938 | 4.5 | 0 | 0.6 | 0 |  |  | 4.5 | 0.90333 | 0.086895 | -0.048223 |  |  | 4.5 | 0.9118 | 0.0281 | -0.045 | 0.0062 | -0.0321 | 4.5 | 0.8405 | 0.011718 | -0.093 | 0.0185 | 0.0377 | 4.5 | 0.8519 | 0.011276 | -0.11752 | 0.015 | 0.0296 | 4.5 | 0.9641 | 0.0084833 | -0.13633 | 0.015 | 0.027075 | 4.5 | 1.0166 | 0.007 | -0.1307 | 0.015 | 0.027075 | 4.5 | 1.0166 | 0.007 | -0.1307
0.5696 | 0.4951 | 5 | 0 | 0.6 | 0 | 0.5696 | 0.4951 | 5 | 0 | 0.6 | 0 |  |  | 5 | 0.97 | 0.086715 | -0.050531 |  |  | 5 | 0.9782 | 0.0281 | -0.0472 | 0.0082 | -0.037 | 5 | 0.902 | 0.012085 | -0.095 | 0.0151 | 0.0339 | 5 | 0.91283 | 0.01142 | -0.11867 | 0.0125 | 0.027 | 5 | 1.0245 | 0.0086551 | -0.13703 | 0.0125 | 0.024452 | 5 | 1.0745 | 0.0071 | -0.1314 | 0.0125 | 0.024452 | 5 | 1.0745 | 0.0071 | -0.1314
0.5609 | 0.4963 | 5.5 | 0 | 0.6 | 0 | 0.5609 | 0.4963 | 5.5 | 0 | 0.6 | 0 |  |  | 5.5 | 1.0367 | 0.086536 | -0.052838 |  |  | 5.5 | 1.0446 | 0.0282 | -0.0494 | 0.0106 | -0.042 | 5.5 | 0.961 | 0.012467 | -0.0965 | 0.0122 | 0.0302 | 5.5 | 0.97183 | 0.011627 | -0.11954 | 0.01 | 0.0241 | 5.5 | 1.0828 | 0.0089047 | -0.13728 | 0.01 | 0.021614 | 5.5 | 1.1319 | 0.0073 | -0.1321 | 0.01 | 0.021614 | 5.5 | 1.1319 | 0.0073 | -0.1321
0.5523 | 0.4973 | 6 | 0 | 0.6 | 0 | 0.5523 | 0.4973 | 6 | 0 | 0.6 | 0 |  |  | 6 | 1.0977 | 0.086371 | -0.055506 |  |  | 6 | 1.111 | 0.0282 | -0.0516 | 0.0134 | -0.0471 | 6 | 1.02 | 0.01285 | -0.098 | 0.0097 | 0.0268 | 6 | 1.0308 | 0.011833 | -0.1204 | 0.009 | 0.0229 | 6 | 1.1412 | 0.0091542 | -0.13753 | 0.009 | 0.020402 | 6 | 1.188 | 0.0076 | -0.1325 | 0.009 | 0.020402 | 6 | 1.188 | 0.0076 | -0.1325
0.5436 | 0.4981 | 6.5 | 0 | 0.6 | 0 | 0.5436 | 0.4981 | 6.5 | 0 | 0.6 | 0 |  |  | 6.5 | 1.1574 | 0.08621 | -0.058265 |  |  | 6.5 | 1.1774 | 0.0282 | -0.0537 | 0.0167 | -0.0524 | 6.5 | 1.0745 | 0.013383 | -0.099 | 0.0075 | 0.0236 | 6.5 | 1.088 | 0.012097 | -0.12091 | 0.008 | 0.0216 | 6.5 | 1.1948 | 0.009482 | -0.13706 | 0.008 | 0.019135 | 6.5 | 1.2419 | 0.0081 | -0.1326 | 0.008 | 0.019135 | 6.5 | 1.2419 | 0.0081 | -0.1326
0.5349 | 0.4988 | 7 | 0 | 0.6 | 0 | 0.5349 | 0.4988 | 7 | 0 | 0.6 | 0 |  |  | 7 | 1.2171 | 0.086048 | -0.061023 |  |  | 7 | 1.2438 | 0.0283 | -0.0559 | 0.0203 | -0.0577 | 7 | 1.129 | 0.013915 | -0.1 | 0.0057 | 0.0206 | 7 | 1.1453 | 0.01236 | -0.12142 | 0.007 | 0.0203 | 7 | 1.2484 | 0.0098098 | -0.13658 | 0.007 | 0.017806 | 7 | 1.291 | 0.009 | -0.1321 | 0.007 | 0.017806 | 7 | 1.291 | 0.009 | -0.1321
0.5262 | 0.4993 | 7.5 | 0 | 0.6 | 0 | 0.5262 | 0.4993 | 7.5 | 0 | 0.6 | 0 |  |  | 7.5 | 1.2768 | 0.085887 | -0.063781 |  |  | 7.5 | 1.3102 | 0.0283 | -0.0581 | 0.0245 | -0.0632 | 7.5 | 1.178 | 0.014627 | -0.101 | 0.0042 | 0.0178 | 7.5 | 1.2004 | 0.012668 | -0.12151 | 0.006 | 0.0189 | 7.5 | 1.289 | 0.010551 | -0.1342 | 0.006 | 0.016398 | 7.5 | 1.3334 | 0.0105 | -0.1304 | 0.006 | 0.016398 | 7.5 | 1.3334 | 0.0105 | -0.1304
0.5174 | 0.4997 | 8 | 0 | 0.6 | 0 | 0.5174 | 0.4997 | 8 | 0 | 0.6 | 0 |  |  | 8 | 1.3365 | 0.085726 | -0.066539 |  |  | 8 | 1.374 | 0.0283 | -0.0611 | 0.0292 | -0.0688 | 8 | 1.227 | 0.01534 | -0.102 | 0.003 | 0.015 | 8 | 1.2555 | 0.012976 | -0.1216 | 0.005 | 0.0174 | 8 | 1.3296 | 0.011292 | -0.13182 | 0.005 | 0.014893 | 8 | 1.3725 | 0.012 | -0.1283 | 0.005 | 0.014893 | 8 | 1.3725 | 0.012 | -0.1283
0.5087 | 0.4999 | 8.5 | 0 | 0.6 | 0 | 0.5087 | 0.4999 | 8.5 | 0 | 0.6 | 0 |  |  | 8.5 | 1.3961 | 0.085565 | -0.069297 |  |  | 8.5 | 1.434 | 0.0284 | -0.0644 | 0.0347 | -0.0747 | 8.5 | 1.2675 | 0.016295 | -0.103 | 0.002 | 0.0124 | 8.5 | 1.3075 | 0.013424 | -0.12124 | 0.004 | 0.0157 | 8.5 | 1.3475 | 0.012992 | -0.12728 | 0.004 | 0.013259 | 8.5 | 1.4118 | 0.0134 | -0.1263 | 0.004 | 0.013259 | 8.5 | 1.4118 | 0.0134 | -0.1263
0.5 | 0.5 | 9 | 0 | 0.6 | 0 | 0.5 | 0.5 | 9 | 0 | 0.6 | 0 |  |  | 9 | 1.4444 | 0.08625 | -0.0725 |  |  | 9 | 1.494 | 0.0285 | -0.0677 | 0.0407 | -0.0807 | 9 | 1.308 | 0.01725 | -0.104 | 0.0012 | 0.0098 | 9 | 1.3595 | 0.013873 | -0.12087 | 0.003 | 0.0139 | 9 | 1.3654 | 0.014693 | -0.12275 | 0.003 | 0.011446 | 9 | 1.4511 | 0.0145 | -0.1242 | 0.003 | 0.011446 | 9 | 1.4511 | 0.0145 | -0.1242
0.4913 | 0.4999 | 9.5 | 0 | 0.6 | 0 | 0.4913 | 0.4999 | 9.5 | 0 | 0.6 | 0 |  |  | 9.5 | 1.485 | 0.0875 | -0.076 |  |  | 9.5 | 1.554 | 0.0286 | -0.071 | 0.0475 | -0.0869 | 9.5 | 1.3385 | 0.019723 | -0.105 | 0.0006 | 0.0073 | 9.5 | 1.4059 | 0.014483 | -0.11976 | 0.002 | 0.0116 | 9.5 | 1.3358 | 0.025407 | -0.12274 | 0.002 | 0.009341 | 9.5 | 1.4887 | 0.0156 | -0.1217 | 0.002 | 0.009341 | 9.5 | 1.4887 | 0.0156 | -0.1217
0.4826 | 0.4997 | 10 | 0 | 0.6 | 0 | 0.4826 | 0.4997 | 10 | 0 | 0.6 | 0 |  |  | 10 | 1.5256 | 0.08875 | -0.0795 |  |  | 10 | 1.614 | 0.0287 | -0.0743 | 0.0549 | -0.0932 | 10 | 1.369 | 0.022195 | -0.106 | 0.0003 | 0.0048 | 10 | 1.4523 | 0.015094 | -0.11864 | 0.0017 | 0.011 | 10 | 1.3062 | 0.03612 | -0.12274 | 0.00175 | 0.008737 | 10 | 1.5162 | 0.0165 | -0.1217 | 0.00175 | 0.008737 | 10 | 1.5162 | 0.0165 | -0.1217
0.4738 | 0.4993 | 10.5 | 0 | 0.6 | 0 | 0.4738 | 0.4993 | 10.5 | 0 | 0.6 | 0 |  |  | 10.5 | 1.24 | 0.1054 | -0.083 |  |  | 10.5 | 1.6629 | 0.0288 | -0.0776 | 0.063 | -0.0994 | 10.5 | 1.381 | 0.025773 | -0.1065 | 0.0001 | 0.0023 | 10.5 | 1.489 | 0.015984 | -0.11654 | 0.0015 | 0.0102 | 10.5 | 1.2313 | 0.04552 | -0.12195 | 0.0015 | 0.00808 | 10.5 | 1.5422 | 0.0178 | -0.1217 | 0.0015 | 0.00808 | 10.5 | 1.5422 | 0.0178 | -0.1217
0.4651 | 0.4988 | 11 | 0 | 0.6 | 0 | 0.4651 | 0.4988 | 11 | 0 | 0.6 | 0 |  |  | 11 | 1.0733 | 0.1256 | -0.04385 |  |  | 11 | 1.6953 | 0.029 | -0.0809 | 0.0717 | -0.1057 | 11 | 1.393 | 0.02935 | -0.107 | 0 | -0.0001 | 11 | 1.5257 | 0.016873 | -0.11443 | 0.0013 | 0.0094 | 11 | 1.1564 | 0.054921 | -0.12115 | 0.00125 | 0.00736 | 11 | 1.5626 | 0.0195 | -0.1217 | 0.00125 | 0.00736 | 11 | 1.5626 | 0.0195 | -0.1217
0.4564 | 0.4981 | 11.5 | 0 | 0.6 | 0 | 0.4564 | 0.4981 | 11.5 | 0 | 0.6 | 0 |  |  | 11.5 | 1.045 | 0.141 | -0.037367 |  |  | 11.5 | 1.7277 | 0.0292 | -0.0842 | 0.0811 | -0.1118 | 11.5 | 1.3675 | 0.035147 | -0.1075 | 0.0001 | -0.0025 | 11.5 | 1.5424 | 0.018453 | -0.11076 | 0.001 | 0.0085 | 11.5 | 1.1325 | 0.058957 | -0.11672 | 0.001 | 0.006562 | 11.5 | 1.5804 | 0.0215 | -0.1222 | 0.001 | 0.006562 | 11.5 | 1.5804 | 0.0215 | -0.1222
0.4477 | 0.4973 | 12 | 0 | 0.6 | 0 | 0.4477 | 0.4973 | 12 | 0 | 0.6 | 0 |  |  | 12 | 1.028 | 0.15542 | -0.03908 |  |  | 12 | 1.76 | 0.0301 | -0.0875 | 0.0909 | -0.1179 | 12 | 1.342 | 0.040945 | -0.108 | 0.0003 | -0.005 | 12 | 1.5592 | 0.020032 | -0.10709 | 0.0008 | 0.0074 | 12 | 1.1087 | 0.062993 | -0.1123 | 0.00075 | 0.005649 | 12 | 1.5871 | 0.035 | -0.1238 | 0.00075 | 0.005649 | 12 | 1.5871 | 0.035 | -0.1238
0.4391 | 0.4963 | 12.5 | 0 | 0.6 | 0 | 0.4391 | 0.4963 | 12.5 | 0 | 0.6 | 0 |  |  | 12.5 | 1.0171 | 0.16922 | -0.04078 |  |  | 12.5 | 0.986 | 0.0334 | -0.0589 | 0.1013 | -0.1237 | 12.5 | 1.3165 | 0.04984 | -0.1085 | 0.0007 | -0.0076 | 12.5 | 1.3775 | 0.039607 | -0.11135 | 0.0005 | 0.006 | 12.5 | 1.1027 | 0.069851 | -0.10895 | 0.0005 | 0.004564 | 12.5 | 1.5486 | 0.0485 | -0.1254 | 0.0005 | 0.004564 | 12.5 | 1.5486 | 0.0485 | -0.1254
0.4304 | 0.4951 | 13 | 0 | 0.6 | 0 | 0.4304 | 0.4951 | 13 | 0 | 0.6 | 0 |  |  | 13 | 1.0097 | 0.1825 | -0.042475 |  |  | 13 | 0.9725 | 0.0351 | -0.0598 | 0.1122 | -0.1293 | 13 | 1.291 | 0.058735 | -0.109 | 0.0013 | -0.0103 | 13 | 1.1958 | 0.059182 | -0.11562 | 0.0004 | 0.0054 | 13 | 1.0967 | 0.076708 | -0.1056 | 0.0004 | 0.004058 | 13 | 1.51 | 0.062 | -0.127 | 0.0004 | 0.004058 | 13 | 1.51 | 0.062 | -0.127
0.4218 | 0.4938 | 13.5 | 0 | 0.6 | 0 | 0.4218 | 0.4938 | 13.5 | 0 | 0.6 | 0 |  |  | 13.5 | 1.0075 | 0.195 | -0.044163 |  |  | 13.5 | 0.985 | 0.0365 | -0.0618 | 0.1237 | -0.1348 | 13.5 | 1.27 | 0.06919 | -0.109 | 0.0021 | -0.0132 | 13.5 | 1.148 | 0.066951 | -0.11419 | 0.0003 | 0.0046 | 13.5 | 1.1044 | 0.084991 | -0.10696 | 0.0003 | 0.003493 | 13.5 | 1.46 | 0.0755 | -0.1286 | 0.0003 | 0.003493 | 13.5 | 1.46 | 0.0755 | -0.1286
0.4132 | 0.4924 | 14 | 0 | 0.6 | 0 | 0.4132 | 0.4924 | 14 | 0 | 0.6 | 0 |  |  | 14 | 1.0072 | 0.2064 | -0.04582 |  |  | 14 | 0.9975 | 0.0377 | -0.0641 | 0.1357 | -0.14 | 14 | 1.249 | 0.079645 | -0.109 | 0.0032 | -0.0161 | 14 | 1.1002 | 0.074721 | -0.11276 | 0.0002 | 0.0038 | 14 | 1.1122 | 0.093274 | -0.10831 | 0.0002 | 0.002833 | 14 | 1.41 | 0.089 | -0.1302 | 0.0002 | 0.002833 | 14 | 1.41 | 0.089 | -0.1302
0.4046 | 0.4908 | 15 | 0 | 0.6 | 0 | 0.4046 | 0.4908 | 15 | 0 | 0.6 | 0 |  |  | 15 | 1.0083 | 0.22748 | -0.049277 |  |  | 15 | 1.054 | 0.0393 | -0.0689 | 0.1482 | -0.145 | 15 | 1.211 | 0.10343 | -0.11 | 0.0045 | -0.0193 | 15 | 1.0499 | 0.088786 | -0.11057 | 0.0001 | 0.0027 | 15 | 1.1257 | 0.111 | -0.11228 | 0.0001 | 0.001983 | 15 | 1.34 | 0.1025 | -0.1318 | 0.0001 | 0.001983 | 15 | 1.34 | 0.1025 | -0.1318
0.396 | 0.4891 | 16 | 0 | 0.6 | 0 | 0.396 | 0.4891 | 16 | 0 | 0.6 | 0 |  |  | 16 | 1.0118 | 0.24586 | -0.052662 |  |  | 16 | 1.1267 | 0.04 | -0.0742 | 0.1612 | -0.1498 | 16 | 1.188 | 0.12955 | -0.119 | 0.006 | -0.0226 | 16 | 1.0215 | 0.1027 | -0.1093 | 0 | 0 | 16 | 1.1288 | 0.12528 | -0.11324 | 0 | 1e-06 | 16 | 1.3 | 0.116 | -0.1334 | 0 | 1e-06 | 16 | 1.3 | 0.116 | -0.1334
0.3875 | 0.4872 | 17 | 0 | 0.6 | 0 | 0.3875 | 0.4872 | 17 | 0 | 0.6 | 0 |  |  | 17 | 0.99385 | 0.25889 | -0.062508 |  |  | 17 | 1.0998 | 0.05355 | -0.083375 | 0.1745 | -0.1542 | 17 | 1.172 | 0.15439 | -0.132 | 0.0079 | -0.0261 | 17 | 1.0073 | 0.11718 | -0.1095 | 0.0001 | -0.0027 | 17 | 1.1216 | 0.13729 | -0.11199 | 0.0001 | -0.001969 | 17 | 1.26 | 0.1295 | -0.135 | 0.0001 | -0.001969 | 17 | 1.26 | 0.1295 | -0.135
0.379 | 0.4851 | 18 | 0 | 0.6 | 0 | 0.379 | 0.4851 | 18 | 0 | 0.6 | 0 |  |  | 18 | 0.97356 | 0.27133 | -0.073072 |  |  | 18 | 1.0729 | 0.0671 | -0.09255 | 0.1882 | -0.1583 | 18 | 1.165 | 0.17908 | -0.143 | 0.0102 | -0.0298 | 18 | 1.0099 | 0.13292 | -0.11172 | 0.0002 | -0.0039 | 18 | 1.1274 | 0.15514 | -0.1149 | 0.0002 | -0.002794 | 18 | 1.2 | 0.143 | -0.1366 | 0.0002 | -0.002794 | 18 | 1.2 | 0.143 | -0.1366
0.3706 | 0.483 | 19 | 0 | 0.6 | 0 | 0.3706 | 0.483 | 19 | 0 | 0.6 | 0 |  |  | 19 | 0.95328 | 0.28376 | -0.083636 |  |  | 19 | 1.046 | 0.08065 | -0.10172 | 0.2023 | -0.1621 | 19 | 1.176 | 0.20348 | -0.148 | 0.0129 | -0.0339 | 19 | 1.0397 | 0.15277 | -0.11769 | 0.0003 | -0.0047 | 19 | 1.1339 | 0.17631 | -0.12142 | 0.0003 | -0.003412 | 19 | 1.1792 | 0.1564 | -0.1382 | 0.0003 | -0.003412 | 19 | 1.1792 | 0.1564 | -0.1382
0.3622 | 0.4806 | 20 | 0 | 0.6 | 0 | 0.3622 | 0.4806 | 20 | 0 | 0.6 | 0 |  |  | 20 | 0.933 | 0.2962 | -0.0942 |  |  | 20 | 1.0191 | 0.0942 | -0.1109 | 0.2167 | -0.1656 | 20 | 1.1521 | 0.21914 | -0.15682 | 0.0162 | -0.0383 | 20 | 1.0655 | 0.17339 | -0.12548 | 0.0004 | -0.0055 | 20 | 1.1391 | 0.19553 | -0.12614 | 0.0004 | -0.003939 | 20 | 1.1552 | 0.17235 | -0.14799 | 0.0004 | -0.003939 | 20 | 1.1552 | 0.17235 | -0.14799
0.3538 | 0.4782 | 22 | 0 | 0.6 | 0 | 0.3538 | 0.4782 | 22 | 0 | 0.6 | 0 |  |  | 22 | 0.91836 | 0.32824 | -0.10636 |  |  | 22 | 0.99724 | 0.1294 | -0.1204 | 0.2313 | -0.1687 | 22 | 1.1137 | 0.25242 | -0.17182 | 0.0199 | -0.0431 | 22 | 1.0946 | 0.21211 | -0.14423 | 0.0005 | -0.0062 | 22 | 1.1472 | 0.24454 | -0.14212 | 0.0005 | -0.0044 | 22 | 1.1164 | 0.20625 | -0.17204 | 0.0005 | -0.0044 | 22 | 1.1164 | 0.20625 | -0.17204
0.3455 | 0.4755 | 24 | 0 | 0.6 | 0 | 0.3455 | 0.4755 | 24 | 0 | 0.6 | 0 |  |  | 24 | 0.90372 | 0.36028 | -0.11852 |  |  | 24 | 0.97538 | 0.1646 | -0.1299 | 0.246 | -0.1714 | 24 | 1.0844 | 0.28818 | -0.18445 | 0.0243 | -0.0482 | 24 | 1.0674 | 0.24847 | -0.1635 | 0.0008 | -0.0076 | 24 | 1.1187 | 0.28218 | -0.16487 | 0.00075 | -0.00539 | 24 | 1.0868 | 0.24269 | -0.19157 | 0.00075 | -0.00539 | 24 | 1.0868 | 0.24269 | -0.19157
0.3372 | 0.4728 | 26 | 0 | 0.6 | 0 | 0.3372 | 0.4728 | 26 | 0 | 0.6 | 0 |  |  | 26 | 0.88908 | 0.39232 | -0.13068 |  |  | 26 | 0.95352 | 0.1998 | -0.1394 | 0.2609 | -0.1737 | 26 | 1.0615 | 0.32626 | -0.19559 | 0.0292 | -0.0536 | 26 | 1.0462 | 0.28719 | -0.17989 | 0.001 | -0.0088 | 26 | 1.0923 | 0.32035 | -0.18419 | 0.001 | -0.00623 | 26 | 1.0637 | 0.2815 | -0.2081 | 0.001 | -0.00623 | 26 | 1.0637 | 0.2815 | -0.2081
0.329 | 0.4698 | 28 | 0 | 0.6 | 0 | 0.329 | 0.4698 | 28 | 0 | 0.6 | 0 |  |  | 28 | 0.87444 | 0.42436 | -0.14284 |  |  | 28 | 0.93166 | 0.235 | -0.1489 | 0.2758 | -0.1757 | 28 | 1.043 | 0.36645 | -0.20577 | 0.0348 | -0.0593 | 28 | 1.0292 | 0.32807 | -0.19433 | 0.0013 | -0.0098 | 28 | 1.0707 | 0.36065 | -0.20091 | 0.00125 | -0.006974 | 28 | 1.0449 | 0.32249 | -0.22259 | 0.00125 | -0.006974 | 28 | 1.0449 | 0.32249 | -0.22259
0.3208 | 0.4668 | 30 | 0 | 0.6 | 0 | 0.3208 | 0.4668 | 30 | 0 | 0.6 | 0 |  |  | 30 | 0.8598 | 0.4564 | -0.155 |  |  | 30 | 0.9098 | 0.2702 | -0.1584 | 0.2907 | -0.1772 | 30 | 1.0272 | 0.40857 | -0.21532 | 0.0409 | -0.0652 | 30 | 1.0148 | 0.37093 | -0.20741 | 0.0015 | -0.0108 | 30 | 1.0523 | 0.40288 | -0.21581 | 0.0015 | -0.007647 | 30 | 1.029 | 0.36545 | -0.23566 | 0.0015 | -0.007647 | 30 | 1.029 | 0.36545 | -0.23566
0.3127 | 0.4636 | 32 | 0 | 0.6 | 0 | 0.3127 | 0.4636 | 32 | 0 | 0.6 | 0 |  |  | 32 | 0.85154 | 0.4954 | -0.1641 |  |  | 32 | 0.89762 | 0.31352 | -0.16558 | 0.3056 | -0.1784 | 32 | 1.0131 | 0.45241 | -0.22445 | 0.0475 | -0.0712 | 32 | 1.0019 | 0.41554 | -0.21952 | 0.0017 | -0.0117 | 32 | 1.0358 | 0.44683 | -0.2294 | 0.00175 | -0.008266 | 32 | 1.0148 | 0.41018 | -0.24774 | 0.00175 | -0.008266 | 32 | 1.0148 | 0.41018 | -0.24774
0.3046 | 0.4603 | 34 | 0 | 0.6 | 0 | 0.3046 | 0.4603 | 34 | 0 | 0.6 | 0 |  |  | 34 | 0.84328 | 0.5344 | -0.1732 |  |  | 34 | 0.88544 | 0.35684 | -0.17276 | 0.3204 | -0.1791 | 34 | 0.99979 | 0.49774 | -0.2333 | 0.0545 | -0.0772 | 34 | 0.9896 | 0.4617 | -0.23095 | 0.002 | -0.0125 | 34 | 1.0203 | 0.49229 | -0.24203 | 0.002 | -0.008844 | 34 | 1.0012 | 0.45646 | -0.2591 | 0.002 | -0.008844 | 34 | 1.0012 | 0.45646 | -0.2591
0.2966 | 0.4568 | 36 | 0 | 0.6 | 0 | 0.2966 | 0.4568 | 36 | 0 | 0.6 | 0 |  |  | 36 | 0.83502 | 0.5734 | -0.1823 |  |  | 36 | 0.87326 | 0.40016 | -0.17994 | 0.335 | -0.1794 | 36 | 0.98647 | 0.54435 | -0.24195 | 0.062 | -0.0832 | 36 | 0.97723 | 0.50918 | -0.24186 | 0.003 | -0.0153 | 36 | 1.005 | 0.53903 | -0.25395 | 0.003 | -0.010865 | 36 | 0.98777 | 0.50406 | -0.26994 | 0.003 | -0.010865 | 36 | 0.98777 | 0.50406 | -0.26994
0.2887 | 0.4532 | 38 | 0 | 0.6 | 0 | 0.2887 | 0.4532 | 38 | 0 | 0.6 | 0 |  |  | 38 | 0.82676 | 0.6124 | -0.1914 |  |  | 38 | 0.86108 | 0.44348 | -0.18712 | 0.3493 | -0.1794 | 38 | 0.9726 | 0.59199 | -0.25045 | 0.0698 | -0.0891 | 38 | 0.96424 | 0.55774 | -0.25238 | 0.004 | -0.0177 | 38 | 0.98944 | 0.58681 | -0.26534 | 0.004 | -0.012581 | 38 | 0.97379 | 0.55275 | -0.28038 | 0.004 | -0.012581 | 38 | 0.97379 | 0.55275 | -0.28038
0.2808 | 0.4494 | 40 | 0 | 0.6 | 0 | 0.2808 | 0.4494 | 40 | 0 | 0.6 | 0 |  |  | 40 | 0.8185 | 0.6514 | -0.2005 |  |  | 40 | 0.8489 | 0.4868 | -0.1943 | 0.3633 | -0.1789 | 40 | 0.95776 | 0.64045 | -0.25885 | 0.078 | -0.0949 | 40 | 0.95018 | 0.60715 | -0.26261 | 0.005 | -0.0197 | 40 | 0.973 | 0.63541 | -0.27631 | 0.005 | -0.014101 | 40 | 0.95883 | 0.6023 | -0.29052 | 0.005 | -0.014101 | 40 | 0.95883 | 0.6023 | -0.29052
0.273 | 0.4455 | 45 | 0 | 0.6 | 0 | 0.273 | 0.4455 | 45 | 0 | 0.6 | 0 |  |  | 45 | 0.781 | 0.7539 | -0.22065 |  |  | 45 | 0.8052 | 0.6025 | -0.21175 | 0.377 | -0.178 | 45 | 0.91417 | 0.76352 | -0.27943 | 0.0864 | -0.1007 | 45 | 0.90831 | 0.73279 | -0.28725 | 0.006 | -0.0216 | 45 | 0.92598 | 0.75887 | -0.30241 | 0.006 | -0.015485 | 45 | 0.91501 | 0.72831 | -0.31493 | 0.006 | -0.015485 | 45 | 0.91501 | 0.72831 | -0.31493
0.2653 | 0.4415 | 50 | 0 | 0.6 | 0 | 0.2653 | 0.4415 | 50 | 0 | 0.6 | 0 |  |  | 50 | 0.7435 | 0.8564 | -0.2408 |  |  | 50 | 0.7615 | 0.7182 | -0.2292 | 0.3908 | -0.1767 | 50 | 0.85862 | 0.88632 | -0.29945 | 0.0952 | -0.1063 | 50 | 0.85415 | 0.85838 | -0.31088 | 0.007 | -0.0233 | 50 | 0.86763 | 0.88209 | -0.32715 | 0.007 | -0.016765 | 50 | 0.85926 | 0.85431 | -0.33838 | 0.007 | -0.016765 | 50 | 0.85926 | 0.85431 | -0.33838
0.2576 | 0.4373 | 55 | 0 | 0.6 | 0 | 0.2576 | 0.4373 | 55 | 0 | 0.6 | 0 |  |  | 55 | 0.68 | 0.9506 | -0.25845 |  |  | 55 | 0.69385 | 0.82775 | -0.24625 | 0.4049 | -0.1749 | 55 | 0.78221 | 1.0011 | -0.31836 | 0.1041 | -0.1117 | 55 | 0.77878 | 0.9763 | -0.33318 | 0.008 | -0.0249 | 55 | 0.78912 | 0.99738 | -0.35028 | 0.008 | -0.01796 | 55 | 0.7827 | 0.97269 | -0.36057 | 0.008 | -0.01796 | 55 | 0.7827 | 0.97269 | -0.36057
0.25 | 0.433 | 60 | 0 | 0.6 | 0 | 0.25 | 0.433 | 60 | 0 | 0.6 | 0 |  |  | 60 | 0.6165 | 1.0448 | -0.2761 |  |  | 60 | 0.6262 | 0.9373 | -0.2633 | 0.4193 | -0.1727 | 60 | 0.7058 | 1.1159 | -0.33726 | 0.1132 | -0.1169 | 60 | 0.7034 | 1.0942 | -0.35549 | 0.009 | -0.0263 | 60 | 0.71062 | 1.1127 | -0.3734 | 0.009 | -0.019089 | 60 | 0.70614 | 1.0911 | -0.38276 | 0.009 | -0.019089 | 60 | 0.70614 | 1.0911 | -0.38276
0.2425 | 0.4286 | 65 | 0 | 0.6 | 0 | 0.2425 | 0.4286 | 65 | 0 | 0.6 | 0 |  |  | 65 | 0.52805 | 1.1184 | -0.29065 |  |  | 65 | 0.53495 | 1.0279 | -0.2791 | 0.4338 | -0.17 | 65 | 0.60292 | 1.2085 | -0.3539 | 0.1224 | -0.1219 | 65 | 0.6012 | 1.1902 | -0.37562 | 0.01 | -0.0278 | 65 | 0.60637 | 1.2057 | -0.39415 | 0.01 | -0.020166 | 65 | 0.60316 | 1.1875 | -0.40288 | 0.01 | -0.020166 | 65 | 0.60316 | 1.1875 | -0.40288
0.235 | 0.424 | 70 | 0 | 0.6 | 0 | 0.235 | 0.424 | 70 | 0 | 0.6 | 0 |  |  | 70 | 0.4396 | 1.192 | -0.3052 |  |  | 70 | 0.4437 | 1.1185 | -0.2949 | 0.4485 | -0.1669 | 70 | 0.50004 | 1.301 | -0.37055 | 0.1318 | -0.1267 | 70 | 0.49901 | 1.2861 | -0.39574 | 0.0125 | -0.031 | 70 | 0.50212 | 1.2987 | -0.41489 | 0.0125 | -0.022668 | 70 | 0.50018 | 1.2839 | -0.423 | 0.0125 | -0.022668 | 70 | 0.50018 | 1.2839 | -0.423
0.2277 | 0.4193 | 75 | 0 | 0.6 | 0 | 0.2277 | 0.4193 | 75 | 0 | 0.6 | 0 |  |  | 75 | 0.3332 | 1.2349 | -0.3159 |  |  | 75 | 0.33575 | 1.1796 | -0.3084 | 0.4633 | -0.1634 | 75 | 0.37833 | 1.3597 | -0.38384 | 0.1413 | -0.1312 | 75 | 0.37768 | 1.3484 | -0.41275 | 0.015 | -0.034 | 75 | 0.37962 | 1.358 | -0.43241 | 0.015 | -0.024963 | 75 | 0.37842 | 1.3468 | -0.44011 | 0.015 | -0.024963 | 75 | 0.37842 | 1.3468 | -0.44011
0.2204 | 0.4145 | 80 | 0 | 0.6 | 0 | 0.2204 | 0.4145 | 80 | 0 | 0.6 | 0 |  |  | 80 | 0.2268 | 1.2779 | -0.3266 |  |  | 80 | 0.2278 | 1.2406 | -0.3219 | 0.4781 | -0.1594 | 80 | 0.25661 | 1.4183 | -0.39714 | 0.1508 | -0.1355 | 80 | 0.25636 | 1.4108 | -0.42976 | 0.0175 | -0.0368 | 80 | 0.25712 | 1.4172 | -0.44992 | 0.0175 | -0.027097 | 80 | 0.25665 | 1.4097 | -0.45721 | 0.0175 | -0.027097 | 80 | 0.25665 | 1.4097 | -0.45721
0.2132 | 0.4096 | 85 | 0 | 0.6 | 0 | 0.2132 | 0.4096 | 85 | 0 | 0.6 | 0 |  |  | 85 | 0.1134 | 1.2839 | -0.3327 |  |  | 85 | 0.1139 | 1.2653 | -0.33185 | 0.4931 | -0.155 | 85 | 0.12831 | 1.4357 | -0.40596 | 0.1605 | -0.1396 | 85 | 0.12818 | 1.4319 | -0.44249 | 0.02 | -0.0394 | 85 | 0.12856 | 1.4351 | -0.46307 | 0.02 | -0.029101 | 85 | 0.12832 | 1.4314 | -0.4701 | 0.02 | -0.029101 | 85 | 0.12832 | 1.4314 | -0.4701
0.2061 | 0.4045 | 90 | 0 | 0.6 | 0 | 0.2061 | 0.4045 | 90 | 0 | 0.6 | 0 |  |  | 90 | 0 | 1.29 | -0.3388 |  |  | 90 | 0 | 1.29 | -0.3418 | 0.5085 | -0.1501 | 90 | 0 | 1.4531 | -0.41478 | 0.1703 | -0.1434 | 90 | 0 | 1.4531 | -0.45522 | 0.025 | -0.0443 | 90 | 0 | 1.4531 | -0.47621 | 0.025 | -0.03279 | 90 | 0 | 1.4531 | -0.48299 | 0.025 | -0.03279 | 90 | 0 | 1.4531 | -0.48299
0.1991 | 0.3993 | 95 | 0 | 0.6 | 0 | 0.1991 | 0.3993 | 95 | 0 | 0.6 | 0 |  |  | 95 | -0.07935 | 1.2839 | -0.3453 |  |  | 95 | -0.0797 | 1.2653 | -0.34305 | 0.5241 | -0.1447 | 95 | -0.089815 | 1.4357 | -0.41894 | 0.18 | -0.1469 | 95 | -0.089725 | 1.4319 | -0.46138 | 0.03 | -0.0486 | 95 | -0.089994 | 1.4351 | -0.48439 | 0.03 | -0.036132 | 95 | -0.089827 | 1.4314 | -0.48905 | 0.03 | -0.036132 | 95 | -0.089827 | 1.4314 | -0.48905
0.1922 | 0.394 | 100 | 0 | 0.6 | 0 | 0.1922 | 0.394 | 100 | 0 | 0.6 | 0 |  |  | 100 | -0.1587 | 1.2779 | -0.3518 |  |  | 100 | -0.1594 | 1.2406 | -0.3443 | 0.5402 | -0.1387 | 100 | -0.17963 | 1.4183 | -0.42309 | 0.1897 | -0.1502 | 100 | -0.17945 | 1.4108 | -0.46755 | 0.035 | -0.0526 | 100 | -0.17999 | 1.4172 | -0.49256 | 0.035 | -0.039187 | 100 | -0.17965 | 1.4097 | -0.49511 | 0.035 | -0.039187 | 100 | -0.17965 | 1.4097 | -0.49511
0.1853 | 0.3886 | 105 | 0 | 0.6 | 0 | 0.1853 | 0.3886 | 105 | 0 | 0.6 | 0 |  |  | 105 | -0.2332 | 1.2349 | -0.351 |  |  | 105 | -0.235 | 1.1796 | -0.3385 | 0.5569 | -0.1322 | 105 | -0.26483 | 1.3597 | -0.41922 | 0.1993 | -0.1531 | 105 | -0.26438 | 1.3484 | -0.4655 | 0.04 | -0.0563 | 105 | -0.26573 | 1.358 | -0.49253 | 0.04 | -0.042007 | 105 | -0.26489 | 1.3468 | -0.49299 | 0.04 | -0.042007 | 105 | -0.26489 | 1.3468 | -0.49299
0.1786 | 0.383 | 110 | 0 | 0.6 | 0 | 0.1786 | 0.383 | 110 | 0 | 0.6 | 0 |  |  | 110 | -0.3077 | 1.192 | -0.3502 |  |  | 110 | -0.3106 | 1.1185 | -0.3327 | 0.5744 | -0.125 | 110 | -0.35003 | 1.301 | -0.41536 | 0.2089 | -0.1558 | 110 | -0.3493 | 1.2861 | -0.46345 | 0.045 | -0.0597 | 110 | -0.35148 | 1.2987 | -0.49249 | 0.045 | -0.044626 | 110 | -0.35013 | 1.2839 | -0.49087 | 0.045 | -0.044626 | 110 | -0.35013 | 1.2839 | -0.49087
0.172 | 0.3774 | 115 | 0 | 0.6 | 0 | 0.172 | 0.3774 | 115 | 0 | 0.6 | 0 |  |  | 115 | -0.36965 | 1.1184 | -0.34335 |  |  | 115 | -0.37445 | 1.0279 | -0.3219 | 0.5925 | -0.1172 | 115 | -0.42204 | 1.2085 | -0.4054 | 0.2183 | -0.1581 | 115 | -0.42084 | 1.1902 | -0.45509 | 0.05 | -0.0629 | 115 | -0.42446 | 1.2057 | -0.4861 | 0.05 | -0.047077 | 115 | -0.42221 | 1.1875 | -0.48252 | 0.05 | -0.047077 | 115 | -0.42221 | 1.1875 | -0.48252
0.1654 | 0.3716 | 120 | 0 | 0.6 | 0 | 0.1654 | 0.3716 | 120 | 0 | 0.6 | 0 |  |  | 120 | -0.4316 | 1.0448 | -0.3365 |  |  | 120 | -0.4383 | 0.9373 | -0.3111 | 0.6114 | -0.1088 | 120 | -0.49406 | 1.1159 | -0.39544 | 0.2277 | -0.1601 | 120 | -0.49238 | 1.0942 | -0.44672 | 0.055 | -0.0659 | 120 | -0.49743 | 1.1127 | -0.4797 | 0.055 | -0.049381 | 120 | -0.4943 | 1.0911 | -0.47417 | 0.055 | -0.049381 | 120 | -0.4943 | 1.0911 | -0.47417
0.159 | 0.3657 | 125 | 0 | 0.6 | 0 | 0.159 | 0.3657 | 125 | 0 | 0.6 | 0 |  |  | 125 | -0.47605 | 0.9506 | -0.32595 |  |  | 125 | -0.48565 | 0.82775 | -0.29825 | 0.6314 | -0.0997 | 125 | -0.54755 | 1.0011 | -0.38251 | 0.2369 | -0.1618 | 125 | -0.54514 | 0.9763 | -0.43529 | 0.06 | -0.0688 | 125 | -0.55239 | 0.99738 | -0.47028 | 0.06 | -0.051557 | 125 | -0.54789 | 0.97269 | -0.46289 | 0.06 | -0.051557 | 125 | -0.54789 | 0.97269 | -0.46289
0.1527 | 0.3597 | 130 | 0 | 0.6 | 0 | 0.1527 | 0.3597 | 130 | 0 | 0.6 | 0 |  |  | 130 | -0.5205 | 0.8564 | -0.3154 |  |  | 130 | -0.533 | 0.7182 | -0.2854 | 0.6524 | -0.0901 | 130 | -0.60104 | 0.88632 | -0.36959 | 0.246 | -0.1632 | 130 | -0.5979 | 0.85838 | -0.42385 | 0.065 | -0.0715 | 130 | -0.60734 | 0.88209 | -0.46086 | 0.065 | -0.053619 | 130 | -0.60148 | 0.85431 | -0.45162 | 0.065 | -0.053619 | 130 | -0.60148 | 0.85431 | -0.45162
0.1464 | 0.3536 | 135 | 0 | 0.6 | 0 | 0.1464 | 0.3536 | 135 | 0 | 0.6 | 0 |  |  | 135 | -0.54675 | 0.7539 | -0.3047 |  |  | 135 | -0.56365 | 0.6025 | -0.2746 | 0.6738 | -0.0802 | 135 | -0.63573 | 0.76338 | -0.35812 | 0.2552 | -0.1643 | 135 | -0.63152 | 0.73276 | -0.41419 | 0.07 | -0.074 | 135 | -0.64422 | 0.75875 | -0.4536 | 0.07 | -0.055575 | 135 | -0.63633 | 0.72831 | -0.44238 | 0.07 | -0.055575 | 135 | -0.63633 | 0.72831 | -0.44238
0.1403 | 0.3473 | 140 | 0 | 0.6 | 0 | 0.1403 | 0.3473 | 140 | 0 | 0.6 | 0 |  |  | 140 | -0.573 | 0.6514 | -0.294 |  |  | 140 | -0.5943 | 0.4868 | -0.2638 | 0.6948 | -0.0705 | 140 | -0.67043 | 0.64045 | -0.34666 | 0.2644 | -0.1652 | 140 | -0.66513 | 0.60715 | -0.40452 | 0.075 | -0.0765 | 140 | -0.6811 | 0.63541 | -0.44634 | 0.075 | -0.057439 | 140 | -0.67118 | 0.6023 | -0.43313 | 0.075 | -0.057439 | 140 | -0.67118 | 0.6023 | -0.43313
0.1343 | 0.341 | 145 | 0 | 0.6 | 0 | 0.1343 | 0.341 | 145 | 0 | 0.6 | 0 |  |  | 145 | -0.5874 | 0.5539 | -0.28905 |  |  | 145 | -0.61555 | 0.3785 | -0.26145 | 0.7147 | -0.0614 | 145 | -0.69475 | 0.52451 | -0.34393 | 0.2736 | -0.1657 | 145 | -0.68775 | 0.48904 | -0.40497 | 0.08 | -0.0789 | 145 | -0.70885 | 0.51915 | -0.45069 | 0.08 | -0.059218 | 145 | -0.69574 | 0.48387 | -0.43452 | 0.08 | -0.059218 | 145 | -0.69574 | 0.48387 | -0.43452
0.1284 | 0.3346 | 150 | 0 | 0.6 | 0 | 0.1284 | 0.3346 | 150 | 0 | 0.6 | 0 |  |  | 150 | -0.6018 | 0.4564 | -0.2841 |  |  | 150 | -0.6368 | 0.2702 | -0.2591 | 0.7337 | -0.053 | 150 | -0.71907 | 0.40857 | -0.34119 | 0.2829 | -0.166 | 150 | -0.71036 | 0.37093 | -0.40543 | 0.085 | -0.0811 | 150 | -0.7366 | 0.40288 | -0.45504 | 0.085 | -0.060918 | 150 | -0.72031 | 0.36545 | -0.43591 | 0.085 | -0.060918 | 150 | -0.72031 | 0.36545 | -0.43591
0.1226 | 0.328 | 155 | 0 | 0.6 | 0 | 0.1226 | 0.328 | 155 | 0 | 0.6 | 0 |  |  | 155 | -0.62745 | 0.3763 | -0.30045 |  |  | 155 | -0.67505 | 0.1822 | -0.2823 | 0.7517 | -0.0453 | 155 | -0.76278 | 0.31386 | -0.36668 | 0.2924 | -0.1659 | 155 | -0.70348 | 0.28188 | -0.43154 | 0.09 | -0.0833 | 155 | -0.71352 | 0.3162 | -0.4776 | 0.09 | -0.062544 | 155 | -0.76446 | 0.2689 | -0.4724 | 0.09 | -0.062544 | 155 | -0.76446 | 0.2689 | -0.4724
0.117 | 0.3214 | 160 | 0 | 0.6 | 0 | 0.117 | 0.3214 | 160 | 0 | 0.6 | 0 |  |  | 160 | -0.6531 | 0.2962 | -0.3168 |  |  | 160 | -0.7133 | 0.0942 | -0.3055 | 0.7689 | -0.0382 | 160 | -0.80649 | 0.21914 | -0.39217 | 0.3019 | -0.1656 | 160 | -0.69659 | 0.19283 | -0.45765 | 0.095 | -0.0854 | 160 | -0.69044 | 0.22952 | -0.50015 | 0.095 | -0.064101 | 160 | -0.80862 | 0.17235 | -0.5089 | 0.095 | -0.064101 | 160 | -0.80862 | 0.17235 | -0.5089
0.1114 | 0.3147 | 165 | 0 | 0.6 | 0 | 0.1114 | 0.3147 | 165 | 0 | 0.6 | 0 |  |  | 165 | -0.54655 | 0.24365 | -0.4084 |  |  | 165 | -0.6031 | 0.0521 | -0.40275 | 0.7855 | -0.0317 | 165 | -0.60487 | 0.16435 | -0.44608 | 0.3117 | -0.165 | 165 | -0.52244 | 0.14462 | -0.47882 | 0.1 | -0.0874 | 165 | -0.51783 | 0.17214 | -0.50008 | 0.1 | -0.065589 | 165 | -0.63905 | 0.12538 | -0.50445 | 0.1 | -0.065589 | 165 | -0.63905 | 0.12538 | -0.50445
0.106 | 0.3078 | 170 | 0 | 0.6 | 0 | 0.106 | 0.3078 | 170 | 0 | 0.6 | 0 |  |  | 170 | -0.44 | 0.1911 | -0.5 |  |  | 170 | -0.4929 | 0.01 | -0.5 | 0.8013 | -0.0258 | 170 | -0.40325 | 0.10957 | -0.5 | 0.3217 | -0.1641 | 170 | -0.3483 | 0.096415 | -0.5 | 0.11 | -0.0913 | 170 | -0.34522 | 0.11476 | -0.5 | 0.11 | -0.068384 | 170 | -0.46948 | 0.078419 | -0.5 | 0.11 | -0.068384 | 170 | -0.46948 | 0.078419 | -0.5
0.1007 | 0.3009 | 175 | 0 | 0.6 | 0 | 0.1007 | 0.3009 | 175 | 0 | 0.6 | 0 |  |  | 175 | -0.22 | 0.17285 | -0.25 |  |  | 175 | -0.24645 | 0.01 | -0.25 | 0.8165 | -0.0206 | 175 | -0.20162 | 0.054785 | -0.25 | 0.3319 | -0.1629 | 175 | -0.17415 | 0.048208 | -0.25 | 0.12 | -0.0948 | 175 | -0.17261 | 0.05738 | -0.25 | 0.12 | -0.070947 | 175 | -0.23474 | 0.03921 | -0.25 | 0.12 | -0.070947 | 175 | -0.23474 | 0.03921 | -0.25
0.0955 | 0.2939 | 180 | 0 | 0.6 | 0 | 0.0955 | 0.2939 | 180 | 0 | 0.6 | 0 |  |  | 180 | 0 | 0.1546 | 0 |  |  | 180 | 0 | 0.01 | 0 | 0.8311 | -0.016 | 180 | 0 | 0 | 0 | 0.3424 | -0.1614 | 180 | 0 | 0 | 0 | 0.13 | -0.0981 | 180 | 0 | 0 | 0 | 0.13 | -0.073297 | 180 | 0 | 0 | 0 | 0.13 | -0.073297 | 180 | 0 | 0 | 0
0.0904 | 0.2868 |  |  |  |  | 0.0904 | 0.2868 | [16 empty] | 0.8452 | -0.012 |  |  |  |  | 0.3531 | -0.1597 |  |  |  |  | 0.14 | -0.1011 |  |  |  |  | 0.14 | -0.075448 |  |  |  |  | 0.14 | -0.075448
0.0855 | 0.2796 |  |  |  |  | 0.0855 | 0.2796 | [16 empty] | 0.8587 | -0.0085 |  |  |  |  | 0.364 | -0.1576 |  |  |  |  | 0.15 | -0.1039 |  |  |  |  | 0.15 | -0.077412 |  |  |  |  | 0.15 | -0.077412
0.0807 | 0.2723 |  |  |  |  | 0.0807 | 0.2723 | [16 empty] | 0.8719 | -0.0055 |  |  |  |  | 0.3753 | -0.1552 |  |  |  |  | 0.16 | -0.1064 |  |  |  |  | 0.16 | -0.079199 |  |  |  |  | 0.16 | -0.079199
0.076 | 0.265 |  |  |  |  | 0.076 | 0.265 | [16 empty] | 0.8847 | -0.0031 |  |  |  |  | 0.3868 | -0.1526 |  |  |  |  | 0.17 | -0.1088 |  |  |  |  | 0.17 | -0.080817 |  |  |  |  | 0.17 | -0.080817
0.0714 | 0.2575 |  |  |  |  | 0.0714 | 0.2575 | [16 empty] | 0.8972 | -0.0011 |  |  |  |  | 0.3986 | -0.1496 |  |  |  |  | 0.18 | -0.1109 |  |  |  |  | 0.18 | -0.082268 |  |  |  |  | 0.18 | -0.082268
0.067 | 0.25 |  |  |  |  | 0.067 | 0.25 | [16 empty] | 0.9094 | 0.0004 |  |  |  |  | 0.4107 | -0.1464 |  |  |  |  | 0.19 | -0.1129 |  |  |  |  | 0.19 | -0.083559 |  |  |  |  | 0.19 | -0.083559
0.0627 | 0.2424 |  |  |  |  | 0.0627 | 0.2424 | [16 empty] | 0.9212 | 0.0014 |  |  |  |  | 0.4232 | -0.1428 |  |  |  |  | 0.2 | -0.1146 |  |  |  |  | 0.2 | -0.084693 |  |  |  |  | 0.2 | -0.084693
0.0585 | 0.2347 |  |  |  |  | 0.0585 | 0.2347 | [16 empty] | 0.9325 | 0.002 |  |  |  |  | 0.4358 | -0.1391 |  |  |  |  | 0.21 | -0.1162 |  |  |  |  | 0.21 | -0.085678 |  |  |  |  | 0.21 | -0.085678
0.0545 | 0.227 |  |  |  |  | 0.0545 | 0.227 | [16 empty] | 0.9432 | 0.0022 |  |  |  |  | 0.4487 | -0.1351 |  |  |  |  | 0.22 | -0.1176 |  |  |  |  | 0.22 | -0.086518 |  |  |  |  | 0.22 | -0.086518
0.0506 | 0.2192 |  |  |  |  | 0.0506 | 0.2192 | [16 empty] | 0.9533 | 0.002 |  |  |  |  | 0.4618 | -0.1309 |  |  |  |  | 0.23 | -0.1188 |  |  |  |  | 0.23 | -0.087214 |  |  |  |  | 0.23 | -0.087214
0.0468 | 0.2113 |  |  |  |  | 0.0468 | 0.2113 | [16 empty] | 0.9631 | 0.0013 |  |  |  |  | 0.4751 | -0.1266 |  |  |  |  | 0.24 | -0.1198 |  |  |  |  | 0.24 | -0.087771 |  |  |  |  | 0.24 | -0.087771
0.0432 | 0.2034 |  |  |  |  | 0.0432 | 0.2034 | [16 empty] | 0.9724 | 0.0003 |  |  |  |  | 0.4887 | -0.122 |  |  |  |  | 0.25 | -0.1207 |  |  |  |  | 0.25 | -0.088188 |  |  |  |  | 0.25 | -0.088188
0.0397 | 0.1954 |  |  |  |  | 0.0397 | 0.1954 | [16 empty] | 0.9818 | -0.0011 |  |  |  |  | 0.5025 | -0.1172 |  |  |  |  | 0.26 | -0.1214 |  |  |  |  | 0.26 | -0.088471 |  |  |  |  | 0.26 | -0.088471
0.0364 | 0.1873 |  |  |  |  | 0.0364 | 0.1873 | [16 empty] | 0.9911 | -0.0029 |  |  |  |  | 0.5165 | -0.1123 |  |  |  |  | 0.27 | -0.1219 |  |  |  |  | 0.27 | -0.088622 |  |  |  |  | 0.27 | -0.088622
0.0332 | 0.1792 |  |  |  |  | 0.0332 | 0.1792 | [16 empty] | 1 | -0.005 |  |  |  |  | 0.5306 | -0.1073 |  |  |  |  | 0.28 | -0.1223 |  |  |  |  | 0.28 | -0.088642 |  |  |  |  | 0.28 | -0.088642
0.0302 | 0.171 |  |  |  |  | 0.0302 | 0.171 | [22 empty] | 0.5449 | -0.1022 |  |  |  |  | 0.29 | -0.1225 |  |  |  |  | 0.29 | -0.088529 |  |  |  |  | 0.29 | -0.088529
0.0272 | 0.1628 |  |  |  |  | 0.0272 | 0.1628 | [22 empty] | 0.5592 | -0.097 |  |  |  |  | 0.3 | -0.1226 |  |  |  |  | 0.3 | -0.088287 |  |  |  |  | 0.3 | -0.088287
0.0245 | 0.1545 |  |  |  |  | 0.0245 | 0.1545 | [22 empty] | 0.5737 | -0.0917 |  |  |  |  | 0.31 | -0.1225 |  |  |  |  | 0.31 | -0.087917 |  |  |  |  | 0.31 | -0.087917
0.0218 | 0.1462 |  |  |  |  | 0.0218 | 0.1462 | [22 empty] | 0.5883 | -0.0864 |  |  |  |  | 0.32 | -0.1223 |  |  |  |  | 0.32 | -0.087427 |  |  |  |  | 0.32 | -0.087427
0.0194 | 0.1378 |  |  |  |  | 0.0194 | 0.1378 | [22 empty] | 0.603 | -0.081 |  |  |  |  | 0.33 | -0.1219 |  |  |  |  | 0.33 | -0.086818 |  |  |  |  | 0.33 | -0.086818
0.017 | 0.1294 |  |  |  |  | 0.017 | 0.1294 | [22 empty] | 0.6176 | -0.0757 |  |  |  |  | 0.34 | -0.1214 |  |  |  |  | 0.34 | -0.086096 |  |  |  |  | 0.34 | -0.086096
0.0149 | 0.121 |  |  |  |  | 0.0149 | 0.121 | [22 empty] | 0.6321 | -0.0704 |  |  |  |  | 0.35 | -0.1207 |  |  |  |  | 0.35 | -0.085264 |  |  |  |  | 0.35 | -0.085264
0.0128 | 0.1125 |  |  |  |  | 0.0128 | 0.1125 | [22 empty] | 0.6464 | -0.0652 |  |  |  |  | 0.36 | -0.1199 |  |  |  |  | 0.36 | -0.084331 |  |  |  |  | 0.36 | -0.084331
0.0109 | 0.104 |  |  |  |  | 0.0109 | 0.104 | [22 empty] | 0.6606 | -0.0602 |  |  |  |  | 0.37 | -0.1189 |  |  |  |  | 0.37 | -0.083294 |  |  |  |  | 0.37 | -0.083294
0.0092 | 0.0954 |  |  |  |  | 0.0092 | 0.0954 | [22 empty] | 0.6747 | -0.0552 |  |  |  |  | 0.38 | -0.1179 |  |  |  |  | 0.38 | -0.082158 |  |  |  |  | 0.38 | -0.082158
0.0076 | 0.0868 |  |  |  |  | 0.0076 | 0.0868 | [22 empty] | 0.6885 | -0.0503 |  |  |  |  | 0.39 | -0.1166 |  |  |  |  | 0.39 | -0.080927 |  |  |  |  | 0.39 | -0.080927
0.0062 | 0.0782 |  |  |  |  | 0.0062 | 0.0782 | [22 empty] | 0.7022 | -0.0457 |  |  |  |  | 0.4 | -0.1153 |  |  |  |  | 0.4 | -0.079601 |  |  |  |  | 0.4 | -0.079601
0.0049 | 0.0696 |  |  |  |  | 0.0049 | 0.0696 | [22 empty] | 0.7158 | -0.0411 |  |  |  |  | 0.41 | -0.1138 |  |  |  |  | 0.41 | -0.078181 |  |  |  |  | 0.41 | -0.078181
0.0037 | 0.0609 |  |  |  |  | 0.0037 | 0.0609 | [22 empty] | 0.7291 | -0.0368 |  |  |  |  | 0.42 | -0.1122 |  |  |  |  | 0.42 | -0.076669 |  |  |  |  | 0.42 | -0.076669
0.0027 | 0.0523 |  |  |  |  | 0.0027 | 0.0523 | [22 empty] | 0.7423 | -0.0326 |  |  |  |  | 0.43 | -0.1105 |  |  |  |  | 0.43 | -0.075065 |  |  |  |  | 0.43 | -0.075065
0.0019 | 0.0436 |  |  |  |  | 0.0019 | 0.0436 | [22 empty] | 0.7552 | -0.0287 |  |  |  |  | 0.44 | -0.1086 |  |  |  |  | 0.44 | -0.073371 |  |  |  |  | 0.44 | -0.073371
0.0012 | 0.0349 |  |  |  |  | 0.0012 | 0.0349 | [22 empty] | 0.7679 | -0.0249 |  |  |  |  | 0.45 | -0.1066 |  |  |  |  | 0.45 | -0.071592 |  |  |  |  | 0.45 | -0.071592
0.0007 | 0.0262 |  |  |  |  | 0.0007 | 0.0262 | [22 empty] | 0.7803 | -0.0215 |  |  |  |  | 0.475 | -0.101 |  |  |  |  | 0.475 | -0.066783 |  |  |  |  | 0.475 | -0.066783
0.0003 | 0.0174 |  |  |  |  | 0.0003 | 0.0174 | [22 empty] | 0.7926 | -0.0182 |  |  |  |  | 0.5 | -0.0947 |  |  |  |  | 0.5 | -0.061496 |  |  |  |  | 0.5 | -0.061496
0.0001 | 0.0087 |  |  |  |  | 0.0001 | 0.0087 | [22 empty] | 0.8046 | -0.0152 |  |  |  |  | 0.525 | -0.0877 |  |  |  |  | 0.525 | -0.055781 |  |  |  |  | 0.525 | -0.055781
0 | 0 |  |  |  |  | 0 | 0 | [22 empty] | 0.8165 | -0.0125 |  |  |  |  | 0.55 | -0.0801 |  |  |  |  | 0.55 | -0.049729 |  |  |  |  | 0.55 | -0.049729
0.0001 | -0.0087 |  |  |  |  | 0.0001 | -0.0087 | [22 empty] | 0.8282 | -0.01 |  |  |  |  | 0.575 | -0.0721 |  |  |  |  | 0.575 | -0.043425 |  |  |  |  | 0.575 | -0.043425
0.0003 | -0.0174 |  |  |  |  | 0.0003 | -0.0174 | [22 empty] | 0.8398 | -0.0078 |  |  |  |  | 0.6 | -0.0636 |  |  |  |  | 0.6 | -0.036944 |  |  |  |  | 0.6 | -0.036944
0.0007 | -0.0262 |  |  |  |  | 0.0007 | -0.0262 | [22 empty] | 0.8511 | -0.0058 |  |  |  |  | 0.625 | -0.0549 |  |  |  |  | 0.625 | -0.03038 |  |  |  |  | 0.625 | -0.03038
0.0012 | -0.0349 |  |  |  |  | 0.0012 | -0.0349 | [22 empty] | 0.8623 | -0.0041 |  |  |  |  | 0.65 | -0.046 |  |  |  |  | 0.65 | -0.023854 |  |  |  |  | 0.65 | -0.023854
0.0019 | -0.0436 |  |  |  |  | 0.0019 | -0.0436 | [22 empty] | 0.8733 | -0.0027 |  |  |  |  | 0.675 | -0.0372 |  |  |  |  | 0.675 | -0.017511 |  |  |  |  | 0.675 | -0.017511
0.0027 | -0.0523 |  |  |  |  | 0.0027 | -0.0523 | [22 empty] | 0.8842 | -0.0015 |  |  |  |  | 0.7 | -0.0287 |  |  |  |  | 0.7 | -0.011505 |  |  |  |  | 0.7 | -0.011505
0.0037 | -0.0609 |  |  |  |  | 0.0037 | -0.0609 | [22 empty] | 0.895 | -0.0006 |  |  |  |  | 0.725 | -0.0206 |  |  |  |  | 0.725 | -0.00597 |  |  |  |  | 0.725 | -0.00597
0.0049 | -0.0696 |  |  |  |  | 0.0049 | -0.0696 | [22 empty] | 0.9056 | 0 |  |  |  |  | 0.75 | -0.0131 |  |  |  |  | 0.75 | -0.001047 |  |  |  |  | 0.75 | -0.001047
0.0062 | -0.0782 |  |  |  |  | 0.0062 | -0.0782 | [22 empty] | 0.9161 | 0.0004 |  |  |  |  | 0.775 | -0.0065 |  |  |  |  | 0.775 | 0.003119 |  |  |  |  | 0.775 | 0.003119
0.0076 | -0.0868 |  |  |  |  | 0.0076 | -0.0868 | [22 empty] | 0.9263 | 0.0005 |  |  |  |  | 0.8 | -0.0009 |  |  |  |  | 0.8 | 0.006352 |  |  |  |  | 0.8 | 0.006352
0.0092 | -0.0954 |  |  |  |  | 0.0092 | -0.0954 | [22 empty] | 0.9363 | 0.0004 |  |  |  |  | 0.825 | 0.0035 |  |  |  |  | 0.825 | 0.008554 |  |  |  |  | 0.825 | 0.008554
0.0109 | -0.104 |  |  |  |  | 0.0109 | -0.104 | [22 empty] | 0.9458 | 0 |  |  |  |  | 0.85 | 0.0066 |  |  |  |  | 0.85 | 0.009729 |  |  |  |  | 0.85 | 0.009729
0.0128 | -0.1125 |  |  |  |  | 0.0128 | -0.1125 | [22 empty] | 0.9549 | -0.0006 |  |  |  |  | 0.875 | 0.0084 |  |  |  |  | 0.875 | 0.009877 |  |  |  |  | 0.875 | 0.009877
0.0149 | -0.121 |  |  |  |  | 0.0149 | -0.121 | [22 empty] | 0.9636 | -0.0015 |  |  |  |  | 0.9 | 0.0088 |  |  |  |  | 0.9 | 0.009017 |  |  |  |  | 0.9 | 0.009017
0.017 | -0.1294 |  |  |  |  | 0.017 | -0.1294 | [22 empty] | 0.972 | -0.0027 |  |  |  |  | 0.91 | 0.0085 |  |  |  |  | 0.91 | 0.008408 |  |  |  |  | 0.91 | 0.008408
0.0194 | -0.1378 |  |  |  |  | 0.0194 | -0.1378 | [22 empty] | 0.9799 | -0.004 |  |  |  |  | 0.92 | 0.008 |  |  |  |  | 0.92 | 0.00766 |  |  |  |  | 0.92 | 0.00766
0.0218 | -0.1462 |  |  |  |  | 0.0218 | -0.1462 | [22 empty] | 0.9872 | -0.0055 |  |  |  |  | 0.93 | 0.0073 |  |  |  |  | 0.93 | 0.006781 |  |  |  |  | 0.93 | 0.006781
0.0245 | -0.1545 |  |  |  |  | 0.0245 | -0.1545 | [22 empty] | 0.994 | -0.0071 |  |  |  |  | 0.94 | 0.0063 |  |  |  |  | 0.94 | 0.005781 |  |  |  |  | 0.94 | 0.005781
0.0272 | -0.1628 |  |  |  |  | 0.0272 | -0.1628 | [22 empty] | 1 | -0.0087 |  |  |  |  | 0.95 | 0.0051 |  |  |  |  | 0.95 | 0.004675 |  |  |  |  | 0.95 | 0.004675
0.0302 | -0.171 |  |  |  |  | 0.0302 | -0.171 | [28 empty] | 0.96 | 0.0036 |  |  |  |  | 0.96 | 0.003486 |  |  |  |  | 0.96 | 0.003486
0.0332 | -0.1792 |  |  |  |  | 0.0332 | -0.1792 | [28 empty] | 0.97 | 0.0021 |  |  |  |  | 0.97 | 0.00223 |  |  |  |  | 0.97 | 0.00223
0.0364 | -0.1873 |  |  |  |  | 0.0364 | -0.1873 | [28 empty] | 0.98 | 0 |  |  |  |  | 0.98 | 0.000949 |  |  |  |  | 0.98 | 0.000949
0.0397 | -0.1954 |  |  |  |  | 0.0397 | -0.1954 | [28 empty] | 0.99 | -0.001 |  |  |  |  | 0.99 | -0.000327 |  |  |  |  | 0.99 | -0.000327
0.0432 | -0.2034 |  |  |  |  | 0.0432 | -0.2034 | [28 empty] | 1 | 0 |  |  |  |  | 1 | -0.001392 |  |  |  |  | 1 | -0.001392
0.0468 | -0.2113 |  |  |  |  | 0.0468 | -0.2113
0.0506 | -0.2192 |  |  |  |  | 0.0506 | -0.2192
0.0545 | -0.227 |  |  |  |  | 0.0545 | -0.227
0.0585 | -0.2347 |  |  |  |  | 0.0585 | -0.2347
0.0627 | -0.2424 |  |  |  |  | 0.0627 | -0.2424
0.067 | -0.25 |  |  |  |  | 0.067 | -0.25
0.0714 | -0.2575 |  |  |  |  | 0.0714 | -0.2575
0.076 | -0.265 |  |  |  |  | 0.076 | -0.265
0.0807 | -0.2723 |  |  |  |  | 0.0807 | -0.2723
0.0855 | -0.2796 |  |  |  |  | 0.0855 | -0.2796
0.0904 | -0.2868 |  |  |  |  | 0.0904 | -0.2868
0.0955 | -0.2939 |  |  |  |  | 0.0955 | -0.2939
0.1007 | -0.3009 |  |  |  |  | 0.1007 | -0.3009
0.106 | -0.3078 |  |  |  |  | 0.106 | -0.3078
0.1114 | -0.3147 |  |  |  |  | 0.1114 | -0.3147
0.117 | -0.3214 |  |  |  |  | 0.117 | -0.3214
0.1226 | -0.328 |  |  |  |  | 0.1226 | -0.328
0.1284 | -0.3346 |  |  |  |  | 0.1284 | -0.3346
0.1343 | -0.341 |  |  |  |  | 0.1343 | -0.341
0.1403 | -0.3473 |  |  |  |  | 0.1403 | -0.3473
0.1464 | -0.3536 |  |  |  |  | 0.1464 | -0.3536
0.1527 | -0.3597 |  |  |  |  | 0.1527 | -0.3597
0.159 | -0.3657 |  |  |  |  | 0.159 | -0.3657
0.1654 | -0.3716 |  |  |  |  | 0.1654 | -0.3716
0.172 | -0.3774 |  |  |  |  | 0.172 | -0.3774
0.1786 | -0.383 |  |  |  |  | 0.1786 | -0.383
0.1853 | -0.3886 |  |  |  |  | 0.1853 | -0.3886
0.1922 | -0.394 |  |  |  |  | 0.1922 | -0.394
0.1991 | -0.3993 |  |  |  |  | 0.1991 | -0.3993
0.2061 | -0.4045 |  |  |  |  | 0.2061 | -0.4045
0.2132 | -0.4096 |  |  |  |  | 0.2132 | -0.4096
0.2204 | -0.4145 |  |  |  |  | 0.2204 | -0.4145
0.2277 | -0.4193 |  |  |  |  | 0.2277 | -0.4193
0.235 | -0.424 |  |  |  |  | 0.235 | -0.424
0.2425 | -0.4286 |  |  |  |  | 0.2425 | -0.4286
0.25 | -0.433 |  |  |  |  | 0.25 | -0.433
0.2576 | -0.4373 |  |  |  |  | 0.2576 | -0.4373
0.2653 | -0.4415 |  |  |  |  | 0.2653 | -0.4415
0.273 | -0.4455 |  |  |  |  | 0.273 | -0.4455
0.2808 | -0.4494 |  |  |  |  | 0.2808 | -0.4494
0.2887 | -0.4532 |  |  |  |  | 0.2887 | -0.4532
0.2966 | -0.4568 |  |  |  |  | 0.2966 | -0.4568
0.3046 | -0.4603 |  |  |  |  | 0.3046 | -0.4603
0.3127 | -0.4636 |  |  |  |  | 0.3127 | -0.4636
0.3208 | -0.4668 |  |  |  |  | 0.3208 | -0.4668
0.329 | -0.4698 |  |  |  |  | 0.329 | -0.4698
0.3372 | -0.4728 |  |  |  |  | 0.3372 | -0.4728
0.3455 | -0.4755 |  |  |  |  | 0.3455 | -0.4755
0.3538 | -0.4782 |  |  |  |  | 0.3538 | -0.4782
0.3622 | -0.4806 |  |  |  |  | 0.3622 | -0.4806
0.3706 | -0.483 |  |  |  |  | 0.3706 | -0.483
0.379 | -0.4851 |  |  |  |  | 0.379 | -0.4851
0.3875 | -0.4872 |  |  |  |  | 0.3875 | -0.4872
0.396 | -0.4891 |  |  |  |  | 0.396 | -0.4891
0.4046 | -0.4908 |  |  |  |  | 0.4046 | -0.4908
0.4132 | -0.4924 |  |  |  |  | 0.4132 | -0.4924
0.4218 | -0.4938 |  |  |  |  | 0.4218 | -0.4938
0.4304 | -0.4951 |  |  |  |  | 0.4304 | -0.4951
0.4391 | -0.4963 |  |  |  |  | 0.4391 | -0.4963
0.4477 | -0.4973 |  |  |  |  | 0.4477 | -0.4973
0.4564 | -0.4981 |  |  |  |  | 0.4564 | -0.4981
0.4651 | -0.4988 |  |  |  |  | 0.4651 | -0.4988
0.4738 | -0.4993 |  |  |  |  | 0.4738 | -0.4993
0.4826 | -0.4997 |  |  |  |  | 0.4826 | -0.4997
0.4913 | -0.4999 |  |  |  |  | 0.4913 | -0.4999
0.5 | -0.5 |  |  |  |  | 0.5 | -0.5
0.5087 | -0.4999 |  |  |  |  | 0.5087 | -0.4999
0.5174 | -0.4997 |  |  |  |  | 0.5174 | -0.4997
0.5262 | -0.4993 |  |  |  |  | 0.5262 | -0.4993
0.5349 | -0.4988 |  |  |  |  | 0.5349 | -0.4988
0.5436 | -0.4981 |  |  |  |  | 0.5436 | -0.4981
0.5523 | -0.4973 |  |  |  |  | 0.5523 | -0.4973
0.5609 | -0.4963 |  |  |  |  | 0.5609 | -0.4963
0.5696 | -0.4951 |  |  |  |  | 0.5696 | -0.4951
0.5782 | -0.4938 |  |  |  |  | 0.5782 | -0.4938
0.5868 | -0.4924 |  |  |  |  | 0.5868 | -0.4924
0.5954 | -0.4908 |  |  |  |  | 0.5954 | -0.4908
0.604 | -0.4891 |  |  |  |  | 0.604 | -0.4891
0.6125 | -0.4872 |  |  |  |  | 0.6125 | -0.4872
0.621 | -0.4851 |  |  |  |  | 0.621 | -0.4851
0.6294 | -0.483 |  |  |  |  | 0.6294 | -0.483
0.6378 | -0.4806 |  |  |  |  | 0.6378 | -0.4806
0.6462 | -0.4782 |  |  |  |  | 0.6462 | -0.4782
0.6545 | -0.4755 |  |  |  |  | 0.6545 | -0.4755
0.6628 | -0.4728 |  |  |  |  | 0.6628 | -0.4728
0.671 | -0.4698 |  |  |  |  | 0.671 | -0.4698
0.6792 | -0.4668 |  |  |  |  | 0.6792 | -0.4668
0.6873 | -0.4636 |  |  |  |  | 0.6873 | -0.4636
0.6954 | -0.4603 |  |  |  |  | 0.6954 | -0.4603
0.7034 | -0.4568 |  |  |  |  | 0.7034 | -0.4568
0.7113 | -0.4532 |  |  |  |  | 0.7113 | -0.4532
0.7192 | -0.4494 |  |  |  |  | 0.7192 | -0.4494
0.727 | -0.4455 |  |  |  |  | 0.727 | -0.4455
0.7347 | -0.4415 |  |  |  |  | 0.7347 | -0.4415
0.7424 | -0.4373 |  |  |  |  | 0.7424 | -0.4373
0.75 | -0.433 |  |  |  |  | 0.75 | -0.433
0.7575 | -0.4286 |  |  |  |  | 0.7575 | -0.4286
0.765 | -0.424 |  |  |  |  | 0.765 | -0.424
0.7723 | -0.4193 |  |  |  |  | 0.7723 | -0.4193
0.7796 | -0.4145 |  |  |  |  | 0.7796 | -0.4145
0.7868 | -0.4096 |  |  |  |  | 0.7868 | -0.4096
0.7939 | -0.4045 |  |  |  |  | 0.7939 | -0.4045
0.8009 | -0.3993 |  |  |  |  | 0.8009 | -0.3993
0.8078 | -0.394 |  |  |  |  | 0.8078 | -0.394
0.8147 | -0.3886 |  |  |  |  | 0.8147 | -0.3886
0.8214 | -0.383 |  |  |  |  | 0.8214 | -0.383
0.828 | -0.3774 |  |  |  |  | 0.828 | -0.3774
0.8346 | -0.3716 |  |  |  |  | 0.8346 | -0.3716
0.841 | -0.3657 |  |  |  |  | 0.841 | -0.3657
0.8473 | -0.3597 |  |  |  |  | 0.8473 | -0.3597
0.8536 | -0.3536 |  |  |  |  | 0.8536 | -0.3536
0.8597 | -0.3473 |  |  |  |  | 0.8597 | -0.3473
0.8657 | -0.341 |  |  |  |  | 0.8657 | -0.341
0.8716 | -0.3346 |  |  |  |  | 0.8716 | -0.3346
0.8774 | -0.328 |  |  |  |  | 0.8774 | -0.328
0.883 | -0.3214 |  |  |  |  | 0.883 | -0.3214
0.8886 | -0.3147 |  |  |  |  | 0.8886 | -0.3147
0.894 | -0.3078 |  |  |  |  | 0.894 | -0.3078
0.8993 | -0.3009 |  |  |  |  | 0.8993 | -0.3009
0.9045 | -0.2939 |  |  |  |  | 0.9045 | -0.2939
0.9096 | -0.2868 |  |  |  |  | 0.9096 | -0.2868
0.9145 | -0.2796 |  |  |  |  | 0.9145 | -0.2796
0.9193 | -0.2723 |  |  |  |  | 0.9193 | -0.2723
0.924 | -0.265 |  |  |  |  | 0.924 | -0.265
0.9286 | -0.2575 |  |  |  |  | 0.9286 | -0.2575
0.933 | -0.25 |  |  |  |  | 0.933 | -0.25
0.9373 | -0.2424 |  |  |  |  | 0.9373 | -0.2424
0.9415 | -0.2347 |  |  |  |  | 0.9415 | -0.2347
0.9455 | -0.227 |  |  |  |  | 0.9455 | -0.227
0.9494 | -0.2192 |  |  |  |  | 0.9494 | -0.2192
0.9532 | -0.2113 |  |  |  |  | 0.9532 | -0.2113
0.9568 | -0.2034 |  |  |  |  | 0.9568 | -0.2034
0.9603 | -0.1954 |  |  |  |  | 0.9603 | -0.1954
0.9636 | -0.1873 |  |  |  |  | 0.9636 | -0.1873
0.9668 | -0.1792 |  |  |  |  | 0.9668 | -0.1792
0.9698 | -0.171 |  |  |  |  | 0.9698 | -0.171
0.9728 | -0.1628 |  |  |  |  | 0.9728 | -0.1628
0.9755 | -0.1545 |  |  |  |  | 0.9755 | -0.1545
0.9782 | -0.1462 |  |  |  |  | 0.9782 | -0.1462
0.9806 | -0.1378 |  |  |  |  | 0.9806 | -0.1378
0.983 | -0.1294 |  |  |  |  | 0.983 | -0.1294
0.9851 | -0.121 |  |  |  |  | 0.9851 | -0.121
0.9872 | -0.1125 |  |  |  |  | 0.9872 | -0.1125
0.9891 | -0.104 |  |  |  |  | 0.9891 | -0.104
0.9908 | -0.0954 |  |  |  |  | 0.9908 | -0.0954
0.9924 | -0.0868 |  |  |  |  | 0.9924 | -0.0868
0.9938 | -0.0782 |  |  |  |  | 0.9938 | -0.0782
0.9951 | -0.0696 |  |  |  |  | 0.9951 | -0.0696
0.9963 | -0.0609 |  |  |  |  | 0.9963 | -0.0609
0.9973 | -0.0523 |  |  |  |  | 0.9973 | -0.0523
0.9981 | -0.0436 |  |  |  |  | 0.9981 | -0.0436
0.9988 | -0.0349 |  |  |  |  | 0.9988 | -0.0349
0.9993 | -0.0262 |  |  |  |  | 0.9993 | -0.0262
0.9997 | -0.0174 |  |  |  |  | 0.9997 | -0.0174
0.9999 | -0.0087 |  |  |  |  | 0.9999 | -0.0087
1 | 0 |  |  |  |  | 1 | 0

## BladeTopology
Eta | Sectional Topology | Position of Front Web | Position of Rear Web | Position Spar Cap towards Leading Edge on Suction Side | Position Spar Cap towards Trailing Edge on Suction Side | Width of the Spar Cap on Suction Side | Position Spar Cap towards Leading Edge on Pressure Side | Position Spar Cap towards Trailing Edge on Pressure Side | Width of the Spar Cap on Pressure Side | Extension of the Reinforcement Strip at Leading Edge | Extension of the Reinforcement Strip at Trailing Edge | Position of the Third Web | Angle of the Webs in the Root Reference Frame | Position of Trailing Edge Add On | Position of Extra Web inside the Trailing Edge Add On | Position of Reinforcement inside the Cylinder
[-] | [-] | [mm] | [mm] | [mm] | [mm] | [mm] | [mm] | [mm] | [mm] | [mm] | [mm] | [mm] | [deg] | [mm] | [mm] | [mm]
0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.01 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.02 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.03 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.04 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.06 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.07 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.1 | 2 | -257.6 | 342.4 | -357.6 | 442.4 | 800 | -357.6 | 442.4 | 800 | 89.6825 | 474.3242 | 0 | 0 | 0 | 0 | 0
0.12 | 2 | -252.2488 | 347.7512 | -352.2488 | 447.7512 | 800 | -352.2488 | 447.7512 | 800 | 89.6825 | 459.1365 | 0 | 0 | 0 | 0 | 0
0.14 | 2 | -246.8976 | 353.1024 | -346.8976 | 453.1024 | 800 | -346.8976 | 453.1024 | 800 | 89.6825 | 436.2848 | 0 | 0 | 0 | 0 | 0
0.16 | 2 | -241.5464 | 358.4536 | -341.5464 | 458.4536 | 800 | -341.5464 | 458.4536 | 800 | 89.6825 | 403.8032 | 0 | 0 | 0 | 0 | 0
0.18 | 2 | -236.1951 | 363.8049 | -336.1951 | 463.8049 | 800 | -336.1951 | 463.8049 | 800 | 89.6825 | 366.3872 | 0 | 0 | 0 | 0 | 0
0.2 | 2 | -233.5195 | 366.4805 | -333.5195 | 466.4805 | 800 | -333.5195 | 466.4805 | 800 | 89.6825 | 357.1429 | 0 | 0 | 0 | 0 | 0
0.22 | 2 | -228.1683 | 371.8317 | -328.1683 | 471.8317 | 800 | -328.1683 | 471.8317 | 800 | 89.6825 | 347.619 | 0 | 0 | 0 | 0 | 0
0.24 | 2 | -222.8171 | 377.1829 | -322.8171 | 477.1829 | 800 | -322.8171 | 477.1829 | 800 | 89.6825 | 338.0952 | 0 | 0 | 0 | 0 | 0
0.26 | 2 | -217.4659 | 382.5341 | -317.4659 | 482.5341 | 800 | -317.4659 | 482.5341 | 800 | 88.0952 | 328.5714 | 0 | 0 | 0 | 0 | 0
0.28 | 2 | -212.1147 | 387.8853 | -312.1147 | 487.8853 | 800 | -312.1147 | 487.8853 | 800 | 86.5079 | 319.0476 | 0 | 0 | 0 | 0 | 0
0.3 | 2 | -209.4391 | 390.5609 | -309.4391 | 490.5609 | 800 | -309.4391 | 490.5609 | 800 | 85.7143 | 314.2857 | 0 | 0 | 0 | 0 | 0
0.32 | 2 | -204.0879 | 395.9121 | -304.0879 | 495.9121 | 800 | -304.0879 | 495.9121 | 800 | 84.127 | 304.7619 | 0 | 0 | 0 | 0 | 0
0.34 | 2 | -198.7367 | 401.2633 | -298.7367 | 501.2633 | 800 | -298.7367 | 501.2633 | 800 | 82.5397 | 295.2381 | 0 | 0 | 0 | 0 | 0
0.36 | 2 | -193.3854 | 406.6146 | -293.3854 | 506.6146 | 800 | -293.3854 | 506.6146 | 800 | 80.9524 | 285.7143 | 0 | 0 | 0 | 0 | 0
0.38 | 2 | -188.0342 | 411.9658 | -288.0342 | 511.9658 | 800 | -288.0342 | 511.9658 | 800 | 79.3651 | 276.1905 | 0 | 0 | 0 | 0 | 0
0.4 | 2 | -185.3586 | 414.6414 | -285.3586 | 514.6414 | 800 | -285.3586 | 514.6414 | 800 | 78.5714 | 271.4286 | 0 | 0 | 0 | 0 | 0
0.42 | 2 | -180.0074 | 419.9926 | -280.0074 | 519.9926 | 800 | -280.0074 | 519.9926 | 800 | 76.9841 | 261.9048 | 0 | 0 | 0 | 0 | 0
0.44 | 2 | -174.6562 | 425.3438 | -274.6562 | 525.3438 | 800 | -274.6562 | 525.3438 | 800 | 75.3968 | 252.381 | 0 | 0 | 0 | 0 | 0
0.46 | 2 | -169.305 | 430.695 | -269.305 | 530.695 | 800 | -269.305 | 530.695 | 800 | 73.8095 | 242.8571 | 0 | 0 | 0 | 0 | 0
0.48 | 2 | -163.9538 | 436.0462 | -263.9538 | 536.0462 | 800 | -263.9538 | 536.0462 | 800 | 72.2222 | 233.3333 | 0 | 0 | 0 | 0 | 0
0.5 | 2 | -161.2782 | 438.7218 | -261.2782 | 538.7218 | 800 | -261.2782 | 538.7218 | 800 | 71.4286 | 228.5714 | 0 | 0 | 0 | 0 | 0
0.52 | 2 | -155.9269 | 444.0731 | -255.9269 | 544.0731 | 800 | -255.9269 | 544.0731 | 800 | 69.8413 | 219.0476 | 0 | 0 | 0 | 0 | 0
0.54 | 2 | -150.5757 | 449.4243 | -250.5757 | 549.4243 | 800 | -250.5757 | 549.4243 | 800 | 68.254 | 209.5238 | 0 | 0 | 0 | 0 | 0
0.56 | 2 | -145.2245 | 454.7755 | -245.2245 | 554.7755 | 800 | -245.2245 | 554.7755 | 800 | 66.6667 | 200 | 0 | 0 | 0 | 0 | 0
0.58 | 2 | -139.8733 | 460.1267 | -239.8733 | 560.1267 | 800 | -239.8733 | 560.1267 | 800 | 65.0794 | 190.4762 | 0 | 0 | 0 | 0 | 0
0.6 | 2 | -137.1977 | 462.8023 | -237.1977 | 562.8023 | 800 | -237.1977 | 562.8023 | 800 | 64.2857 | 185.7143 | 0 | 0 | 0 | 0 | 0
0.62 | 2 | -131.8465 | 468.1535 | -231.8465 | 568.1535 | 800 | -231.8465 | 568.1535 | 800 | 62.6984 | 176.1905 | 0 | 0 | 0 | 0 | 0
0.64 | 2 | -126.4953 | 473.5047 | -226.4953 | 573.5047 | 800 | -226.4953 | 573.5047 | 800 | 61.1111 | 166.6667 | 0 | 0 | 0 | 0 | 0
0.66 | 2 | -121.1441 | 478.8559 | -221.1441 | 578.8559 | 800 | -221.1441 | 578.8559 | 800 | 59.5238 | 157.1429 | 0 | 0 | 0 | 0 | 0
0.68 | 2 | -115.7928 | 484.2072 | -215.7928 | 584.2072 | 800 | -215.7928 | 584.2072 | 800 | 57.9365 | 147.619 | 0 | 0 | 0 | 0 | 0
0.7 | 2 | -113.1172 | 486.8828 | -213.1172 | 586.8828 | 800 | -213.1172 | 586.8828 | 800 | 57.1429 | 142.8571 | 0 | 0 | 0 | 0 | 0
0.72 | 2 | -107.766 | 492.234 | -207.766 | 592.234 | 800 | -207.766 | 592.234 | 800 | 54.1682 | 134.7207 | 0 | 0 | 0 | 0 | 0
0.74 | 2 | -102.4148 | 497.5852 | -202.4148 | 597.5852 | 800 | -202.4148 | 597.5852 | 800 | 48.9974 | 128.7804 | 0 | 0 | 0 | 0 | 0
0.76 | 2 | -97.0636 | 502.9364 | -197.0636 | 602.9364 | 800 | -197.0636 | 602.9364 | 800 | 43.9103 | 122.7564 | 0 | 0 | 0 | 0 | 0
0.78 | 2 | -91.7124 | 508.2876 | -191.7124 | 608.2876 | 800 | -191.7124 | 608.2876 | 800 | 39.2482 | 116.3074 | 0 | 0 | 0 | 0 | 0
0.8 | 2 | -89.0368 | 510.9632 | -189.0368 | 610.9632 | 800 | -189.0368 | 610.9632 | 800 | 37.0733 | 112.9267 | 0 | 0 | 0 | 0 | 0
0.82 | 2 | -83.6856 | 516.3144 | -183.6856 | 616.3144 | 800 | -183.6856 | 616.3144 | 800 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.84 | 2 | -78.3344 | 521.6656 | -178.3344 | 621.6656 | 800 | -178.3344 | 621.6656 | 800 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.86 | 2 | -72.9831 | 527.0169 | -172.9831 | 627.0169 | 800 | -172.9831 | 627.0169 | 800 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.88 | 2 | -67.6319 | 532.3681 | -167.6319 | 632.3681 | 800 | -167.6319 | 632.3681 | 800 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.9 | 2 | -64.9563 | 535.0437 | -164.9563 | 635.0437 | 800 | -164.9563 | 635.0437 | 800 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.92 | 2 | -59.6051 | 540.3949 | -159.6051 | 640.3949 | 800 | -159.6051 | 640.3949 | 800 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.94 | 2 | -54.2539 | 545.7461 | -154.2539 | 645.7461 | 800 | -154.2539 | 645.7461 | 800 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.96 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.98 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note on B1: Pietro Bortolotti: 1: root cylinder 2: traditional structure with 2 or 3 webs 3: tip region 4: industrial specific 5: industrial specific

## BladeCompThickness
Eta | Topology | Thickness Shell Skin on Trailing Edge Suction Side | Thickness Shell Skin on Leading Edge Suction Side | Thickness Shell Skin on Leading Edge Pressure Side | Thickness Shell Skin on Trailing Edge Pressure Side | Thickness Root Reinforcement | Thickness Suction Spar Cap | Thickness Pressure Spar Cap | Thickness Front Web | Thickness Rear Web | Thickness Third Web | Thickness Reinforcement at Leading Edge | Thickness Reinforcement at Trailing Edge | Thickness Extra Structural Component 1 | Thickness Extra Structural Component 2 | Thickness Extra Structural Component 3 | Thickness Sandwich Core at Trailing Edge Suction Side | Thickness Sandwich Core at Leading Edge Suction Side | Thickness Sandwich Core at Leading Edge Pressure Side | Thickness Sandwich Core at Trailing Edge Pressure Side | Thickness Sandwich Core Front Web | Thickness Sandwich Core Rear Web | Thickness Sandwich Core Third Web
[-] | [-] | [mm] | [mm] | [mm] | [mm] | [mm] | [mm] | [mm] | [mm] | [mm] | [mm] | [mm] | [mm] | [mm] | [mm] | [mm] | [mm] | [mm] | [mm] | [mm] | [mm] | [mm] | [mm]
0 | 1 | 65 | 65 | 65 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.01 | 1 | 60 | 60 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.02 | 1 | 55 | 55 | 55 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.03 | 1 | 50 | 50 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.04 | 1 | 45.7143 | 45.7143 | 45.7143 | 45.7143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2857 | 0.71429 | 0.14286 | 1.2857 | 6.1429 | 7 | 0
0.05 | 1 | 41.4286 | 41.4286 | 41.4286 | 41.4286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5714 | 1.4286 | 0.28571 | 2.5714 | 12.2857 | 14 | 0
0.06 | 1 | 37.1429 | 37.1429 | 37.1429 | 37.1429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8571 | 2.1429 | 0.42857 | 3.8571 | 18.4286 | 21 | 0
0.07 | 1 | 32.8571 | 32.8571 | 32.8571 | 32.8571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1429 | 2.8571 | 0.57143 | 5.1429 | 24.5714 | 28 | 0
0.08 | 1 | 28.5714 | 28.5714 | 28.5714 | 28.5714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4286 | 3.5714 | 0.71429 | 6.4286 | 30.7143 | 35 | 0
0.1 | 2 | 20 | 20 | 20 | 20 | 0 | 9.9333 | 9.9333 | 1 | 1 | 0 | 3.1006 | 1.1773 | 0 | 0 | 0 | 9 | 5 | 1 | 9 | 43 | 49 | 0
0.12 | 2 | 16.8677 | 16.8677 | 16.8677 | 16.8677 | 0 | 15.9467 | 15.9467 | 1.0822 | 1.0822 | 0 | 3.1852 | 2.2404 | 0 | 0 | 0 | 16.2 | 7 | 3.4 | 14.6 | 41 | 47 | 0
0.14 | 2 | 13.7353 | 13.7353 | 13.7353 | 13.7353 | 0 | 21.96 | 21.96 | 1.1644 | 1.1644 | 0 | 3.2698 | 3.3036 | 0 | 0 | 0 | 23.4 | 9 | 5.8 | 20.2 | 39 | 45 | 0
0.16 | 2 | 10.603 | 10.603 | 10.603 | 10.603 | 0 | 27.9733 | 27.9733 | 1.2465 | 1.2465 | 0 | 3.3544 | 4.3668 | 0 | 0 | 0 | 30.6 | 11 | 8.2 | 25.8 | 37 | 43 | 0
0.18 | 2 | 7.4707 | 7.4707 | 7.4707 | 7.4707 | 0 | 33.9867 | 33.9867 | 1.3287 | 1.3287 | 0 | 3.439 | 5.4299 | 0 | 0 | 0 | 37.8 | 13 | 10.6 | 31.4 | 35 | 41 | 0
0.2 | 2 | 4.3383 | 4.3383 | 4.3383 | 4.3383 | 0 | 40 | 40 | 1.4109 | 1.4109 | 0 | 3.5235 | 6.4931 | 0 | 0 | 0 | 45 | 15 | 13 | 37 | 33 | 39 | 0
0.22 | 2 | 3.7444 | 3.7444 | 3.7444 | 3.7444 | 0 | 44.7599 | 44.7599 | 1.6132 | 1.6132 | 0 | 3.2582 | 6.6851 | 0 | 0 | 0 | 48.2 | 14.2 | 12.6 | 43.8 | 32.2 | 37.8 | 0
0.24 | 2 | 3.1504 | 3.1504 | 3.1504 | 3.1504 | 0 | 49.5198 | 49.5198 | 1.8155 | 1.8155 | 0 | 2.9929 | 6.8771 | 0 | 0 | 0 | 51.4 | 13.4 | 12.2 | 50.6 | 31.4 | 36.6 | 0
0.26 | 2 | 2.5565 | 2.5565 | 2.5565 | 2.5565 | 0 | 54.2798 | 54.2798 | 2.0177 | 2.0177 | 0 | 2.7276 | 7.0691 | 0 | 0 | 0 | 54.6 | 12.6 | 11.8 | 57.4 | 30.6 | 35.4 | 0
0.28 | 2 | 1.9626 | 1.9626 | 1.9626 | 1.9626 | 0 | 59.0397 | 59.0397 | 2.22 | 2.22 | 0 | 2.4623 | 7.261 | 0 | 0 | 0 | 57.8 | 11.8 | 11.4 | 64.2 | 29.8 | 34.2 | 0
0.3 | 2 | 1.3686 | 1.3686 | 1.3686 | 1.3686 | 0 | 63.7996 | 63.7996 | 2.4223 | 2.4223 | 0 | 2.197 | 7.453 | 0 | 0 | 0 | 61 | 11 | 11 | 71 | 29 | 33 | 0
0.32 | 2 | 1.3359 | 1.3359 | 1.3359 | 1.3359 | 0 | 61.2178 | 61.2178 | 2.4935 | 2.4935 | 0 | 2.0602 | 7.3203 | 0 | 0 | 0 | 60.6 | 10.6 | 10.6 | 68.2 | 28.2 | 31.8 | 0
0.34 | 2 | 1.3032 | 1.3032 | 1.3032 | 1.3032 | 0 | 58.6361 | 58.6361 | 2.5647 | 2.5647 | 0 | 1.9233 | 7.1876 | 0 | 0 | 0 | 60.2 | 10.2 | 10.2 | 65.4 | 27.4 | 30.6 | 0
0.36 | 2 | 1.2705 | 1.2705 | 1.2705 | 1.2705 | 0 | 56.0543 | 56.0543 | 2.6358 | 2.6358 | 0 | 1.7864 | 7.0549 | 0 | 0 | 0 | 59.8 | 9.8 | 9.8 | 62.6 | 26.6 | 29.4 | 0
0.38 | 2 | 1.2378 | 1.2378 | 1.2378 | 1.2378 | 0 | 53.4726 | 53.4726 | 2.707 | 2.707 | 0 | 1.6495 | 6.9222 | 0 | 0 | 0 | 59.4 | 9.4 | 9.4 | 59.8 | 25.8 | 28.2 | 0
0.4 | 2 | 1.2051 | 1.2051 | 1.2051 | 1.2051 | 0 | 50.8908 | 50.8908 | 2.7782 | 2.7782 | 0 | 1.5127 | 6.7895 | 0 | 0 | 0 | 59 | 9 | 9 | 57 | 25 | 27 | 0
0.42 | 2 | 1.1641 | 1.1641 | 1.1641 | 1.1641 | 0 | 50.4587 | 50.4587 | 2.8919 | 2.8919 | 0 | 1.4495 | 7.1995 | 0 | 0 | 0 | 55.4 | 8.6 | 9 | 51.8 | 23.8 | 25.4 | 0
0.44 | 2 | 1.123 | 1.123 | 1.123 | 1.123 | 0 | 50.0265 | 50.0265 | 3.0056 | 3.0056 | 0 | 1.3863 | 7.6096 | 0 | 0 | 0 | 51.8 | 8.2 | 9 | 46.6 | 22.6 | 23.8 | 0
0.46 | 2 | 1.082 | 1.082 | 1.082 | 1.082 | 0 | 49.5943 | 49.5943 | 3.1193 | 3.1193 | 0 | 1.3231 | 8.0196 | 0 | 0 | 0 | 48.2 | 7.8 | 9 | 41.4 | 21.4 | 22.2 | 0
0.48 | 2 | 1.041 | 1.041 | 1.041 | 1.041 | 0 | 49.1621 | 49.1621 | 3.233 | 3.233 | 0 | 1.2599 | 8.4297 | 0 | 0 | 0 | 44.6 | 7.4 | 9 | 36.2 | 20.2 | 20.6 | 0
0.5 | 2 | 1 | 1 | 1 | 1 | 0 | 48.7299 | 48.7299 | 3.3467 | 3.3467 | 0 | 1.1967 | 8.8397 | 0 | 0 | 0 | 41 | 7 | 9 | 31 | 19 | 19 | 0
0.52 | 2 | 1 | 1 | 1 | 1 | 0 | 47.2328 | 47.2328 | 3.4549 | 3.4549 | 0 | 1.2466 | 7.6705 | 0 | 0 | 0 | 39.4 | 7 | 9 | 29 | 18.2 | 17.8 | 0
0.54 | 2 | 1 | 1 | 1 | 1 | 0 | 45.7357 | 45.7357 | 3.5631 | 3.5631 | 0 | 1.2965 | 6.5013 | 0 | 0 | 0 | 37.8 | 7 | 9 | 27 | 17.4 | 16.6 | 0
0.56 | 2 | 1 | 1 | 1 | 1 | 0 | 44.2386 | 44.2386 | 3.6713 | 3.6713 | 0 | 1.3464 | 5.3321 | 0 | 0 | 0 | 36.2 | 7 | 9 | 25 | 16.6 | 15.4 | 0
0.58 | 2 | 1 | 1 | 1 | 1 | 0 | 42.7415 | 42.7415 | 3.7795 | 3.7795 | 0 | 1.3964 | 4.1628 | 0 | 0 | 0 | 34.6 | 7 | 9 | 23 | 15.8 | 14.2 | 0
0.6 | 2 | 1 | 1 | 1 | 1 | 0 | 41.2444 | 41.2444 | 3.8878 | 3.8878 | 0 | 1.4463 | 2.9936 | 0 | 0 | 0 | 33 | 7 | 9 | 21 | 15 | 13 | 0
0.62 | 2 | 1 | 1 | 1 | 1 | 0 | 38.8404 | 38.8404 | 3.8847 | 3.8847 | 0 | 1.4249 | 2.5949 | 0 | 0 | 0 | 30.6 | 7 | 8.6 | 19 | 14.6 | 12.2 | 0
0.64 | 2 | 1 | 1 | 1 | 1 | 0 | 36.4363 | 36.4363 | 3.8816 | 3.8816 | 0 | 1.4035 | 2.1962 | 0 | 0 | 0 | 28.2 | 7 | 8.2 | 17 | 14.2 | 11.4 | 0
0.66 | 2 | 1 | 1 | 1 | 1 | 0 | 34.0323 | 34.0323 | 3.8785 | 3.8785 | 0 | 1.382 | 1.7974 | 0 | 0 | 0 | 25.8 | 7 | 7.8 | 15 | 13.8 | 10.6 | 0
0.68 | 2 | 1 | 1 | 1 | 1 | 0 | 31.6283 | 31.6283 | 3.8754 | 3.8754 | 0 | 1.3606 | 1.3987 | 0 | 0 | 0 | 23.4 | 7 | 7.4 | 13 | 13.4 | 9.8 | 0
0.7 | 2 | 1 | 1 | 1 | 1 | 0 | 29.2242 | 29.2242 | 3.8723 | 3.8723 | 0 | 1.3392 | 1 | 0 | 0 | 0 | 21 | 7 | 7 | 11 | 13 | 9 | 0
0.72 | 2 | 1.0186 | 1.0186 | 1.0186 | 1.0186 | 0 | 29.3912 | 29.3912 | 3.6366 | 3.6366 | 0 | 1.4307 | 1.1469 | 0 | 0 | 0 | 19.4 | 7 | 7 | 10.2 | 12.6 | 8.6 | 0
0.74 | 2 | 1.0373 | 1.0373 | 1.0373 | 1.0373 | 0 | 29.5581 | 29.5581 | 3.4009 | 3.4009 | 0 | 1.5222 | 1.2937 | 0 | 0 | 0 | 17.8 | 7 | 7 | 9.4 | 12.2 | 8.2 | 0
0.76 | 2 | 1.0559 | 1.0559 | 1.0559 | 1.0559 | 0 | 29.7251 | 29.7251 | 3.1652 | 3.1652 | 0 | 1.6136 | 1.4406 | 0 | 0 | 0 | 16.2 | 7 | 7 | 8.6 | 11.8 | 7.8 | 0
0.78 | 2 | 1.0746 | 1.0746 | 1.0746 | 1.0746 | 0 | 29.8921 | 29.8921 | 2.9294 | 2.9294 | 0 | 1.7051 | 1.5875 | 0 | 0 | 0 | 14.6 | 7 | 7 | 7.8 | 11.4 | 7.4 | 0
0.8 | 2 | 1.0932 | 1.0932 | 1.0932 | 1.0932 | 0 | 30.059 | 30.059 | 2.6937 | 2.6937 | 0 | 1.7965 | 1.7344 | 0 | 0 | 0 | 13 | 7 | 7 | 7 | 11 | 7 | 0
0.82 | 2 | 1.0746 | 1.0746 | 1.0746 | 1.0746 | 0 | 24.4814 | 24.4814 | 2.4125 | 2.4125 | 0 | 0 | 0 | 0 | 0 | 0 | 13.4 | 6.6 | 6.6 | 7.4 | 10.6 | 6.6 | 0
0.84 | 2 | 1.0559 | 1.0559 | 1.0559 | 1.0559 | 0 | 18.9038 | 18.9038 | 2.1312 | 2.1312 | 0 | 0 | 0 | 0 | 0 | 0 | 13.8 | 6.2 | 6.2 | 7.8 | 10.2 | 6.2 | 0
0.86 | 2 | 1.0373 | 1.0373 | 1.0373 | 1.0373 | 0 | 13.3262 | 13.3262 | 1.8499 | 1.8499 | 0 | 0 | 0 | 0 | 0 | 0 | 14.2 | 5.8 | 5.8 | 8.2 | 9.8 | 5.8 | 0
0.88 | 2 | 1.0186 | 1.0186 | 1.0186 | 1.0186 | 0 | 7.7486 | 7.7486 | 1.5687 | 1.5687 | 0 | 0 | 0 | 0 | 0 | 0 | 14.6 | 5.4 | 5.4 | 8.6 | 9.4 | 5.4 | 0
0.9 | 2 | 1 | 1 | 1 | 1 | 0 | 2.171 | 2.171 | 1.2874 | 1.2874 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 5 | 9 | 9 | 5 | 0
0.92 | 2 | 1 | 1 | 1 | 1 | 0 | 2.0855 | 2.0855 | 1.2792 | 1.2792 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 4 | 4 | 6 | 7 | 4 | 0
0.94 | 2 | 1 | 1 | 1 | 1 | 0 | 2 | 2 | 1.271 | 1.271 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3 | 3 | 3 | 5 | 3 | 0
0.96 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.98 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## BladeMaterials
MATERIAL DATA |  |  | CORE DATA
Shell skin |  |  | Skin Core
E11 | 21790 | [MPa] | E | 50 | [MPa]
E22 | 14670 | [MPa] | G | 150 | [MPa]
v12 | 0.478 | [-] | Density | 110 | [kg/m^3]
G12 | 9413 | [MPa] | Sigma11Max | 0.694 | [MPa]
Sigma11Max | 480.4 | [MPa] | Sigma11Min | 0.4 | [MPa]
Sigma11Min | 393 | [MPa] | TauMax | 0.307 | [MPa]
Sigma22Max | 90.4 | [MPa]
Sigma22Min | 152.7 | [MPa] | Web Core
TauMax | 114 | [MPa] | E | 50 | [MPa]
Epsilon11Max | 2.2 | % | G | 150 | [MPa]
Epsilon11Min | 1.8 | % | Density | 110 | [kg/m^3]
Epsilon22Max | 0.62 | % | Sigma11Max | 0.694 | [MPa]
Epsilon22Min | 1.04 | % | Sigma11Min | 0.4 | [MPa]
GammaMax | 1.21 | % | TauMax | 0.307 | [MPa]
FiberOrientation | 0 | [deg]
LayerThickness | 0.1 | [mm] | Adhesive
FiberFraction | 0.47931 | [-] | E | 4.56 | [MPa]
densityEpoxy | 1150 | [kg/m^3] | G | 1.45 | [MPa]
densityFiber | 2600 | [kg/m^3] | Density | 1100 | [kg/m^3]
density | 1845 | [kg/m^3] | Sigma11Max | 61.513 | [MPa]
FatigueSNSlope | 10 |  | Sigma11Min | 65.361 | [MPa]
PriceEpoxy | 4.67 | [$/kg] | TauMax | 36.611 | [MPa]
PriceFiber | 2.97 | [$/kg]
Paint
Spar caps |  |  | E | 1e-06 | [MPa]
E11 | 42000 | [MPa] | G | 3.84e-07 | [MPa]
E22 | 12300 | [MPa] | Density | 1400 | [kg/m^3]
v12 | 0.31 | [-] | Sigma11Max | 10 | [MPa]
G12 | 3470 | [MPa] | Sigma11Min | 10 | [MPa]
Sigma11Max | 868 | [MPa] | TauMax | 10 | [MPa]
Sigma11Min | 869 | [MPa] | LayerThickness | 0.5 | [mm]
Sigma22Max | 53.7 | [MPa]
Sigma22Min | 160 | [MPa] | NonStructural Masses
TauMax | 45.8 | [MPa] | NSMassInfusionPly | 0 | [kg/m^2] | (for 1 spar)
Epsilon11Max | 2.19 | % | NSMassResinSkin | 2.5 | [kg/m^2]
Epsilon11Min | 2 | % | NSMassResinWeb | 0.8 | [kg/m^2] | (for 1 web)
Epsilon22Max | 0.49 | % | NSMassGlueWeb | 2.3 | [kg/m] | (for 1 web)
Epsilon22Min | 2.19 | % | NSMassGlueLETE | 2.88 | [kg/m] | (for LE & TE)
GammaMax | 5 | % | NSMassLight | 0.5 | [kg/m]
FiberOrientation | 0 | [deg] | NSMassBonding | 3.9 | [kg/m] | (for 1 web)
LayerThickness | 0.1 | [mm]
FiberFraction | 0.528 | [-]
densityEpoxy | 1180 | [kg/m^3]
densityFiber | 2620 | [kg/m^3]
density | 1940 | [kg/m^3]
FatigueSNSlope | 10
PriceEpoxy | 4.67 | [$/kg]
PriceFiber | 2.11 | [$/kg]
Webs skin
E11 | 13920 | [MPa]
E22 | 13920 | [MPa]
v12 | 0.533 | [-]
G12 | 11500 | [MPa]
Sigma11Max | 223.2 | [MPa]
Sigma11Min | 209.2 | [MPa]
Sigma22Max | 223.2 | [MPa]
Sigma22Min | 209.2 | [MPa]
TauMax | 140.3 | [MPa]
Epsilon11Max | 1.6 | %
Epsilon11Min | 1.5 | %
Epsilon22Max | 1.6 | %
Epsilon22Min | 1.5 | %
GammaMax | 1.22 | %
FiberOrientation | 0 | [deg]
LayerThickness | 0.1 | [mm]
FiberFraction | 0.47931 | [-]
densityEpoxy | 1150 | [kg/m^3]
densityFiber | 2600 | [kg/m^3]
density | 1845 | [kg/m^3]
FatigueSNSlope | 10
PriceEpoxy | 4.67 | [$/kg]
PriceFiber | 2.97 | [$/kg]
TE-LE reinforcemnents
E11 | 41630 | [MPa]
E22 | 14930 | [MPa]
v12 | 0.241 | [-]
G12 | 5047 | [MPa]
Sigma11Max | 876.1 | [MPa]
Sigma11Min | 625.8 | [MPa]
Sigma22Max | 74.03 | [MPa]
Sigma22Min | 189.4 | [MPa]
TauMax | 56.58 | [MPa]
Epsilon11Max | 2.1 | %
Epsilon11Min | 1.5 | %
Epsilon22Max | 0.5 | %
Epsilon22Min | 1.27 | %
GammaMax | 1.12 | %
FiberOrientation | 0 | [deg]
LayerThickness | 0.1 | [mm]
FiberFraction | 0.52793 | [-]
densityEpoxy | 1150 | [kg/m^3]
densityFiber | 2600 | [kg/m^3]
density | 1915.5 | [kg/m^3]
FatigueSNSlope | 10
PriceEpoxy | 4.67 | [$/kg]
PriceFiber | 2.11 | [$/kg]
Root reinforcement
E11 | 41630 | [MPa]
E22 | 14930 | [MPa]
v12 | 0.241 | [-]
G12 | 5047 | [MPa]
Sigma11Max | 876.1 | [MPa]
Sigma11Min | 625.8 | [MPa]
Sigma22Max | 74.03 | [MPa]
Sigma22Min | 189.4 | [MPa]
TauMax | 56.58 | [MPa]
Epsilon11Max | 2.1 | %
Epsilon11Min | 1.5 | %
Epsilon22Max | 0.5 | %
Epsilon22Min | 1.27 | %
GammaMax | 1.12 | %
FiberOrientation | 0 | [deg]
LayerThickness | 0.1 | [mm]
FiberFraction | 0.52793 | [-]
densityEpoxy | 1150 | [kg/m^3]
densityFiber | 2600 | [kg/m^3]
density | 1915.5 | [kg/m^3]
FatigueSNSlope | 10
PriceEpoxy | 4.67 | [$/kg]
PriceFiber | 2.11 | [$/kg]
Third Shear Web
E11 | 21790 | [MPa]
E22 | 14670 | [MPa]
v12 | 0.478 | [-]
G12 | 9413 | [MPa]
Sigma11Max | 480.4 | [MPa]
Sigma11Min | 393 | [MPa]
Sigma22Max | 90.4 | [MPa]
Sigma22Min | 152.7 | [MPa]
TauMax | 114 | [MPa]
Epsilon11Max | 2.2 | %
Epsilon11Min | 1.8 | %
Epsilon22Max | 0.62 | %
Epsilon22Min | 1.04 | %
GammaMax | 1.21 | %
FiberOrientation | 0 | [deg]
LayerThickness | 0.1 | [mm]
FiberFraction | 0.47931 | [-]
densityEpoxy | 1150 | [kg/m^3]
densityFiber | 2600 | [kg/m^3]
density | 1845 | [kg/m^3]
FatigueSNSlope | 10
PriceEpoxy | 4.67 | [$/kg]
PriceFiber | 2.97 | [$/kg]
Extra 1
E11 | 28544 | [MPa]
E22 | 10280 | [MPa]
v12 | 0.438 | [-]
G12 | 6470 | [MPa]
Sigma11Max | 513.8 | [MPa]
Sigma11Min | 356.8 | [MPa]
Sigma22Max | 185 | [MPa]
Sigma22Min | 123.4 | [MPa]
TauMax | 148.8 | [MPa]
Epsilon11Max | 1.8 | %
Epsilon11Min | 1.25 | %
Epsilon22Max | 1.8 | %
Epsilon22Min | 1.2 | %
GammaMax | 2.3 | %
FiberOrientation | 0 | [deg]
LayerThickness | 0.92 | [mm]
FiberFraction | 0.479 | [-]
densityEpoxy | 1150 | [kg/m^3]
densityFiber | 2600 | [kg/m^3]
density | 1888 | [kg/m^3]
FatigueSNSlope | 10
PriceEpoxy | 4.67 | [$/kg]
PriceFiber | 2.97 | [$/kg]
Extra 2
E11 | 28544 | [MPa]
E22 | 10280 | [MPa]
v12 | 0.438 | [-]
G12 | 6470 | [MPa]
Sigma11Max | 513.8 | [MPa]
Sigma11Min | 356.8 | [MPa]
Sigma22Max | 185 | [MPa]
Sigma22Min | 123.4 | [MPa]
TauMax | 148.8 | [MPa]
Epsilon11Max | 1.8 | %
Epsilon11Min | 1.25 | %
Epsilon22Max | 1.8 | %
Epsilon22Min | 1.2 | %
GammaMax | 2.3 | %
FiberOrientation | 0 | [deg]
LayerThickness | 0.92 | [mm]
FiberFraction | 0.479 | [-]
densityEpoxy | 1150 | [kg/m^3]
densityFiber | 2600 | [kg/m^3]
density | 1888 | [kg/m^3]
FatigueSNSlope | 10
PriceEpoxy | 4.67 | [$/kg]
PriceFiber | 2.97 | [$/kg]
Extra 3
E11 | 28544 | [MPa]
E22 | 10280 | [MPa]
v12 | 0.438 | [-]
G12 | 6470 | [MPa]
Sigma11Max | 513.8 | [MPa]
Sigma11Min | 356.8 | [MPa]
Sigma22Max | 185 | [MPa]
Sigma22Min | 123.4 | [MPa]
TauMax | 148.8 | [MPa]
Epsilon11Max | 1.8 | %
Epsilon11Min | 1.25 | %
Epsilon22Max | 1.8 | %
Epsilon22Min | 1.2 | %
GammaMax | 2.3 | %
FiberOrientation | 0 | [deg]
LayerThickness | 0.92 | [mm]
FiberFraction | 0.479 | [-]
densityEpoxy | 1150 | [kg/m^3]
densityFiber | 2600 | [kg/m^3]
density | 1888 | [kg/m^3]
FatigueSNSlope | 10
PriceEpoxy | 4.67 | [$/kg]
PriceFiber | 2.97 | [$/kg]
Trailing edge root
E11 | 0.001 | [MPa]
E22 | 0.001 | [MPa]
v12 | 0.3 | [-]
G12 | 1000 | [MPa]
density | 2000 | [kg/m^3]

## BladeStructuralProperties
Eta | T11 | T22 | EA | E11 | E22 | GJ | Centroid Xs | Centroid Ys | DeltaTheta | ShearCenter Xs | ShearCenter Ys | Mass | J3 | J1 | J2 | CenterOfMass Xm | CenterOfMass Ym | Non Structural Mass | Point Mass
[-] | [N] | [N] | [N] | [Nm^2] | [Nm^2] | [Nm^2] | [m] | [m] | [deg] | [m] | [m] | [kg/m] | [kgm^2/m] | [kgm^2/m] | [kgm^2/m] | [m] | [m] | [kg/m] | [kg]
0 | 2435763320 | 2435648824 | 11275588420 | 9049466584 | 9049929800 | 7816921648 | -5.137e-05 | 0.0002146 | 79.68 | -5.469e-05 | 0.0002149 | 954.8272 | 1532.6735 | 766.3171 | 766.3564 | -5.137e-05 | 0.0002146 | 9.0879 | 0
0.01 | 2252832604 | 2252724849 | 10428764710 | 8402876600 | 8403313562 | 7258400833 | -0.009102 | 0.0002149 | 79.82 | -0.009105 | 0.0002152 | 883.1174 | 1423.1636 | 711.5633 | 711.6003 | -0.009102 | 0.0002149 | 9.0879 | 0
0.02 | 2069160582 | 2069064935 | 9578521331 | 7748226192 | 7748616483 | 6692909043 | -0.01815 | 0.0002157 | 79.55 | -0.01815 | 0.000216 | 811.118 | 1312.2869 | 656.1269 | 656.16 | -0.01815 | 0.0002157 | 9.0964 | 0
0.03 | 1903876682 | 1877653160 | 8753026516 | 7104770205 | 7203985454 | 6179431510 | -0.03788 | -0.0004808 | -2.909 | -0.03787 | -0.0004739 | 741.2143 | 1211.6786 | 601.6385 | 610.0401 | -0.03788 | -0.0004808 | 9.1049 | 0
0.04 | 1793471424 | 1701158363 | 8090544170 | 6578833558 | 6935697908 | 5831700144 | -0.078 | -0.002207 | -2.617 | -0.0779 | -0.002104 | 685.1147 | 1144.4229 | 557.1017 | 587.3213 | -0.078 | -0.002207 | 17.8525 | 0
0.05 | 1702192767 | 1516931976 | 7458686177 | 6070427610 | 6811537687 | 5540644477 | -0.1373 | -0.004939 | -2.42 | -0.1369 | -0.004411 | 631.6084 | 1090.8567 | 514.0494 | 576.8073 | -0.1373 | -0.004939 | 26.6001 | 0
0.06 | 1620814558 | 1329548483 | 6849253937 | 5580895852 | 6802878925 | 5283648445 | -0.2164 | -0.009134 | -2.095 | -0.2149 | -0.007503 | 580.0011 | 1048.6694 | 472.5954 | 576.074 | -0.2164 | -0.009134 | 35.3478 | 0
0.07 | 1515572327 | 1123164742 | 6148374836 | 4853250433 | 6548026889 | 4789296458 | -0.2904 | -0.01461 | -1.663 | -0.287 | -0.01081 | 520.65 | 965.4706 | 410.9777 | 554.4929 | -0.2904 | -0.01461 | 44.0954 | 0
0.08 | 1392244053 | 916543042.4 | 5411159118 | 4054558608 | 6158677125 | 4180851731 | -0.366 | -0.02086 | -1.202 | -0.3592 | -0.0134 | 458.2219 | 864.8662 | 343.3437 | 521.5224 | -0.366 | -0.02086 | 52.843 | 0
0.1 | 1103665935 | 521073914.1 | 5260541582 | 3328216013 | 6862119795 | 2738424738 | -0.6003 | -0.05682 | 2.55 | -0.1692 | 0.05064 | 412.7902 | 802.7684 | 252.6103 | 550.1581 | -0.6246 | -0.0605 | 70.3382 | 0
0.12 | 1031480314 | 396211544.2 | 5105369544 | 2864562005 | 7026388012 | 2203930403 | -0.6667 | -0.06068 | 3.205 | -0.3147 | 0.04938 | 379.453 | 745.059 | 204.3886 | 540.6705 | -0.7031 | -0.06719 | 73.6513 | 0
0.14 | 913897069.5 | 318672723.4 | 4842776876 | 2590630074 | 6657673400 | 1825944913 | -0.6476 | -0.04714 | 2.818 | -0.4671 | 0.02182 | 339.398 | 664.2743 | 173.8072 | 490.467 | -0.698 | -0.05583 | 76.9644 | 0
0.16 | 749206083 | 246777513.9 | 4522958744 | 2359419431 | 5728069018 | 1400860490 | -0.5656 | -0.02996 | 2.138 | -0.4538 | -0.003371 | 297.4481 | 552.7043 | 147.0564 | 405.6479 | -0.6298 | -0.03961 | 80.2776 | 0
0.18 | 553539310.3 | 178698118.2 | 4316650890 | 2185749484 | 5146548458 | 954593370.1 | -0.5149 | -0.02337 | 2.656 | -0.3339 | -0.005822 | 263.9626 | 470.8341 | 125.8566 | 344.9775 | -0.5875 | -0.03298 | 83.5907 | 0
0.2 | 336537588.3 | 123065130.2 | 4116633878 | 2061747611 | 4480300917 | 550792220.1 | -0.449 | -0.0163 | 3.228 | -0.2126 | -0.01031 | 230.35 | 384.5288 | 109.1146 | 275.4142 | -0.5129 | -0.02406 | 86.9038 | 0
0.22 | 296228334.4 | 115788881.4 | 4292915785 | 2097485137 | 4294469766 | 448423837.7 | -0.4116 | -0.01282 | 3.091 | -0.1446 | -0.008949 | 234.4661 | 369.0171 | 108.2651 | 260.7519 | -0.4747 | -0.01875 | 89.0354 | 0
0.24 | 253750880 | 109373007.9 | 4442076160 | 2117747135 | 3845083377 | 349531591.9 | -0.361 | -0.01035 | 2.391 | -0.08482 | -0.002437 | 236.9847 | 338.2281 | 106.8532 | 231.3749 | -0.4195 | -0.01341 | 91.1671 | 0
0.26 | 209778276 | 104031903.3 | 4607255648 | 2137055811 | 3426330653 | 264425415.1 | -0.3186 | -0.0116 | 2.224 | -0.04838 | 0.0002653 | 240.2613 | 308.4983 | 105.7587 | 202.7396 | -0.369 | -0.01254 | 93.2988 | 0
0.28 | 164438199.5 | 99247684.24 | 4784986030 | 2145677130 | 3037771928 | 192255457.1 | -0.2831 | -0.01469 | 3.036 | -0.03093 | 0.002696 | 244.1004 | 279.2848 | 104.4675 | 174.8173 | -0.3227 | -0.01431 | 95.4304 | 0
0.3 | 117404654.7 | 94520724.36 | 4974910104 | 2136966004 | 2694571797 | 131851818.4 | -0.2526 | -0.01885 | 5.824 | -0.02784 | 0.005258 | 248.4817 | 251.1249 | 102.6732 | 148.4517 | -0.2796 | -0.01787 | 97.5621 | 0
0.32 | 114337071 | 93110743.85 | 4772838350 | 1937356887 | 2484605939 | 117968852.2 | -0.2536 | -0.02272 | 6.002 | -0.02556 | 0.002974 | 238.7488 | 230.3052 | 93.1225 | 137.1827 | -0.2801 | -0.02118 | 93.995 | 0
0.34 | 110911378.5 | 91149330.13 | 4571094355 | 1731229001 | 2293155294 | 107714796.2 | -0.2569 | -0.02798 | 6.797 | -0.03373 | 0.0008605 | 228.9139 | 209.7801 | 83.2926 | 126.4875 | -0.2825 | -0.02629 | 90.4279 | 0
0.36 | 107424017.4 | 88910407.41 | 4368099893 | 1535003899 | 2085174707 | 97718041.11 | -0.2588 | -0.03196 | 7.445 | -0.04203 | -0.0009673 | 218.9705 | 188.7899 | 73.9142 | 114.8756 | -0.283 | -0.03018 | 86.8608 | 0
0.38 | 103855530.4 | 86448018.39 | 4164377728 | 1349512230 | 1871244951 | 88091657.75 | -0.2595 | -0.03468 | 7.931 | -0.05067 | -0.002273 | 208.9439 | 167.9572 | 65.026 | 102.9312 | -0.2821 | -0.03285 | 83.2938 | 0
0.4 | 99899258.62 | 83806305.76 | 3963257628 | 1175200718 | 1674913801 | 79013438.91 | -0.2583 | -0.03622 | 7.861 | -0.05708 | -0.003348 | 198.9896 | 148.4752 | 56.6366 | 91.8385 | -0.2791 | -0.03442 | 79.7267 | 0
0.42 | 95432345.17 | 81761728.64 | 3917934060 | 1052733528 | 1543695961 | 70775734.28 | -0.2589 | -0.03673 | 7.608 | -0.06777 | -0.002849 | 196.2283 | 134.3627 | 50.6528 | 83.7099 | -0.2766 | -0.03506 | 74.5022 | 0
0.44 | 91083347.22 | 79411370.35 | 3872047434 | 934804313.5 | 1407374547 | 63067371.47 | -0.2585 | -0.03636 | 7.297 | -0.07891 | -0.001795 | 193.4061 | 120.4157 | 44.8998 | 75.516 | -0.2731 | -0.03486 | 69.2778 | 0
0.46 | 86913880.36 | 76806203.62 | 3825922637 | 822915768.1 | 1272007400 | 55969645.17 | -0.2575 | -0.03533 | 6.882 | -0.09061 | -0.0005205 | 190.5487 | 107.0296 | 39.452 | 67.5775 | -0.2693 | -0.03403 | 64.0534 | 0
0.48 | 83009030.04 | 74012616.54 | 3780190712 | 718399477.1 | 1142710789 | 49521130.93 | -0.256 | -0.03385 | 6.324 | -0.1029 | 0.0006696 | 187.6956 | 94.5241 | 34.3745 | 60.1495 | -0.2653 | -0.03274 | 58.829 | 0
0.5 | 78975695.51 | 71160142.44 | 3738795316 | 622817865.4 | 1036667058 | 43814039.87 | -0.2538 | -0.03217 | 5.358 | -0.1129 | 0.001697 | 185.039 | 83.7698 | 29.7372 | 54.0325 | -0.2608 | -0.03124 | 53.6045 | 0
0.52 | 83329044.05 | 68302301.22 | 3599190653 | 525172142.3 | 837419638.4 | 39046227.7 | -0.24 | -0.03064 | 6.056 | -0.1239 | 0.001106 | 178.0831 | 69.1274 | 25.086 | 44.0414 | -0.2466 | -0.02979 | 50.92 | 0
0.54 | 90120387.65 | 65450394.12 | 3459920782 | 440940398 | 675786226.6 | 34924608.26 | -0.2271 | -0.02358 | 7.34 | -0.1321 | 0.004309 | 171.1613 | 56.9803 | 21.0837 | 35.8966 | -0.2333 | -0.02289 | 48.2354 | 0
0.56 | 100116914.8 | 62934266.71 | 3322694417 | 368624704.9 | 545603825.7 | 31250948.29 | -0.2157 | -0.01553 | 8.804 | -0.1393 | 0.008057 | 164.3388 | 46.9488 | 17.6489 | 29.2999 | -0.2217 | -0.01499 | 45.5508 | 0
0.58 | 114592179 | 61048860.45 | 3188266515 | 307316831.1 | 441371998.4 | 27959048.01 | -0.206 | -0.00792 | 10.24 | -0.1461 | 0.01123 | 157.6582 | 38.7244 | 14.7354 | 23.989 | -0.2118 | -0.007532 | 42.8662 | 0
0.6 | 133856087.8 | 59892302.16 | 3057970315 | 256380607.9 | 361079057.2 | 25057967.8 | -0.1959 | -0.001078 | 11.29 | -0.1495 | 0.01357 | 151.1896 | 32.1768 | 12.3086 | 19.8682 | -0.2015 | -0.0008102 | 40.1816 | 0
0.62 | 144287642.7 | 55536070.56 | 2876273543 | 210921789.1 | 311492395.2 | 22182224.81 | -0.1954 | 0.005279 | 9.495 | -0.1548 | 0.01771 | 142.2304 | 27.3405 | 10.1143 | 17.2262 | -0.2005 | 0.005437 | 38.4941 | 0
0.64 | 154040702.7 | 51489197.08 | 2696091388 | 173895446.7 | 269698417.6 | 19686152.71 | -0.1955 | 0.0107 | 7.996 | -0.1599 | 0.021 | 133.3935 | 23.3252 | 8.333 | 14.9922 | -0.2002 | 0.01076 | 36.8066 | 0
0.66 | 161429099.6 | 47759142.51 | 2518025144 | 144015565.5 | 235222511.7 | 17552654.67 | -0.1961 | 0.01514 | 6.684 | -0.1645 | 0.02354 | 124.7145 | 20.0473 | 6.8994 | 13.1479 | -0.2004 | 0.01512 | 35.1191 | 0
0.68 | 164841826.3 | 44450280.26 | 2341348107 | 119979295.8 | 205958577.1 | 15724664.47 | -0.1974 | 0.01868 | 5.618 | -0.1686 | 0.02528 | 116.155 | 17.3329 | 5.7494 | 11.5835 | -0.2013 | 0.0186 | 33.4316 | 0
0.7 | 163240959.8 | 41274120.96 | 2165943420 | 99749002.39 | 181432049.8 | 14066051.12 | -0.1966 | 0.02221 | 4.538 | -0.1695 | 0.02725 | 107.6921 | 15.0587 | 4.7829 | 10.2758 | -0.2003 | 0.02205 | 31.744 | 0
0.72 | 165845052.7 | 36707129.28 | 2173050979 | 89064968.68 | 177990734.2 | 12606136.49 | -0.2009 | 0.02589 | 3.424 | -0.1748 | 0.03088 | 107.5128 | 14.2234 | 4.2608 | 9.9626 | -0.2041 | 0.02567 | 31.0058 | 0
0.74 | 167758903.8 | 32758498.93 | 2180423001 | 80203474.78 | 175336657.9 | 11350986.91 | -0.2058 | 0.02903 | 2.66 | -0.1801 | 0.03418 | 107.4136 | 13.5451 | 3.8299 | 9.7152 | -0.2086 | 0.02878 | 30.2675 | 0
0.76 | 169482460.4 | 29303004.31 | 2188331533 | 72849228.52 | 173273370.5 | 10273740.57 | -0.2109 | 0.03185 | 2.125 | -0.1854 | 0.03724 | 107.3998 | 12.9924 | 3.4737 | 9.5188 | -0.2135 | 0.03158 | 29.5292 | 0
0.78 | 171014037.7 | 26288471.32 | 2196710903 | 66972835.25 | 171801207.6 | 9367134.599 | -0.2161 | 0.03428 | 1.759 | -0.1904 | 0.03999 | 107.4657 | 12.5622 | 3.1896 | 9.3726 | -0.2186 | 0.03398 | 28.791 | 0
0.8 | 171964585.3 | 23678675.58 | 2206264254 | 62598173.29 | 171662458.6 | 8635000.826 | -0.219 | 0.03615 | 1.51 | -0.1919 | 0.04233 | 107.6396 | 12.2882 | 2.9781 | 9.3102 | -0.2218 | 0.03585 | 28.0527 | 0
0.82 | 146736848.3 | 20847123.89 | 1788807518 | 49787543.21 | 121847844.6 | 7420390.93 | -0.2202 | 0.0382 | 1.817 | -0.1929 | 0.04014 | 87.9282 | 9.2375 | 2.379 | 6.8585 | -0.2233 | 0.03785 | 27.5497 | 0
0.84 | 119964279.8 | 17988634.91 | 1401239787 | 37801830.59 | 99082690.11 | 6377828.151 | -0.2269 | 0.03927 | 1.553 | -0.1879 | 0.04135 | 69.666 | 7.5418 | 1.8179 | 5.724 | -0.2309 | 0.03886 | 27.0466 | 0
0.86 | 92697911.39 | 15066167.03 | 1013300282 | 26068236.35 | 75793515.67 | 5230549.464 | -0.2346 | 0.03949 | 1.133 | -0.1805 | 0.04189 | 51.3696 | 5.8144 | 1.2681 | 4.5463 | -0.2398 | 0.03896 | 26.5436 | 0
0.88 | 64630941.24 | 11928452.47 | 624175380.7 | 14697202.01 | 51558263.6 | 3894841.114 | -0.2443 | 0.03859 | 0.4965 | -0.1673 | 0.04141 | 32.9731 | 4.0235 | 0.73378 | 3.2898 | -0.2512 | 0.03787 | 26.0405 | 0
0.9 | 35520630.55 | 8219214.591 | 232937343.5 | 4440652.901 | 26252990.58 | 2266008.718 | -0.2631 | 0.03535 | -0.5022 | -0.1361 | 0.0408 | 14.4251 | 2.1948 | 0.2496 | 1.9452 | -0.2716 | 0.03425 | 25.5375 | 0
0.92 | 32315846.27 | 7002126.716 | 219408067.3 | 3343212.259 | 21497165.72 | 1758722.358 | -0.2589 | 0.03274 | -0.7221 | -0.1305 | 0.03633 | 13.4262 | 1.7385 | 0.18754 | 1.551 | -0.2636 | 0.03161 | 23.3978 | 0
0.94 | 28190866.7 | 5349697.957 | 203407470.9 | 2142594.585 | 16564434.83 | 1184374.59 | -0.2523 | 0.02889 | -0.9708 | -0.1086 | 0.0304 | 12.1857 | 1.2567 | 0.1198 | 1.1369 | -0.2515 | 0.02773 | 21.2582 | 0
0.96 | 15857108.11 | 1018969.147 | 45938997.69 | 238131.0316 | 4083186.651 | 369694.445 | -0.2239 | 0.019 | -1.131 | 0.05005 | 0.02468 | 3.8902 | 0.36593 | 0.020165 | 0.34577 | -0.2239 | 0.019 | 21.2582 | 0
0.98 | 10206350.63 | 653903.2133 | 29566592.53 | 63279.5882 | 1088638.441 | 98246.1527 | -0.1459 | 0.01225 | -1.136 | 0.03071 | 0.01587 | 2.5037 | 0.097545 | 0.0053586 | 0.092187 | -0.1459 | 0.01225 | 21.2582 | 0
1 | 3094881.275 | 195730.7117 | 8962292.668 | 1740.7053 | 30330.9508 | 2698.9601 | -0.04702 | 0.003781 | -1.196 | 0.006725 | 0.004755 | 0.75894 | 0.0027159 | 0.0001474 | 0.0025685 | -0.04702 | 0.003781 | 21.2582 | 0

## Wind
Grid
Height of the wind grid centre | 110 | [m]
Height of the wind grid | 140 | [m]
Width of the wind grid | 140 | [m]
Vertical grid-point matrix dimension | 12 | [-]
Horizontal grid-point matrix dimension | 12 | [-]
Wind grid time step | 0.05 | [s]
Wind shear power law exponent | 0.2
Weibull
Average wind speed for AEP calculation | 7.5 | [m/s]
Weibull shape factor | 2
Wind turbine lifetime | 20 | [years]
Wind turbine cut-in wind speed | 4 | [m/s]
Wind turbine cut-out wind speed | 25 | [m/s]
Air density | 1.225
Uniform wind speed tilt | 8 | [deg]
Equivalent number of cycles for DELs | 10000000 | [-]

## TowerStructure
Tower Material Data
Youngs Modulus | 210 | [GPa] |  | Cycles number in S-N diagram at slope change | 5000000 | [-]
Poisson Coefficient | 0.3 | [-] |  | Normal stress value in S-N diagram at slope change (cycles number = Nd) | 65.7 | [MPa]
Density (higher than actual density of steel to account for some secondary structures) | 8500 | [kg/m3] | (higher than actual density of steel to account for some secondary structures) | Slope of first part of S-N diagram | 3 | [-]
Yield Strength | 355 | [MPa] |  | Slope of second part of S-N diagram | 5 | [-]
Ultimate Strength | 400 | [MPa] |  | Cycles number in S-N diagram at cut off | 100000000 | [-]
|  |  |  | Cycles number to compute equivalent loads (standard defined) | 2000000 | [-]
|  |  |  | Shear Stress value in S-N diagram at cut off | 46.1594 | [MPa]
Tower N.D. Height | Wall Thickness | Tower Diameter | Section Area | Mass per Unit Length | Axial Stiffness | Bending Stiffness | Torsional Stiffness | Shear Stiffness | Polar Moment of Inertia
[-] | [mm] | [m] | [m2] | [kg/m] | [N] | [Nm2] | [Nm2] | [N] | [m4]
0 | 56.9709 | 5.9869 | 1.0613 | 9021.376 | 222881053700.6582 | 979771166264.2949 | 753670127895.6116 | 42861741096.2804 | 9.3312
0.10004 | 56.9709 | 5.9277 | 1.0507 | 8931.2712 | 220654934662.4305 | 950707551259.0909 | 731313500968.5315 | 42433641281.2366 | 9.0544
0.10004 | 50.4733 | 5.9277 | 0.93193 | 7921.4031 | 195705254033.5937 | 845060353350.3323 | 650046425654.1018 | 37635625775.6911 | 8.0482
0.20007 | 50.4733 | 5.9277 | 0.93193 | 7921.4031 | 195705254033.5937 | 845060353350.3323 | 650046425654.1018 | 37635625775.6911 | 8.0482
0.20007 | 46.6442 | 5.9277 | 0.86179 | 7325.2259 | 180976169981.9815 | 782469895489.1349 | 601899919607.0269 | 34803109611.9195 | 7.4521
0.30011 | 46.6442 | 5.9277 | 0.86179 | 7325.2259 | 180976169981.9815 | 782469895489.1349 | 601899919607.0269 | 34803109611.9195 | 7.4521
0.30011 | 39.3487 | 5.9277 | 0.7279 | 6187.1765 | 152859654480.7159 | 662533763343.2695 | 509641356417.8997 | 29396087400.1377 | 6.3098
0.40014 | 39.3487 | 5.9277 | 0.7279 | 6187.1765 | 152859654480.7159 | 662533763343.2695 | 509641356417.8997 | 29396087400.1377 | 6.3098
0.40014 | 33.5444 | 5.9277 | 0.62114 | 5279.7054 | 130439779674.0195 | 566468345717.734 | 435744881321.3339 | 25084573014.2345 | 5.3949
0.50018 | 33.5444 | 5.9277 | 0.62114 | 5279.7054 | 130439779674.0195 | 566468345717.734 | 435744881321.3339 | 25084573014.2345 | 5.3949
0.50018 | 28.01 | 5.9277 | 0.51915 | 4412.7596 | 109021119621.0175 | 474337155192.3311 | 364874734763.3316 | 20965599927.1187 | 4.5175
0.60022 | 28.01 | 5.8503 | 0.51234 | 4354.8904 | 107591410671.6452 | 455919637119.7615 | 350707413169.0474 | 20690655898.3933 | 4.3421
0.60022 | 23.5685 | 5.8503 | 0.43143 | 3667.1378 | 90599875494.4612 | 384501195944.3033 | 295770150726.3871 | 17423052979.7041 | 3.6619
0.70025 | 23.5685 | 5.1162 | 0.37707 | 3205.1354 | 79185698366.2426 | 256718603865.2406 | 197475849127.1081 | 15228018916.5851 | 2.4449
0.70025 | 23.7353 | 5.1162 | 0.37973 | 3227.7139 | 79743520917.4882 | 258510198198.6026 | 198853998614.3097 | 15335292484.1323 | 2.462
0.80029 | 23.7353 | 4.3618 | 0.32348 | 2749.5516 | 67930097493.5074 | 159801826692.0954 | 122924482070.8426 | 13063480287.213 | 1.5219
0.80029 | 22.4091 | 4.3618 | 0.3055 | 2596.7154 | 64154145302.2344 | 151010902006.8213 | 116162232312.9395 | 12337335635.0451 | 1.4382
0.90032 | 22.4091 | 3.6074 | 0.25238 | 2145.2701 | 53000790752.7986 | 85150375212.64 | 65500288625.1077 | 10192459760.1536 | 0.81096
0.90032 | 26.7413 | 3.6074 | 0.30081 | 2556.9049 | 63170591297.5433 | 101245599850.8008 | 77881230654.4622 | 12148190634.1429 | 0.96424
1 | 26.7413 | 3 | 0.24978 | 2123.1652 | 52454669147.5834 | 57968851355.6209 | 44591424119.7084 | 10087436374.5353 | 0.55208

## Nacelle, Hub, DT and Actuators
Hub
Hub Inertia About Shaft Axis | 60131 | [kg m2]
Hub Inertia Off Shaft Axis | 300650 | [kg m2]
Hub calculation method | 1 | [-]
Distance c.g. from rotor center | 0 | [m]
Flexible hub | 1
Axial stiffness blade root connection | 1000000000000 | [Nm2]
Bending stiffness blade root connection | 1000000000000 | [Nm2]
Torsional stiffness blade root connection | 1000000000000 | [Nm2]
Shear stiffness blade root connection | 1000000000000 | [Nm2]
Nacelle
Nacelle Inertia About Yaw Axis | 1210200 | [kg m2]
Nacelle Inertia Rolling | 177200 | [kg m2]
Nacelle Inertia Nodding | 370330 | [kg m2]
Nacelle Length | 12 | [m]
Nacelle Width | 6 | [m]
Nacelle Height | 5 | [m]
Location CoG Nacelle Downwind of Yaw Axis | 0.0995 | [m]
Location CoG Nacelle Above the Yaw Bearing | 0.5843 | [m]
Vertical Distance Along Yaw Axis from Yaw Bearing to Shaft | 2 | [m]
Nacelle lifting line | 1
Nacelle Drag Coefficient | 0.5 | [-]
Axial stiffness shaft | 1000000000000 | [Nm2]
Bending stiffness shaft | 1000000000000 | [Nm2]
Torsional stiffness shaft | 1000000000000 | [Nm2]
Shear stiffness shaft | 1000000000000 | [Nm2]
Drive Train and Generator
Flag Model Electrical Generator Efficiency | 1 | [-] | Flag to indicate which model is used to model losses. 1 corresponds to data specified in terms of power in kW and efficiency non-dimensional
Generator Inertia About Medium-Speed Shaft | 0 | [kg m2] |  |  | Power [kW] | Efficiency [-]
Generator Inertia Rolling | 0 | [kg m2] |  |  | 0 | 0.98
Generator Inertia Nodding | 0 | [kg m2] |  |  | 10000 | 0.98
Location CoG Generator Downwind of Yaw Axis | 0 | [m]
Location CoG Generator Above the Yaw Bearing | 0 | [m]
Generator Torque Dynamics - Beta | 1 | [-]
Generator Torque Dynamics - w0 | 0.01 | [rad/s]
Maximum Generator Torque (LSS) | 4250000 | [N-m]
Flexible shaft | 1
Axial stiffness shaft | 1000000000000 | [Nm2]
Bending stiffness shaft | 1000000000000 | [Nm2]
Torsional stiffness shaft | 1000000000000 | [Nm2]
Shear stiffness shaft | 1000000000000 | [Nm2]
Mechanical efficiency | 0.955 | [-]
Suspension Drive | 4 | [-]
Main Bearing 1 Type | SRF1 | [-]
Main Bearing 2 Type | SRF2 | [-]
Drivetrain Design | geared | [-]
Fully-Deployed Medium-Speed Shaft Brake Torque | 52253.5 | [N-m]
Medium-Speed Shaft Brake Time Constant | 0.74 | [s]
Structural damping (free-free system) | 5 | [% critical]
Rated Generator Speed | 1140.0391 | [rpm]
Gearbox Ratio | 97 | [-]
Gearbox configuration | eep | [-]
Number of planets | 3 | [-]
Transformer position | 1 | [-]
Actuators
Pitch ωn | 10
Pitch ξ | 0.8
Yaw time constant | 0
Yaw gain | 1
Standard max pitch rate [deg/s] | 7
Normal shut down max pitch rate [deg/s] | 7
Emergency shut down max pitch rate [deg/s] | 7
Yaw rate [deg/s] | 0.25
| Hub | Low Speed Shaft | Bearings | Gearbox | High Speed Shaft | Generator | Transformer | Bedplate | Yaw | Nacelle
Mass Ref | 39467.5684 |  |  |  |  | 16953.9 |  |  |  | 220493 | [kg]
Mass DriveSE | 39467.5684 | 23979.4169 | 2968 | 41053.257 | 1176.1211 | 16953.9 | 10399.2 | 58412.2185 | 8824.9828 | 220493 | [kg]
Mass Center X | -5.5917 | -2.54 | -0.76196 | 0.1 | 1.63 | 2.6988 | 0 | -0.48943 | 0 | -0.5435 | [m]
Mass Center Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [m]
Mass Center Z | 1.0705 | 0.943 | 0.78717 | 0.78 | 1.17 | 1.17 | 0 | -0.7218 | -0.6996 | 0.70836 | [m]
Note on A1: Pietro Bortolotti: All values are inputs to Cp-Max
Note on A4: Simon Franz: 1: actual blade root diameter 2: scaled blade root diameter
Note on A5: Pietro Bortolotti: Positive value means cog is downwind of the rotor center
Note on A6: Pietro Bortolotti: If the flag is set to 1 then the blade root connections to the rotor center are modelled with the stiffness defined in the cells below
Note on A22: Helena Canet: If the flag is set to 1, a beam perpendicular to tower_top_frame is modeled with the drag coefficient and structural properties. If set to 0, the nacelle is just modeled as a mass point.
Note on A39: Helena Canet: If 1, both static and rotational beams are modeled as flexible beams with the properties defined underneath. If 0, the shaft is defined as a single rigid body.
Note on A44: Helena Canet: Mechanical efficiency is used to model the mechanical losses in the generator. The losses are computed in reference to the rated speed and torque indicated in the Controller tab.
Note on A46: Simon Franz: CARB, SRB, TRB1, TRB2, CRB, RB
Note on A47: Simon Franz: CARB, SRB, TRB1, TRB2, CRB, RB
Note on A48: Simon Franz: geared, single_stage, multi_drive or pm_direct_drive
Note on A54: Simon Franz: eep: Planetary-Planetary-Parallel epp: Planetary-Parallel-Parallel
Note on A55: Simon Franz: 3, 4 or 5
Note on A56: Simon Franz: 1: tower top 2: tower bottom
Note on B68: Pietro Bortolotti: All values are inputs to Cp-Max
Note on K68: Simon Franz: In DriveSE the Nacelle values are the sum of all listed Nacelle components

## RotorEnvelope
Envelope @ Station 1 - Eta = 0 - SAFETY FACTORS ALREADY APPLIED.
| Fx | Fy | Fz | Mx | My | Mz | Fxy | Mxy | Blade Nb | DLC | Time | Safety Factor
| [N] | [N] | [N] | [Nm] | [Nm] | [Nm] | [N] | [Nm] | [-] | [-] | [sec] | [-]
Loads @ max Fx | 398138.5575 | -247078.7159 | 886473.4109 | 11209846.608 | 10283582.907 | -23309.1585 | 468574.6502 | 15212256.1897 | Blade 2 | DLC13_Seed2_13ms | 266.38 | 1.35
Loads @ min Fx | -286331.7479 | -30489.6392 | 630591.2261 | -1698875.442 | -8570732.566 | 159412.7128 | 287950.4957 | 8737484.4484 | Blade 1 | DLC23_vr+2a | 41.78 | 1.1
Loads @ max Fy | -86801.33 | 289589.4991 | -88990.5541 | -7241406.634 | -2534821.498 | 169077.2919 | 302318.6215 | 7672241.5281 | Blade 1 | DLC62_ID_T_YMdeg60_Seed1 | 157.58 | 1.1
Loads @ min Fy | 23473.1853 | -594062.1135 | 883989.6876 | 18962746.38 | 3156345.4815 | -101711.3146 | 594525.6808 | 19223638.2371 | Blade 3 | DLC13_Seed2_9ms | 211.54 | 1.35
Loads @ max Fz | 200848.2507 | -227125.2366 | 1125477.7254 | 8342002.593 | 6335447.0085 | -59702.0431 | 303192.8312 | 10475060.6709 | Blade 2 | DLC13_Seed2_15ms | 331.58 | 1.35
Loads @ min Fz | -82323.6328 | 133262.9067 | -184262.903 | -3666057.879 | -2738881.189 | 49454.5079 | 156640.2976 | 4576182.9661 | Blade 1 | DLC61_ID_T_Seed1_YMdeg8a | 131.72 | 1.1
Loads @ max Mx | 23473.1853 | -594062.1135 | 883989.6876 | 18962746.38 | 3156345.4815 | -101711.3146 | 594525.6808 | 19223638.2371 | Blade 3 | DLC13_Seed2_9ms | 211.54 | 1.35
Loads @ min Mx | -91011.2588 | 288343.6138 | -62886.3745 | -7506492.686 | -2795444.993 | 152055.3914 | 302365.8196 | 8010115.1773 | Blade 1 | DLC62_ID_T_YMdeg60_Seed1 | 442.98 | 1.1
Loads @ max My | 383202.4505 | -112446.5882 | 738831.5964 | 4876769.754 | 10426245.6825 | -146479.4901 | 399359.9294 | 11510407.563 | Blade 3 | DLC13_Seed2_23ms | 305.98 | 1.35
Loads @ min My | -286331.7479 | -30489.6392 | 630591.2261 | -1698875.442 | -8570732.566 | 159412.7128 | 287950.4957 | 8737484.4484 | Blade 1 | DLC23_vr+2a | 41.78 | 1.1
Loads @ max Mz | -109187.263 | 175033.837 | -83391.4462 | -4129130.335 | -2428361.276 | 199986.2304 | 206297.6066 | 4790266.7786 | Blade 3 | DLC62_ID_T_YMdeg150_Seed1 | 156.18 | 1.1
Loads @ min Mz | -119013.3223 | -245141.4618 | 475056.7205 | 7037260.398 | -1480717.2465 | -328348.9332 | 272504.1416 | 7191352.9654 | Blade 1 | DLC13_Seed1_9ms | 98.78 | 1.35
Loads @ max Fxy | 23473.1853 | -594062.1135 | 883989.6876 | 18962746.38 | 3156345.4815 | -101711.3146 | 594525.6808 | 19223638.2371 | Blade 3 | DLC13_Seed2_9ms | 211.54 | 1.35
Loads @ max Mxy | 23473.1853 | -594062.1135 | 883989.6876 | 18962746.38 | 3156345.4815 | -101711.3146 | 594525.6808 | 19223638.2371 | Blade 3 | DLC13_Seed2_9ms | 211.54 | 1.35
Envelope @ Station 2 - Eta = 0.5 - SAFETY FACTORS ALREADY APPLIED.
| Fx | Fy | Fz | Mx | My | Mz | Fxy | Mxy | Blade Nb | DLC | Time | Safety Factor
| [N] | [N] | [N] | [Nm] | [Nm] | [Nm] | [N] | [Nm] | [-] | [-] | [sec] | [-]
Loads @ max Fx | 302545.5881 | -92937.4318 | 447479.4834 | 1168126.4178 | 4293696.762 | -56719.2999 | 316498.3398 | 4449758.5566 | Blade 1 | DLC13_Seed1_13ms | 546.8 | 1.35
Loads @ min Fx | -149782.2287 | -39229.4869 | 347275.4 | 418648.1774 | -2155934.88 | -10552.2646 | 154834.3265 | 2196206.1614 | Blade 3 | DLC13_Seed1_25ms | 49.18 | 1.35
Loads @ max Fy | 24055.2937 | 108064.9003 | 358513.1591 | -1338571.0755 | -343710.2903 | -53053.7103 | 110709.8904 | 1381994.6772 | Blade 3 | DLC13_Seed1_25ms | 519.18 | 1.35
Loads @ min Fy | 287208.5121 | -117788.7915 | 413272.0224 | 1493202.6 | 4239179.0235 | -49874.3167 | 310423.7891 | 4494473.5841 | Blade 3 | DLC13_Seed2_9ms | 211.44 | 1.35
Loads @ max Fz | 114842.8984 | -12679.4262 | 502426.7514 | 180029.6172 | 1847978.604 | -32904.8267 | 115540.7251 | 1856727.1162 | Blade 2 | DLC13_Seed2_13ms | 269.98 | 1.35
Loads @ min Fz | -49387.2159 | 3989.5364 | -46747.0395 | -65641.4851 | -790025.8927 | -11966.5675 | 49548.0928 | 792748.2045 | Blade 1 | DLC61_ID_T_Seed1_YMdeg8a | 291.68 | 1.1
Loads @ max Mx | 294603.8148 | -116624.974 | 339019.6883 | 1653885.0405 | 4651738.74 | -75305.4399 | 316848.2164 | 4937004.0543 | Blade 1 | DLC13_Seed1_9ms | 608.12 | 1.35
Loads @ min Mx | 24055.2937 | 108064.9003 | 358513.1591 | -1338571.0755 | -343710.2903 | -53053.7103 | 110709.8904 | 1381994.6772 | Blade 3 | DLC13_Seed1_25ms | 519.18 | 1.35
Loads @ max My | 290028.4906 | -100580.0958 | 335900.9939 | 1446307.2045 | 4654156.0095 | -56244.6802 | 306973.7465 | 4873702.1545 | Blade 1 | DLC13_Seed1_9ms | 607.92 | 1.35
Loads @ min My | -122108.0465 | -52926.3962 | 376885.8545 | 859078.3901 | -2430968.058 | 46721.6609 | 133084.8542 | 2578298.1556 | Blade 2 | DLC13_Seed1_25ms | 178.38 | 1.35
Loads @ max Mz | -80466.1465 | -59720.1499 | 207983.8343 | 845097.4675 | -1297669.989 | 69680.476 | 100206.2725 | 1548591.983 | Blade 3 | DLC23_vr+2a | 42.78 | 1.1
Loads @ min Mz | 151981.0412 | -26761.7327 | 343498.4928 | 306488.2617 | 1563059.2005 | -170297.4969 | 154319.238 | 1592824.2586 | Blade 2 | DLC13_Seed1_25ms | 395.98 | 1.35
Loads @ max Fxy | 294603.8148 | -116624.974 | 339019.6883 | 1653885.0405 | 4651738.74 | -75305.4399 | 316848.2164 | 4937004.0543 | Blade 1 | DLC13_Seed1_9ms | 608.12 | 1.35
Loads @ max Mxy | 294603.8148 | -116624.974 | 339019.6883 | 1653885.0405 | 4651738.74 | -75305.4399 | 316848.2164 | 4937004.0543 | Blade 1 | DLC13_Seed1_9ms | 608.12 | 1.35
Envelope @ Station 3 - Eta = 0.8 - SAFETY FACTORS ALREADY APPLIED.
| Fx | Fy | Fz | Mx | My | Mz | Fxy | Mxy | Blade Nb | DLC | Time | Safety Factor
| [N] | [N] | [N] | [Nm] | [Nm] | [Nm] | [N] | [Nm] | [-] | [-] | [sec] | [-]
Loads @ max Fx | 128160.4189 | -25509.6302 | 111435.3395 | 173777.7875 | 733314.4043 | -28071.7196 | 130674.5354 | 753623.7356 | Blade 1 | DLC13_Seed2_13ms | 262.38 | 1.35
Loads @ min Fx | -123251.1667 | 18449.9343 | 98134.8283 | -33287.8046 | 128432.061 | 50149.8513 | 124624.4365 | 132675.8163 | Blade 1 | DLC13_Seed2_21ms | 303.58 | 1.35
Loads @ max Fy | 19982.165 | 31576.0962 | 89627.7007 | -136061.4794 | 67639.236 | -35138.2859 | 37367.5898 | 151946.6762 | Blade 1 | DLC13_Seed2_23ms | 242.78 | 1.35
Loads @ min Fy | 116441.2265 | -31019.443 | 102005.5607 | 183020.9229 | 679388.5206 | -19264.2342 | 120502.1373 | 703608.8545 | Blade 2 | DLC13_Seed2_13ms | 259.58 | 1.35
Loads @ max Fz | 64999.1855 | 6121.921 | 119911.786 | -4527.5022 | 380870.6603 | -10672.1475 | 65286.8442 | 380897.5691 | Blade 2 | DLC13_Seed2_15ms | 331.98 | 1.35
Loads @ min Fz | 4737.0531 | 1838.4443 | -10938.2304 | -11463.088 | 28713.5939 | -5885.8599 | 5081.2941 | 30917.1936 | Blade 3 | DLC62_ID_T_YMdeg-120_Seed1 | 524.78 | 1.1
Loads @ max Mx | 116441.2265 | -31019.443 | 102005.5607 | 183020.9229 | 679388.5206 | -19264.2342 | 120502.1373 | 703608.8545 | Blade 2 | DLC13_Seed2_13ms | 259.58 | 1.35
Loads @ min Mx | 19982.165 | 31576.0962 | 89627.7007 | -136061.4794 | 67639.236 | -35138.2859 | 37367.5898 | 151946.6762 | Blade 1 | DLC13_Seed2_23ms | 242.78 | 1.35
Loads @ max My | 128160.4189 | -25509.6302 | 111435.3395 | 173777.7875 | 733314.4043 | -28071.7196 | 130674.5354 | 753623.7356 | Blade 1 | DLC13_Seed2_13ms | 262.38 | 1.35
Loads @ min My | -68441.7554 | -20228.3577 | 85281.8697 | 126823.8452 | -387791.9037 | 34102.368 | 71368.4828 | 408003.4905 | Blade 2 | DLC13_Seed1_25ms | 178.38 | 1.35
Loads @ max Mz | -123251.1667 | 18449.9343 | 98134.8283 | -33287.8046 | 128432.061 | 50149.8513 | 124624.4365 | 132675.8163 | Blade 1 | DLC13_Seed2_21ms | 303.58 | 1.35
Loads @ min Mz | 20571.7456 | -2001.727 | 84352.816 | 34408.7181 | 44370.8816 | -65742.9008 | 20668.9049 | 56149.2209 | Blade 2 | DLC13_Seed1_25ms | 395.98 | 1.35
Loads @ max Fxy | 128160.4189 | -25509.6302 | 111435.3395 | 173777.7875 | 733314.4043 | -28071.7196 | 130674.5354 | 753623.7356 | Blade 1 | DLC13_Seed2_13ms | 262.38 | 1.35
Loads @ max Mxy | 128160.4189 | -25509.6302 | 111435.3395 | 173777.7875 | 733314.4043 | -28071.7196 | 130674.5354 | 753623.7356 | Blade 1 | DLC13_Seed2_13ms | 262.38 | 1.35

## WTEnvelopes
Envelope @ Hub Centre - SAFETY FACTORS ALREADY APPLIED
| Fx | Fy | Fz | Mx | My | Mz | Fxy | Mxy | DLC | Time | Safety Factor
| [N] | [N] | [N] | [Nm] | [Nm] | [Nm] | [N] | [Nm] | [-] | [sec] | [-]
Loads @ max Fx | 1252153.7766 | -66064.7085 | -1030068.657 | 5893758.423 | 3237846.8175 | 4431173.634 | 1032185.0531 | 5488073.5954 | DLC13_Seed2_9ms | 211.84 | 1.35
Loads @ min Fx | -590284.0559 | -16516.5567 | -839344.473 | 190013.1354 | 2985533.507 | -3456225.454 | 839506.963 | 4567154.9908 | DLC23_vr+2b | 42.18 | 1.1
Loads @ max Fy | -35011.3774 | 537905.7497 | -726710.1336 | 3939.2283 | 2890771.752 | 1216281.209 | 904129.5338 | 3136224.0516 | DLC62_ID_T_YMdeg-120_Seed1 | 99.98 | 1.1
Loads @ min Fy | 61784.9639 | -543353.921 | -652789.1337 | -4932.7223 | 422497.4006 | -1325653.626 | 849333.3483 | 1391352.4319 | DLC62_ID_T_YMdeg60_Seed1 | 99.38 | 1.1
Loads @ max Fz | 115293.3056 | 5474.6229 | -360161.3741 | -2044.9499 | 698661.1115 | 1576345.782 | 360202.9801 | 1724237.0409 | DLC61_ID_T_Seed1_YMdeg0a | 147 | 1.1
Loads @ min Fz | 520183.7078 | 93415.601 | -1368069.8445 | 3035580.003 | 855015.9633 | 2021695.821 | 1371255.4736 | 2195064.0743 | DLC13_Seed2_9ms | 317.84 | 1.35
Loads @ max Mx | 931311.9949 | 2195.7229 | -1028264.0837 | 6033303.0225 | -367945.011 | 2640729.546 | 1028266.428 | 2666240.0616 | DLC13_Seed1_11ms | 387.58 | 1.35
Loads @ min Mx | 66721.8166 | 223650.6976 | -596527.4975 | -22001.1208 | 2447185.389 | 1935387.971 | 637075.1053 | 3120006.8792 | DLC62_ID_T_YMdeg-30_Seed1 | 140.98 | 1.1
Loads @ max My | 476887.7524 | -68140.698 | -1051261.4943 | 4197546.6975 | 12299018.6295 | 4206947.976 | 1053467.5525 | 12998625.7167 | DLC13_Seed1_19ms | 522.78 | 1.35
Loads @ min My | 411211.1246 | 152633.3449 | -929611.6403 | 4218382.449 | -12802658.7825 | -1216308.5199 | 942058.7772 | 12860306.3073 | DLC13_Seed2_17ms | 214.78 | 1.35
Loads @ max Mz | 748980.4631 | 46.0701 | -1111544.6279 | 4743352.5075 | 4324524.9165 | 10870723.422 | 1111544.6288 | 11699322.3509 | DLC13_Seed1_13ms | 294.2 | 1.35
Loads @ min Mz | 187292.7171 | -55675.9371 | -907331.9787 | 4240383.0345 | -2850270.498 | -11660588.2665 | 909038.5743 | 12003889.3961 | DLC13_Seed1_21ms | 246.38 | 1.35
Loads @ max Fxy | 520183.7078 | 93415.601 | -1368069.8445 | 3035580.003 | 855015.9633 | 2021695.821 | 1371255.4736 | 2195064.0743 | DLC13_Seed2_9ms | 317.84 | 1.35
Loads @ max Mxy | 476887.7524 | -68140.698 | -1051261.4943 | 4197546.6975 | 12299018.6295 | 4206947.976 | 1053467.5525 | 12998625.7167 | DLC13_Seed1_19ms | 522.78 | 1.35
Envelope @ Tower Top - SAFETY FACTORS ALREADY APPLIED
| Fx | Fy | Fz | Mx | My | Mz | Fxy | Mxy | DLC | Time | Safety Factor
| [N] | [N] | [N] | [Nm] | [Nm] | [Nm] | [N] | [Nm] | [-] | [sec] | [-]
Loads @ max Fx | 1171652.0049 | 48026.5278 | -3640006.3905 | 5984680.5045 | -3241001.6325 | 2305253.6415 | 1172635.906 | 6805915.9797 | DLC13_Seed2_9ms | 212.24 | 1.35
Loads @ min Fx | -1017036.6162 | -33762.5576 | -2861512.038 | -155157.2627 | -5830756.305 | -3359890.699 | 1017596.8696 | 5832820.3182 | DLC23_vr+2b | 42.38 | 1.1
Loads @ max Fy | 189910.0236 | 485312.3066 | -2820899.73 | -1491421.8 | -1830921.917 | -1530034.132 | 521146.6703 | 2361485.5603 | DLC63_ID_T_YMdeg20a_Seed1 | 267 | 1.1
Loads @ min Fy | -42588.9555 | -743209.3229 | -2746142.993 | 2302200.824 | -3236757.843 | 2588060.365 | 744428.5841 | 3971993.1984 | DLC63_ID_T_YMdeg-20a_Seed1 | 433.36 | 1.1
Loads @ max Fz | -15066.4987 | 200065.5536 | -2403816.371 | -213858.1852 | 592985.2346 | 574394.1093 | 200632.064 | 630370.3767 | DLC61_ID_T_Seed1_YMdeg8a | 88.88 | 1.1
Loads @ min Fz | 204057.5598 | -45716.172 | -3787761.7035 | 2531755.3455 | -1575438.0525 | 371549.6042 | 209115.8915 | 2981910.4927 | DLC13_Seed2_9ms | 315.34 | 1.35
Loads @ max Mx | 859904.2728 | -1860.3844 | -3674666.4255 | 6403837.6845 | -930189.3282 | 6286679.433 | 859906.2852 | 6471042.3639 | DLC13_Seed1_13ms | 210.4 | 1.35
Loads @ min Mx | 361609.7573 | -62653.6351 | -2888408.655 | -2903794.487 | 2436304.75 | -1316047.326 | 366997.404 | 3790462.143 | DLC62_ID_T_YMdeg120_Seed1 | 294.18 | 1.1
Loads @ max My | 347034.695 | -58714.3366 | -3506076.765 | 4217514.156 | 12774968.109 | -1057058.3889 | 351966.5507 | 13453149.6625 | DLC13_Seed2_17ms | 214.78 | 1.35
Loads @ min My | 469236.4844 | 117596.8126 | -3612746.988 | 4335325.47 | -12535446.4515 | 3794549.2875 | 483747.7531 | 13263953.5837 | DLC13_Seed1_19ms | 522.78 | 1.35
Loads @ max Mz | 419211.6431 | -24468.6656 | -3650438.4345 | 5271978.933 | -3439939.0635 | 10811885.67 | 419925.1329 | 6294993.4575 | DLC13_Seed1_19ms | 327.58 | 1.35
Loads @ min Mz | 37562.5212 | 91881.6022 | -3440971.206 | 2995079.5035 | 2404246.2255 | -12179670.8805 | 99263.1444 | 3840690.1912 | DLC13_Seed1_21ms | 246.38 | 1.35
Loads @ max Fxy | 1171652.0049 | 48026.5278 | -3640006.3905 | 5984680.5045 | -3241001.6325 | 2305253.6415 | 1172635.906 | 6805915.9797 | DLC13_Seed2_9ms | 212.24 | 1.35
Loads @ max Mxy | 347034.695 | -58714.3366 | -3506076.765 | 4217514.156 | 12774968.109 | -1057058.3889 | 351966.5507 | 13453149.6625 | DLC13_Seed2_17ms | 214.78 | 1.35
Envelope @ Tower Root - SAFETY FACTORS ALREADY APPLIED
| Fx | Fy | Fz | Mx | My | Mz | Fxy | Mxy | DLC | Time | Safety Factor
| [N] | [N] | [N] | [Nm] | [Nm] | [Nm] | [N] | [Nm] | [-] | [sec] | [-]
Loads @ max Fx | 1354387.8915 | -929.6925 | -10950366.3615 | 6458854.977 | 128061688.23 | -1951346.3895 | 1354388.2106 | 128224462.5644 | DLC13_Seed2_9ms | 212.54 | 1.35
Loads @ min Fx | -1229141.232 | -126755.3441 | -8828002.37 | 6331985.704 | -135435491.4 | -2286287.201 | 1235659.7774 | 135583429.5691 | DLC23_vr+2b | 42.58 | 1.1
Loads @ max Fy | 397022.8328 | 661076.8065 | -8779676.114 | -66272877.33 | 28650483.51 | -1256554.849 | 771135.3149 | 72200723.5071 | DLC63_ID_T_YMdeg20a_Seed1 | 570 | 1.1
Loads @ min Fy | 71470.214 | -991673.3134 | -8661723.081 | 101041425.21 | -7833113.189 | 2406769.739 | 994245.4184 | 101344596.6527 | DLC63_ID_T_YMdeg-20a_Seed1 | 433.48 | 1.1
Loads @ max Fz | 483141.3873 | 92567.938 | -8280061.119 | -15691689.97 | 23095758.51 | 579742.4809 | 491929.2869 | 27922091.5274 | DLC61_ID_T_Seed1_YMdeg8a | 88.88 | 1.1
Loads @ min Fz | 556911.8779 | -21708.4041 | -11085118.6905 | 5813237.8215 | 54758054.16 | -2343278.646 | 557334.8137 | 55065762.7692 | DLC13_Seed2_9ms | 173.54 | 1.35
Loads @ max Mx | 103520.2362 | -987350.9008 | -8638099.052 | 101412485.68 | -4644393.468 | 2466149.191 | 992762.9327 | 101518779.7527 | DLC63_ID_T_YMdeg-20a_Seed1 | 433.44 | 1.1
Loads @ min Mx | 397022.8328 | 661076.8065 | -8779676.114 | -66272877.33 | 28650483.51 | -1256554.849 | 771135.3149 | 72200723.5071 | DLC63_ID_T_YMdeg20a_Seed1 | 570 | 1.1
Loads @ max My | 1329276.3174 | 95963.7819 | -10984154.5935 | -1051483.6881 | 133186047.525 | 3251287.782 | 1332735.7485 | 133190198.1126 | DLC13_Seed2_9ms | 212.14 | 1.35
Loads @ min My | -1229141.232 | -126755.3441 | -8828002.37 | 6331985.704 | -135435491.4 | -2286287.201 | 1235659.7774 | 135583429.5691 | DLC23_vr+2b | 42.58 | 1.1
Loads @ max Mz | 456396.8774 | -61511.5689 | -10945743.516 | 11982119.913 | 44188613.91 | 10915810.1145 | 460523.3792 | 45784329.1629 | DLC13_Seed1_19ms | 327.58 | 1.35
Loads @ min Mz | 156137.2754 | -573.0404 | -10743035.724 | -278892.8159 | 11050143.498 | -12250999.2645 | 156138.3269 | 11053662.4034 | DLC13_Seed1_21ms | 246.38 | 1.35
Loads @ max Fxy | 1354387.8915 | -929.6925 | -10950366.3615 | 6458854.977 | 128061688.23 | -1951346.3895 | 1354388.2106 | 128224462.5644 | DLC13_Seed2_9ms | 212.54 | 1.35
Loads @ max Mxy | -1229141.232 | -126755.3441 | -8828002.37 | 6331985.704 | -135435491.4 | -2286287.201 | 1235659.7774 | 135583429.5691 | DLC23_vr+2b | 42.58 | 1.1
z axis parallel with tower axis
z axis parallel with tower axis
x axis tilted with the shaft

## Fatigue
SensorName | Blade_1_FixedLoads_eta0 | SensorName | Blade_1_FixedLoads_eta0 | SensorName | Blade_1_FixedLoads_eta0 | SensorName | Blade_2_FixedLoads_eta0 | SensorName | Blade_2_FixedLoads_eta0 | SensorName | Blade_2_FixedLoads_eta0 | SensorName | Blade_3_FixedLoads_eta0 | SensorName | Blade_3_FixedLoads_eta0 | SensorName | Blade_3_FixedLoads_eta0 | SensorName | Blade_1_FixedLoads_eta0 | SensorName | Blade_1_FixedLoads_eta0 | SensorName | Blade_1_FixedLoads_eta0 | SensorName | Blade_2_FixedLoads_eta0 | SensorName | Blade_2_FixedLoads_eta0 | SensorName | Blade_2_FixedLoads_eta0 | SensorName | Blade_3_FixedLoads_eta0 | SensorName | Blade_3_FixedLoads_eta0 | SensorName | Blade_3_FixedLoads_eta0 | SensorName | HubFixedForces | SensorName | HubFixedForces | SensorName | HubFixedForces | SensorName | HubFixedForces | SensorName | HubFixedForces | SensorName | HubFixedForces | SensorName | TowerTipLocalForces | SensorName | TowerTipLocalForces | SensorName | TowerTipLocalForces | SensorName | TowerTipLocalForces | SensorName | TowerTipLocalForces | SensorName | TowerTipLocalForces | SensorName | TowerTipLocalForces | SensorName | TowerTipLocalForces
Sensor Component | Mx | Sensor Component | My | Sensor Component | Mz | Sensor Component | Mx | Sensor Component | My | Sensor Component | Mz | Sensor Component | Mx | Sensor Component | My | Sensor Component | Mz | Sensor Component | Mx | Sensor Component | My | Sensor Component | Mz | Sensor Component | Mx | Sensor Component | My | Sensor Component | Mz | Sensor Component | Mx | Sensor Component | My | Sensor Component | Mz | Sensor Component | Fx | Sensor Component | My | Sensor Component | Mz | Sensor Component | Fx | Sensor Component | My | Sensor Component | Mz | Sensor Component | Fx | Sensor Component | Fy | Sensor Component | Mx | Sensor Component | My | Sensor Component | Fx | Sensor Component | Fy | Sensor Component | Mx | Sensor Component | My
Sensor Component Number | 4 | Sensor Component Number | 5 | Sensor Component Number | 6 | Sensor Component Number | 4 | Sensor Component Number | 5 | Sensor Component Number | 6 | Sensor Component Number | 4 | Sensor Component Number | 5 | Sensor Component Number | 6 | Sensor Component Number | 4 | Sensor Component Number | 5 | Sensor Component Number | 6 | Sensor Component Number | 4 | Sensor Component Number | 5 | Sensor Component Number | 6 | Sensor Component Number | 4 | Sensor Component Number | 5 | Sensor Component Number | 6 | Sensor Component Number | 1 | Sensor Component Number | 5 | Sensor Component Number | 6 | Sensor Component Number | 1 | Sensor Component Number | 5 | Sensor Component Number | 6 | Sensor Component Number | 1 | Sensor Component Number | 2 | Sensor Component Number | 4 | Sensor Component Number | 5 | Sensor Component Number | 1 | Sensor Component Number | 2 | Sensor Component Number | 4 | Sensor Component Number | 5
Type | Forces | Type | Forces | Type | Forces | Type | Forces | Type | Forces | Type | Forces | Type | Forces | Type | Forces | Type | Forces | Type | Forces | Type | Forces | Type | Forces | Type | Forces | Type | Forces | Type | Forces | Type | Forces | Type | Forces | Type | Forces | Type | Forces | Type | Forces | Type | Forces | Type | Forces | Type | Forces | Type | Forces | Type | Forces | Type | Forces | Type | Forces | Type | Forces | Type | Forces | Type | Forces | Type | Forces | Type | Forces
Frame | FrameBlade1RotatingPitchable | Frame | FrameBlade1RotatingPitchable | Frame | FrameBlade1RotatingPitchable | Frame | FrameBlade2RotatingPitchable | Frame | FrameBlade2RotatingPitchable | Frame | FrameBlade2RotatingPitchable | Frame | FrameBlade3RotatingPitchable | Frame | FrameBlade3RotatingPitchable | Frame | FrameBlade3RotatingPitchable | Frame | FrameBlade1RotatingPitchable | Frame | FrameBlade1RotatingPitchable | Frame | FrameBlade1RotatingPitchable | Frame | FrameBlade2RotatingPitchable | Frame | FrameBlade2RotatingPitchable | Frame | FrameBlade2RotatingPitchable | Frame | FrameBlade3RotatingPitchable | Frame | FrameBlade3RotatingPitchable | Frame | FrameBlade3RotatingPitchable | Frame | FrameHubFixed | Frame | FrameHubFixed | Frame | FrameHubFixed | Frame | FrameHubFixed | Frame | FrameHubFixed | Frame | FrameHubFixed | Frame | FrameTowerLocal | Frame | FrameTowerLocal | Frame | FrameTowerLocal | Frame | FrameTowerLocal | Frame | FrameTowerLocal | Frame | FrameTowerLocal | Frame | FrameTowerLocal | Frame | FrameTowerLocal
Units | [kNm] | Units | [kNm] | Units | [kNm] | Units | [kNm] | Units | [kNm] | Units | [kNm] | Units | [kNm] | Units | [kNm] | Units | [kNm] | Units | [kNm] | Units | [kNm] | Units | [kNm] | Units | [kNm] | Units | [kNm] | Units | [kNm] | Units | [kNm] | Units | [kNm] | Units | [kNm] | Units | [kN] | Units | [kNm] | Units | [kNm] | Units | [kN] | Units | [kNm] | Units | [kNm] | Units | [kN] | Units | [kN] | Units | [kNm] | Units | [kNm] | Units | [kN] | Units | [kN] | Units | [kNm] | Units | [kNm]
Wöhler exp [-] | 10 | Wöhler exp [-] | 10 | Wöhler exp [-] | 10 | Wöhler exp [-] | 10 | Wöhler exp [-] | 10 | Wöhler exp [-] | 10 | Wöhler exp [-] | 10 | Wöhler exp [-] | 10 | Wöhler exp [-] | 10 | Wöhler exp [-] | 4 | Wöhler exp [-] | 4 | Wöhler exp [-] | 4 | Wöhler exp [-] | 4 | Wöhler exp [-] | 4 | Wöhler exp [-] | 4 | Wöhler exp [-] | 4 | Wöhler exp [-] | 4 | Wöhler exp [-] | 4 | Wöhler exp [-] | 9 | Wöhler exp [-] | 9 | Wöhler exp [-] | 9 | Wöhler exp [-] | 4 | Wöhler exp [-] | 4 | Wöhler exp [-] | 4 | Wöhler exp [-] | 9 | Wöhler exp [-] | 9 | Wöhler exp [-] | 9 | Wöhler exp [-] | 9 | Wöhler exp [-] | 4 | Wöhler exp [-] | 4 | Wöhler exp [-] | 4 | Wöhler exp [-] | 4
Weibull DEL | 8357.3826 | Weibull DEL | 7904.8522 | Weibull DEL | 69.8313 | Weibull DEL | 8365.8239 | Weibull DEL | 7795.3016 | Weibull DEL | 69.729 | Weibull DEL | 8366.8166 | Weibull DEL | 7677.0414 | Weibull DEL | 69.428 | Weibull DEL | 11438.0494 | Weibull DEL | 7070.1815 | Weibull DEL | 76.9905 | Weibull DEL | 11449.9696 | Weibull DEL | 7027.4291 | Weibull DEL | 77.2561 | Weibull DEL | 11445.7951 | Weibull DEL | 7020.8946 | Weibull DEL | 76.9464 | Weibull DEL | 365.9173 | Weibull DEL | 7160.5774 | Weibull DEL | 6859.6847 | Weibull DEL | 296.0072 | Weibull DEL | 5871.7396 | Weibull DEL | 5775.5566 | Weibull DEL | 402.9783 | Weibull DEL | 228.8479 | Weibull DEL | 2313.5237 | Weibull DEL | 7168.2757 | Weibull DEL | 353.0287 | Weibull DEL | 258.516 | Weibull DEL | 1598.9283 | Weibull DEL | 5876.125
log10 N Cycles | Range Load | log10 N Cycles | Range Load | log10 N Cycles | Range Load | log10 N Cycles | Range Load | log10 N Cycles | Range Load | log10 N Cycles | Range Load | log10 N Cycles | Range Load | log10 N Cycles | Range Load | log10 N Cycles | Range Load | log10 N Cycles | Range Load | log10 N Cycles | Range Load | log10 N Cycles | Range Load | log10 N Cycles | Range Load | log10 N Cycles | Range Load | log10 N Cycles | Range Load | log10 N Cycles | Range Load | log10 N Cycles | Range Load | log10 N Cycles | Range Load | log10 N Cycles | Range Load | log10 N Cycles | Range Load | log10 N Cycles | Range Load | log10 N Cycles | Range Load | log10 N Cycles | Range Load | log10 N Cycles | Range Load | log10 N Cycles | Range Load | log10 N Cycles | Range Load | log10 N Cycles | Range Load | log10 N Cycles | Range Load | log10 N Cycles | Range Load | log10 N Cycles | Range Load | log10 N Cycles | Range Load | log10 N Cycles | Range Load
8.0599 | 0 | 8.7903 | 0 | 9.0643 | 0 | 8.0489 | 0 | 8.7955 | 0 | 9.0669 | 0 | 8.0625 | 0 | 8.7955 | 0 | 9.0631 | 0 | 8.0599 | 0 | 8.7903 | 0 | 9.0643 | 0 | 8.0489 | 0 | 8.7955 | 0 | 9.0669 | 0 | 8.0625 | 0 | 8.7955 | 0 | 9.0631 | 0 | 9.016 | 0 | 8.8463 | 0 | 8.8041 | 0 | 9.016 | 0 | 8.8463 | 0 | 8.8041 | 0 | 8.9688 | 0 | 8.8558 | 0 | 8.902 | 0 | 8.8719 | 0 | 8.9688 | 0 | 8.8558 | 0 | 8.902 | 0 | 8.8719 | 0
8.0599 | 0 | 8.7903 | 0 | 9.0643 | 0 | 8.0489 | 0 | 8.7955 | 0 | 9.0669 | 0 | 8.0625 | 0 | 8.7955 | 0 | 9.0631 | 0 | 8.0599 | 0 | 8.7903 | 0 | 9.0643 | 0 | 8.0489 | 0 | 8.7955 | 0 | 9.0669 | 0 | 8.0625 | 0 | 8.7955 | 0 | 9.0631 | 0 | 9.016 | 0 | 8.8463 | 0 | 8.8041 | 0 | 9.016 | 0 | 8.8463 | 0 | 8.8041 | 0 | 8.9688 | 0 | 8.8558 | 0 | 8.902 | 0 | 8.8719 | 0 | 8.9688 | 0 | 8.8558 | 0 | 8.902 | 0 | 8.8719 | 0
8.0599 | 48.0012 | 8.7903 | 122.3723 | 9.0643 | 1.3289 | 8.0489 | 49.1004 | 8.7955 | 121.2578 | 9.0669 | 1.2716 | 8.0625 | 48.6182 | 8.7955 | 119.7077 | 9.0631 | 1.3232 | 8.0599 | 48.0012 | 8.7903 | 122.3723 | 9.0643 | 1.3289 | 8.0489 | 49.1004 | 8.7955 | 121.2578 | 9.0669 | 1.2716 | 8.0625 | 48.6182 | 8.7955 | 119.7077 | 9.0631 | 1.3232 | 9.016 | 8.2477 | 8.8463 | 79.6439 | 8.8041 | 78.8938 | 9.016 | 8.2477 | 8.8463 | 79.6439 | 8.8041 | 78.8938 | 8.9688 | 7.8224 | 8.8558 | 2.1285 | 8.902 | 46.267 | 8.8719 | 82.0931 | 8.9688 | 7.8224 | 8.8558 | 2.1285 | 8.902 | 46.267 | 8.8719 | 82.0931
8.0599 | 48.0012 | 8.7903 | 122.3723 | 9.0643 | 1.3289 | 8.0489 | 49.1004 | 8.7955 | 121.2578 | 9.0669 | 1.2716 | 8.0625 | 48.6182 | 8.7955 | 119.7077 | 9.0631 | 1.3232 | 8.0599 | 48.0012 | 8.7903 | 122.3723 | 9.0643 | 1.3289 | 8.0489 | 49.1004 | 8.7955 | 121.2578 | 9.0669 | 1.2716 | 8.0625 | 48.6182 | 8.7955 | 119.7077 | 9.0631 | 1.3232 | 9.016 | 8.2477 | 8.8463 | 79.6439 | 8.8041 | 78.8938 | 9.016 | 8.2477 | 8.8463 | 79.6439 | 8.8041 | 78.8938 | 8.9688 | 7.8224 | 8.8558 | 2.1285 | 8.902 | 46.267 | 8.8719 | 82.0931 | 8.9688 | 7.8224 | 8.8558 | 2.1285 | 8.902 | 46.267 | 8.8719 | 82.0931
7.9564 | 96.0025 | 8.5413 | 244.7446 | 8.8136 | 2.6578 | 7.9516 | 98.2007 | 8.5423 | 242.5156 | 8.8181 | 2.5432 | 7.9535 | 97.2364 | 8.5394 | 239.4155 | 8.8104 | 2.6464 | 7.9564 | 96.0025 | 8.5413 | 244.7446 | 8.8136 | 2.6578 | 7.9516 | 98.2007 | 8.5423 | 242.5156 | 8.8181 | 2.5432 | 7.9535 | 97.2364 | 8.5394 | 239.4155 | 8.8104 | 2.6464 | 8.673 | 16.4953 | 8.6869 | 159.2878 | 8.6672 | 157.7875 | 8.673 | 16.4953 | 8.6869 | 159.2878 | 8.6672 | 157.7875 | 8.7579 | 15.6448 | 8.7621 | 4.257 | 8.4746 | 92.5341 | 8.6992 | 164.1862 | 8.7579 | 15.6448 | 8.7621 | 4.257 | 8.4746 | 92.5341 | 8.6992 | 164.1862
7.9564 | 96.0025 | 8.5413 | 244.7446 | 8.8136 | 2.6578 | 7.9516 | 98.2007 | 8.5423 | 242.5156 | 8.8181 | 2.5432 | 7.9535 | 97.2364 | 8.5394 | 239.4155 | 8.8104 | 2.6464 | 7.9564 | 96.0025 | 8.5413 | 244.7446 | 8.8136 | 2.6578 | 7.9516 | 98.2007 | 8.5423 | 242.5156 | 8.8181 | 2.5432 | 7.9535 | 97.2364 | 8.5394 | 239.4155 | 8.8104 | 2.6464 | 8.673 | 16.4953 | 8.6869 | 159.2878 | 8.6672 | 157.7875 | 8.673 | 16.4953 | 8.6869 | 159.2878 | 8.6672 | 157.7875 | 8.7579 | 15.6448 | 8.7621 | 4.257 | 8.4746 | 92.5341 | 8.6992 | 164.1862 | 8.7579 | 15.6448 | 8.7621 | 4.257 | 8.4746 | 92.5341 | 8.6992 | 164.1862
7.9363 | 144.0037 | 8.4073 | 367.1169 | 8.6629 | 3.9867 | 7.9368 | 147.3011 | 8.4129 | 363.7735 | 8.6709 | 3.8148 | 7.9359 | 145.8547 | 8.4162 | 359.1232 | 8.6688 | 3.9695 | 7.9363 | 144.0037 | 8.4073 | 367.1169 | 8.6629 | 3.9867 | 7.9368 | 147.3011 | 8.4129 | 363.7735 | 8.6709 | 3.8148 | 7.9359 | 145.8547 | 8.4162 | 359.1232 | 8.6688 | 3.9695 | 8.5225 | 24.743 | 8.6147 | 238.9316 | 8.602 | 236.6813 | 8.5225 | 24.743 | 8.6147 | 238.9316 | 8.602 | 236.6813 | 8.6402 | 23.4671 | 8.6945 | 6.3855 | 8.2852 | 138.8011 | 8.6244 | 246.2793 | 8.6402 | 23.4671 | 8.6945 | 6.3855 | 8.2852 | 138.8011 | 8.6244 | 246.2793
7.9363 | 144.0037 | 8.4073 | 367.1169 | 8.6629 | 3.9867 | 7.9368 | 147.3011 | 8.4129 | 363.7735 | 8.6709 | 3.8148 | 7.9359 | 145.8547 | 8.4162 | 359.1232 | 8.6688 | 3.9695 | 7.9363 | 144.0037 | 8.4073 | 367.1169 | 8.6629 | 3.9867 | 7.9368 | 147.3011 | 8.4129 | 363.7735 | 8.6709 | 3.8148 | 7.9359 | 145.8547 | 8.4162 | 359.1232 | 8.6688 | 3.9695 | 8.5225 | 24.743 | 8.6147 | 238.9316 | 8.602 | 236.6813 | 8.5225 | 24.743 | 8.6147 | 238.9316 | 8.602 | 236.6813 | 8.6402 | 23.4671 | 8.6945 | 6.3855 | 8.2852 | 138.8011 | 8.6244 | 246.2793 | 8.6402 | 23.4671 | 8.6945 | 6.3855 | 8.2852 | 138.8011 | 8.6244 | 246.2793
7.9301 | 192.0049 | 8.3053 | 489.4892 | 8.5628 | 5.3156 | 7.9305 | 196.4015 | 8.3055 | 485.0313 | 8.5737 | 5.0864 | 7.9301 | 194.4729 | 8.3113 | 478.831 | 8.5665 | 5.2927 | 7.9301 | 192.0049 | 8.3053 | 489.4892 | 8.5628 | 5.3156 | 7.9305 | 196.4015 | 8.3055 | 485.0313 | 8.5737 | 5.0864 | 7.9301 | 194.4729 | 8.3113 | 478.831 | 8.5665 | 5.2927 | 8.3934 | 32.9907 | 8.5617 | 318.5755 | 8.5502 | 315.575 | 8.3934 | 32.9907 | 8.5617 | 318.5755 | 8.5502 | 315.575 | 8.5369 | 31.2895 | 8.6349 | 8.514 | 8.1133 | 185.0682 | 8.5688 | 328.3724 | 8.5369 | 31.2895 | 8.6349 | 8.514 | 8.1133 | 185.0682 | 8.5688 | 328.3724
7.9301 | 192.0049 | 8.3053 | 489.4892 | 8.5628 | 5.3156 | 7.9305 | 196.4015 | 8.3055 | 485.0313 | 8.5737 | 5.0864 | 7.9301 | 194.4729 | 8.3113 | 478.831 | 8.5665 | 5.2927 | 7.9301 | 192.0049 | 8.3053 | 489.4892 | 8.5628 | 5.3156 | 7.9305 | 196.4015 | 8.3055 | 485.0313 | 8.5737 | 5.0864 | 7.9301 | 194.4729 | 8.3113 | 478.831 | 8.5665 | 5.2927 | 8.3934 | 32.9907 | 8.5617 | 318.5755 | 8.5502 | 315.575 | 8.3934 | 32.9907 | 8.5617 | 318.5755 | 8.5502 | 315.575 | 8.5369 | 31.2895 | 8.6349 | 8.514 | 8.1133 | 185.0682 | 8.5688 | 328.3724 | 8.5369 | 31.2895 | 8.6349 | 8.514 | 8.1133 | 185.0682 | 8.5688 | 328.3724
7.9266 | 240.0062 | 8.2183 | 611.8615 | 8.478 | 6.6445 | 7.927 | 245.5018 | 8.22 | 606.2891 | 8.4925 | 6.358 | 7.927 | 243.0911 | 8.2201 | 598.5387 | 8.4879 | 6.6159 | 7.9266 | 240.0062 | 8.2183 | 611.8615 | 8.478 | 6.6445 | 7.927 | 245.5018 | 8.22 | 606.2891 | 8.4925 | 6.358 | 7.927 | 243.0911 | 8.2201 | 598.5387 | 8.4879 | 6.6159 | 8.2651 | 41.2384 | 8.5166 | 398.2194 | 8.5098 | 394.4688 | 8.2651 | 41.2384 | 8.5166 | 398.2194 | 8.5098 | 394.4688 | 8.4378 | 39.1119 | 8.5833 | 10.6424 | 7.9396 | 231.3352 | 8.5229 | 410.4654 | 8.4378 | 39.1119 | 8.5833 | 10.6424 | 7.9396 | 231.3352 | 8.5229 | 410.4654
7.9266 | 240.0062 | 8.2183 | 611.8615 | 8.478 | 6.6445 | 7.927 | 245.5018 | 8.22 | 606.2891 | 8.4925 | 6.358 | 7.927 | 243.0911 | 8.2201 | 598.5387 | 8.4879 | 6.6159 | 7.9266 | 240.0062 | 8.2183 | 611.8615 | 8.478 | 6.6445 | 7.927 | 245.5018 | 8.22 | 606.2891 | 8.4925 | 6.358 | 7.927 | 243.0911 | 8.2201 | 598.5387 | 8.4879 | 6.6159 | 8.2651 | 41.2384 | 8.5166 | 398.2194 | 8.5098 | 394.4688 | 8.2651 | 41.2384 | 8.5166 | 398.2194 | 8.5098 | 394.4688 | 8.4378 | 39.1119 | 8.5833 | 10.6424 | 7.9396 | 231.3352 | 8.5229 | 410.4654 | 8.4378 | 39.1119 | 8.5833 | 10.6424 | 7.9396 | 231.3352 | 8.5229 | 410.4654
7.9248 | 288.0074 | 8.1448 | 734.2339 | 8.4075 | 7.9734 | 7.9244 | 294.6022 | 8.146 | 727.5469 | 8.4269 | 7.6296 | 7.9251 | 291.7093 | 8.1484 | 718.2465 | 8.4209 | 7.9391 | 7.9248 | 288.0074 | 8.1448 | 734.2339 | 8.4075 | 7.9734 | 7.9244 | 294.6022 | 8.146 | 727.5469 | 8.4269 | 7.6296 | 7.9251 | 291.7093 | 8.1484 | 718.2465 | 8.4209 | 7.9391 | 8.1373 | 49.486 | 8.4805 | 477.8633 | 8.4765 | 473.3625 | 8.1373 | 49.486 | 8.4805 | 477.8633 | 8.4765 | 473.3625 | 8.3485 | 46.9343 | 8.5354 | 12.7709 | 7.7662 | 277.6023 | 8.4841 | 492.5585 | 8.3485 | 46.9343 | 8.5354 | 12.7709 | 7.7662 | 277.6023 | 8.4841 | 492.5585
7.9248 | 288.0074 | 8.1448 | 734.2339 | 8.4075 | 7.9734 | 7.9244 | 294.6022 | 8.146 | 727.5469 | 8.4269 | 7.6296 | 7.9251 | 291.7093 | 8.1484 | 718.2465 | 8.4209 | 7.9391 | 7.9248 | 288.0074 | 8.1448 | 734.2339 | 8.4075 | 7.9734 | 7.9244 | 294.6022 | 8.146 | 727.5469 | 8.4269 | 7.6296 | 7.9251 | 291.7093 | 8.1484 | 718.2465 | 8.4209 | 7.9391 | 8.1373 | 49.486 | 8.4805 | 477.8633 | 8.4765 | 473.3625 | 8.1373 | 49.486 | 8.4805 | 477.8633 | 8.4765 | 473.3625 | 8.3485 | 46.9343 | 8.5354 | 12.7709 | 7.7662 | 277.6023 | 8.4841 | 492.5585 | 8.3485 | 46.9343 | 8.5354 | 12.7709 | 7.7662 | 277.6023 | 8.4841 | 492.5585
7.9235 | 336.0086 | 8.0818 | 856.6062 | 8.3484 | 9.3023 | 7.9231 | 343.7026 | 8.0812 | 848.8048 | 8.3678 | 8.9012 | 7.9241 | 340.3276 | 8.087 | 837.9542 | 8.3585 | 9.2623 | 7.9235 | 336.0086 | 8.0818 | 856.6062 | 8.3484 | 9.3023 | 7.9231 | 343.7026 | 8.0812 | 848.8048 | 8.3678 | 8.9012 | 7.9241 | 340.3276 | 8.087 | 837.9542 | 8.3585 | 9.2623 | 7.9999 | 57.7337 | 8.4483 | 557.5071 | 8.4439 | 552.2563 | 7.9999 | 57.7337 | 8.4483 | 557.5071 | 8.4439 | 552.2563 | 8.2624 | 54.7567 | 8.4917 | 14.8994 | 7.5936 | 323.8693 | 8.4519 | 574.6516 | 8.2624 | 54.7567 | 8.4917 | 14.8994 | 7.5936 | 323.8693 | 8.4519 | 574.6516
7.9235 | 336.0086 | 8.0818 | 856.6062 | 8.3484 | 9.3023 | 7.9231 | 343.7026 | 8.0812 | 848.8048 | 8.3678 | 8.9012 | 7.9241 | 340.3276 | 8.087 | 837.9542 | 8.3585 | 9.2623 | 7.9235 | 336.0086 | 8.0818 | 856.6062 | 8.3484 | 9.3023 | 7.9231 | 343.7026 | 8.0812 | 848.8048 | 8.3678 | 8.9012 | 7.9241 | 340.3276 | 8.087 | 837.9542 | 8.3585 | 9.2623 | 7.9999 | 57.7337 | 8.4483 | 557.5071 | 8.4439 | 552.2563 | 7.9999 | 57.7337 | 8.4483 | 557.5071 | 8.4439 | 552.2563 | 8.2624 | 54.7567 | 8.4917 | 14.8994 | 7.5936 | 323.8693 | 8.4519 | 574.6516 | 8.2624 | 54.7567 | 8.4917 | 14.8994 | 7.5936 | 323.8693 | 8.4519 | 574.6516
7.9228 | 384.0098 | 8.0315 | 978.9785 | 8.2941 | 10.6312 | 7.9224 | 392.8029 | 8.0317 | 970.0626 | 8.3118 | 10.1728 | 7.9234 | 388.9458 | 8.0362 | 957.6619 | 8.3019 | 10.5854 | 7.9228 | 384.0098 | 8.0315 | 978.9785 | 8.2941 | 10.6312 | 7.9224 | 392.8029 | 8.0317 | 970.0626 | 8.3118 | 10.1728 | 7.9234 | 388.9458 | 8.0362 | 957.6619 | 8.3019 | 10.5854 | 7.8695 | 65.9814 | 8.421 | 637.151 | 8.4152 | 631.1501 | 7.8695 | 65.9814 | 8.421 | 637.151 | 8.4152 | 631.1501 | 8.185 | 62.5791 | 8.4521 | 17.0279 | 7.4396 | 370.1363 | 8.4239 | 656.7447 | 8.185 | 62.5791 | 8.4521 | 17.0279 | 7.4396 | 370.1363 | 8.4239 | 656.7447
7.9228 | 384.0098 | 8.0315 | 978.9785 | 8.2941 | 10.6312 | 7.9224 | 392.8029 | 8.0317 | 970.0626 | 8.3118 | 10.1728 | 7.9234 | 388.9458 | 8.0362 | 957.6619 | 8.3019 | 10.5854 | 7.9228 | 384.0098 | 8.0315 | 978.9785 | 8.2941 | 10.6312 | 7.9224 | 392.8029 | 8.0317 | 970.0626 | 8.3118 | 10.1728 | 7.9234 | 388.9458 | 8.0362 | 957.6619 | 8.3019 | 10.5854 | 7.8695 | 65.9814 | 8.421 | 637.151 | 8.4152 | 631.1501 | 7.8695 | 65.9814 | 8.421 | 637.151 | 8.4152 | 631.1501 | 8.185 | 62.5791 | 8.4521 | 17.0279 | 7.4396 | 370.1363 | 8.4239 | 656.7447 | 8.185 | 62.5791 | 8.4521 | 17.0279 | 7.4396 | 370.1363 | 8.4239 | 656.7447
7.9223 | 432.0111 | 7.9824 | 1101.3508 | 8.2451 | 11.9601 | 7.9216 | 441.9033 | 7.986 | 1091.3204 | 8.2632 | 11.4444 | 7.9228 | 437.564 | 7.9942 | 1077.3697 | 8.2493 | 11.9086 | 7.9223 | 432.0111 | 7.9824 | 1101.3508 | 8.2451 | 11.9601 | 7.9216 | 441.9033 | 7.986 | 1091.3204 | 8.2632 | 11.4444 | 7.9228 | 437.564 | 7.9942 | 1077.3697 | 8.2493 | 11.9086 | 7.7455 | 74.2291 | 8.395 | 716.7949 | 8.3879 | 710.0438 | 7.7455 | 74.2291 | 8.395 | 716.7949 | 8.3879 | 710.0438 | 8.1087 | 70.4014 | 8.4164 | 19.1564 | 7.334 | 416.4034 | 8.3936 | 738.8378 | 8.1087 | 70.4014 | 8.4164 | 19.1564 | 7.334 | 416.4034 | 8.3936 | 738.8378
7.9223 | 432.0111 | 7.9824 | 1101.3508 | 8.2451 | 11.9601 | 7.9216 | 441.9033 | 7.986 | 1091.3204 | 8.2632 | 11.4444 | 7.9228 | 437.564 | 7.9942 | 1077.3697 | 8.2493 | 11.9086 | 7.9223 | 432.0111 | 7.9824 | 1101.3508 | 8.2451 | 11.9601 | 7.9216 | 441.9033 | 7.986 | 1091.3204 | 8.2632 | 11.4444 | 7.9228 | 437.564 | 7.9942 | 1077.3697 | 8.2493 | 11.9086 | 7.7455 | 74.2291 | 8.395 | 716.7949 | 8.3879 | 710.0438 | 7.7455 | 74.2291 | 8.395 | 716.7949 | 8.3879 | 710.0438 | 8.1087 | 70.4014 | 8.4164 | 19.1564 | 7.334 | 416.4034 | 8.3936 | 738.8378 | 8.1087 | 70.4014 | 8.4164 | 19.1564 | 7.334 | 416.4034 | 8.3936 | 738.8378
7.9219 | 480.0123 | 7.9383 | 1223.7231 | 8.2036 | 13.289 | 7.9213 | 491.0037 | 7.9448 | 1212.5782 | 8.221 | 12.7161 | 7.9222 | 486.1822 | 7.9521 | 1197.0774 | 8.206 | 13.2318 | 7.9219 | 480.0123 | 7.9383 | 1223.7231 | 8.2036 | 13.289 | 7.9213 | 491.0037 | 7.9448 | 1212.5782 | 8.221 | 12.7161 | 7.9222 | 486.1822 | 7.9521 | 1197.0774 | 8.206 | 13.2318 | 7.6521 | 82.4767 | 8.3665 | 796.4388 | 8.3569 | 788.9376 | 7.6521 | 82.4767 | 8.3665 | 796.4388 | 8.3569 | 788.9376 | 8.0401 | 78.2238 | 8.3856 | 21.2849 | 7.2225 | 462.6704 | 8.3632 | 820.9309 | 8.0401 | 78.2238 | 8.3856 | 21.2849 | 7.2225 | 462.6704 | 8.3632 | 820.9309
7.9219 | 480.0123 | 7.9383 | 1223.7231 | 8.2036 | 13.289 | 7.9213 | 491.0037 | 7.9448 | 1212.5782 | 8.221 | 12.7161 | 7.9222 | 486.1822 | 7.9521 | 1197.0774 | 8.206 | 13.2318 | 7.9219 | 480.0123 | 7.9383 | 1223.7231 | 8.2036 | 13.289 | 7.9213 | 491.0037 | 7.9448 | 1212.5782 | 8.221 | 12.7161 | 7.9222 | 486.1822 | 7.9521 | 1197.0774 | 8.206 | 13.2318 | 7.6521 | 82.4767 | 8.3665 | 796.4388 | 8.3569 | 788.9376 | 7.6521 | 82.4767 | 8.3665 | 796.4388 | 8.3569 | 788.9376 | 8.0401 | 78.2238 | 8.3856 | 21.2849 | 7.2225 | 462.6704 | 8.3632 | 820.9309 | 8.0401 | 78.2238 | 8.3856 | 21.2849 | 7.2225 | 462.6704 | 8.3632 | 820.9309
7.9217 | 528.0135 | 7.8995 | 1346.0954 | 8.1657 | 14.6179 | 7.921 | 540.104 | 7.9023 | 1333.8361 | 8.1811 | 13.9877 | 7.9218 | 534.8005 | 7.9134 | 1316.7852 | 8.1677 | 14.555 | 7.9217 | 528.0135 | 7.8995 | 1346.0954 | 8.1657 | 14.6179 | 7.921 | 540.104 | 7.9023 | 1333.8361 | 8.1811 | 13.9877 | 7.9218 | 534.8005 | 7.9134 | 1316.7852 | 8.1677 | 14.555 | 7.5568 | 90.7244 | 8.3381 | 876.0826 | 8.3248 | 867.8313 | 7.5568 | 90.7244 | 8.3381 | 876.0826 | 8.3248 | 867.8313 | 7.9718 | 86.0462 | 8.3579 | 23.4134 | 7.1492 | 508.9375 | 8.333 | 903.024 | 7.9718 | 86.0462 | 8.3579 | 23.4134 | 7.1492 | 508.9375 | 8.333 | 903.024
7.9217 | 528.0135 | 7.8995 | 1346.0954 | 8.1657 | 14.6179 | 7.921 | 540.104 | 7.9023 | 1333.8361 | 8.1811 | 13.9877 | 7.9218 | 534.8005 | 7.9134 | 1316.7852 | 8.1677 | 14.555 | 7.9217 | 528.0135 | 7.8995 | 1346.0954 | 8.1657 | 14.6179 | 7.921 | 540.104 | 7.9023 | 1333.8361 | 8.1811 | 13.9877 | 7.9218 | 534.8005 | 7.9134 | 1316.7852 | 8.1677 | 14.555 | 7.5568 | 90.7244 | 8.3381 | 876.0826 | 8.3248 | 867.8313 | 7.5568 | 90.7244 | 8.3381 | 876.0826 | 8.3248 | 867.8313 | 7.9718 | 86.0462 | 8.3579 | 23.4134 | 7.1492 | 508.9375 | 8.333 | 903.024 | 7.9718 | 86.0462 | 8.3579 | 23.4134 | 7.1492 | 508.9375 | 8.333 | 903.024
7.9216 | 576.0148 | 7.8597 | 1468.4677 | 8.1269 | 15.9468 | 7.9209 | 589.2044 | 7.8613 | 1455.0939 | 8.1463 | 15.2593 | 7.9217 | 583.4187 | 7.8709 | 1436.4929 | 8.1301 | 15.8782 | 7.9216 | 576.0148 | 7.8597 | 1468.4677 | 8.1269 | 15.9468 | 7.9209 | 589.2044 | 7.8613 | 1455.0939 | 8.1463 | 15.2593 | 7.9217 | 583.4187 | 7.8709 | 1436.4929 | 8.1301 | 15.8782 | 7.4746 | 98.9721 | 8.3065 | 955.7265 | 8.2957 | 946.7251 | 7.4746 | 98.9721 | 8.3065 | 955.7265 | 8.2957 | 946.7251 | 7.9104 | 93.8686 | 8.3322 | 25.5419 | 7.0802 | 555.2045 | 8.3026 | 985.1171 | 7.9104 | 93.8686 | 8.3322 | 25.5419 | 7.0802 | 555.2045 | 8.3026 | 985.1171
7.9216 | 576.0148 | 7.8597 | 1468.4677 | 8.1269 | 15.9468 | 7.9209 | 589.2044 | 7.8613 | 1455.0939 | 8.1463 | 15.2593 | 7.9217 | 583.4187 | 7.8709 | 1436.4929 | 8.1301 | 15.8782 | 7.9216 | 576.0148 | 7.8597 | 1468.4677 | 8.1269 | 15.9468 | 7.9209 | 589.2044 | 7.8613 | 1455.0939 | 8.1463 | 15.2593 | 7.9217 | 583.4187 | 7.8709 | 1436.4929 | 8.1301 | 15.8782 | 7.4746 | 98.9721 | 8.3065 | 955.7265 | 8.2957 | 946.7251 | 7.4746 | 98.9721 | 8.3065 | 955.7265 | 8.2957 | 946.7251 | 7.9104 | 93.8686 | 8.3322 | 25.5419 | 7.0802 | 555.2045 | 8.3026 | 985.1171 | 7.9104 | 93.8686 | 8.3322 | 25.5419 | 7.0802 | 555.2045 | 8.3026 | 985.1171
7.9211 | 624.016 | 7.8251 | 1590.84 | 8.095 | 17.2757 | 7.9207 | 638.3048 | 7.828 | 1576.3517 | 8.1141 | 16.5309 | 7.9213 | 632.0369 | 7.8354 | 1556.2006 | 8.0935 | 17.2014 | 7.9211 | 624.016 | 7.8251 | 1590.84 | 8.095 | 17.2757 | 7.9207 | 638.3048 | 7.828 | 1576.3517 | 8.1141 | 16.5309 | 7.9213 | 632.0369 | 7.8354 | 1556.2006 | 8.0935 | 17.2014 | 7.4018 | 107.2198 | 8.2752 | 1035.3704 | 8.2613 | 1025.6189 | 7.4018 | 107.2198 | 8.2752 | 1035.3704 | 8.2613 | 1025.6189 | 7.8475 | 101.691 | 8.3124 | 27.6703 | 7.0138 | 601.4716 | 8.2692 | 1067.2101 | 7.8475 | 101.691 | 8.3124 | 27.6703 | 7.0138 | 601.4716 | 8.2692 | 1067.2101
7.9211 | 624.016 | 7.8251 | 1590.84 | 8.095 | 17.2757 | 7.9207 | 638.3048 | 7.828 | 1576.3517 | 8.1141 | 16.5309 | 7.9213 | 632.0369 | 7.8354 | 1556.2006 | 8.0935 | 17.2014 | 7.9211 | 624.016 | 7.8251 | 1590.84 | 8.095 | 17.2757 | 7.9207 | 638.3048 | 7.828 | 1576.3517 | 8.1141 | 16.5309 | 7.9213 | 632.0369 | 7.8354 | 1556.2006 | 8.0935 | 17.2014 | 7.4018 | 107.2198 | 8.2752 | 1035.3704 | 8.2613 | 1025.6189 | 7.4018 | 107.2198 | 8.2752 | 1035.3704 | 8.2613 | 1025.6189 | 7.8475 | 101.691 | 8.3124 | 27.6703 | 7.0138 | 601.4716 | 8.2692 | 1067.2101 | 7.8475 | 101.691 | 8.3124 | 27.6703 | 7.0138 | 601.4716 | 8.2692 | 1067.2101
7.9207 | 672.0172 | 7.7856 | 1713.2123 | 8.0626 | 18.6046 | 7.9207 | 687.4051 | 7.7885 | 1697.6095 | 8.0799 | 17.8025 | 7.9212 | 680.6551 | 7.8031 | 1675.9084 | 8.0601 | 18.5245 | 7.9207 | 672.0172 | 7.7856 | 1713.2123 | 8.0626 | 18.6046 | 7.9207 | 687.4051 | 7.7885 | 1697.6095 | 8.0799 | 17.8025 | 7.9212 | 680.6551 | 7.8031 | 1675.9084 | 8.0601 | 18.5245 | 7.3311 | 115.4674 | 8.2427 | 1115.0143 | 8.2262 | 1104.5126 | 7.3311 | 115.4674 | 8.2427 | 1115.0143 | 8.2262 | 1104.5126 | 7.7789 | 109.5134 | 8.2945 | 29.7988 | 6.9741 | 647.7386 | 8.2304 | 1149.3032 | 7.7789 | 109.5134 | 8.2945 | 29.7988 | 6.9741 | 647.7386 | 8.2304 | 1149.3032
7.9207 | 672.0172 | 7.7856 | 1713.2123 | 8.0626 | 18.6046 | 7.9207 | 687.4051 | 7.7885 | 1697.6095 | 8.0799 | 17.8025 | 7.9212 | 680.6551 | 7.8031 | 1675.9084 | 8.0601 | 18.5245 | 7.9207 | 672.0172 | 7.7856 | 1713.2123 | 8.0626 | 18.6046 | 7.9207 | 687.4051 | 7.7885 | 1697.6095 | 8.0799 | 17.8025 | 7.9212 | 680.6551 | 7.8031 | 1675.9084 | 8.0601 | 18.5245 | 7.3311 | 115.4674 | 8.2427 | 1115.0143 | 8.2262 | 1104.5126 | 7.3311 | 115.4674 | 8.2427 | 1115.0143 | 8.2262 | 1104.5126 | 7.7789 | 109.5134 | 8.2945 | 29.7988 | 6.9741 | 647.7386 | 8.2304 | 1149.3032 | 7.7789 | 109.5134 | 8.2945 | 29.7988 | 6.9741 | 647.7386 | 8.2304 | 1149.3032
7.9207 | 720.0185 | 7.7524 | 1835.5846 | 8.0309 | 19.9335 | 7.9205 | 736.5055 | 7.7468 | 1818.8673 | 8.0508 | 19.0741 | 7.9211 | 729.2734 | 7.7679 | 1795.6161 | 8.0307 | 19.8477 | 7.9207 | 720.0185 | 7.7524 | 1835.5846 | 8.0309 | 19.9335 | 7.9205 | 736.5055 | 7.7468 | 1818.8673 | 8.0508 | 19.0741 | 7.9211 | 729.2734 | 7.7679 | 1795.6161 | 8.0307 | 19.8477 | 7.2647 | 123.7151 | 8.2039 | 1194.6581 | 8.1902 | 1183.4064 | 7.2647 | 123.7151 | 8.2039 | 1194.6581 | 8.1902 | 1183.4064 | 7.714 | 117.3357 | 8.2784 | 31.9273 | 6.9168 | 694.0056 | 8.1918 | 1231.3963 | 7.714 | 117.3357 | 8.2784 | 31.9273 | 6.9168 | 694.0056 | 8.1918 | 1231.3963
7.9207 | 720.0185 | 7.7524 | 1835.5846 | 8.0309 | 19.9335 | 7.9205 | 736.5055 | 7.7468 | 1818.8673 | 8.0508 | 19.0741 | 7.9211 | 729.2734 | 7.7679 | 1795.6161 | 8.0307 | 19.8477 | 7.9207 | 720.0185 | 7.7524 | 1835.5846 | 8.0309 | 19.9335 | 7.9205 | 736.5055 | 7.7468 | 1818.8673 | 8.0508 | 19.0741 | 7.9211 | 729.2734 | 7.7679 | 1795.6161 | 8.0307 | 19.8477 | 7.2647 | 123.7151 | 8.2039 | 1194.6581 | 8.1902 | 1183.4064 | 7.2647 | 123.7151 | 8.2039 | 1194.6581 | 8.1902 | 1183.4064 | 7.714 | 117.3357 | 8.2784 | 31.9273 | 6.9168 | 694.0056 | 8.1918 | 1231.3963 | 7.714 | 117.3357 | 8.2784 | 31.9273 | 6.9168 | 694.0056 | 8.1918 | 1231.3963
7.9206 | 768.0197 | 7.7178 | 1957.9569 | 7.9971 | 21.2624 | 7.9204 | 785.6059 | 7.7194 | 1940.1252 | 8.0232 | 20.3457 | 7.921 | 777.8916 | 7.726 | 1915.3239 | 8.0006 | 21.1709 | 7.9206 | 768.0197 | 7.7178 | 1957.9569 | 7.9971 | 21.2624 | 7.9204 | 785.6059 | 7.7194 | 1940.1252 | 8.0232 | 20.3457 | 7.921 | 777.8916 | 7.726 | 1915.3239 | 8.0006 | 21.1709 | 7.2033 | 131.9628 | 8.1693 | 1274.302 | 8.1506 | 1262.3001 | 7.2033 | 131.9628 | 8.1693 | 1274.302 | 8.1506 | 1262.3001 | 7.6571 | 125.1581 | 8.2647 | 34.0558 | 6.8663 | 740.2727 | 8.156 | 1313.4894 | 7.6571 | 125.1581 | 8.2647 | 34.0558 | 6.8663 | 740.2727 | 8.156 | 1313.4894
7.9206 | 768.0197 | 7.7178 | 1957.9569 | 7.9971 | 21.2624 | 7.9204 | 785.6059 | 7.7194 | 1940.1252 | 8.0232 | 20.3457 | 7.921 | 777.8916 | 7.726 | 1915.3239 | 8.0006 | 21.1709 | 7.9206 | 768.0197 | 7.7178 | 1957.9569 | 7.9971 | 21.2624 | 7.9204 | 785.6059 | 7.7194 | 1940.1252 | 8.0232 | 20.3457 | 7.921 | 777.8916 | 7.726 | 1915.3239 | 8.0006 | 21.1709 | 7.2033 | 131.9628 | 8.1693 | 1274.302 | 8.1506 | 1262.3001 | 7.2033 | 131.9628 | 8.1693 | 1274.302 | 8.1506 | 1262.3001 | 7.6571 | 125.1581 | 8.2647 | 34.0558 | 6.8663 | 740.2727 | 8.156 | 1313.4894 | 7.6571 | 125.1581 | 8.2647 | 34.0558 | 6.8663 | 740.2727 | 8.156 | 1313.4894
7.9206 | 816.0209 | 7.6837 | 2080.3293 | 7.9663 | 22.5913 | 7.9203 | 834.7063 | 7.6862 | 2061.383 | 7.991 | 21.6173 | 7.921 | 826.5098 | 7.6881 | 2035.0316 | 7.9715 | 22.4941 | 7.9206 | 816.0209 | 7.6837 | 2080.3293 | 7.9663 | 22.5913 | 7.9203 | 834.7063 | 7.6862 | 2061.383 | 7.991 | 21.6173 | 7.921 | 826.5098 | 7.6881 | 2035.0316 | 7.9715 | 22.4941 | 7.1503 | 140.2105 | 8.1302 | 1353.9459 | 8.1125 | 1341.1939 | 7.1503 | 140.2105 | 8.1302 | 1353.9459 | 8.1125 | 1341.1939 | 7.6023 | 132.9805 | 8.2517 | 36.1843 | 6.8134 | 786.5397 | 8.1134 | 1395.5825 | 7.6023 | 132.9805 | 8.2517 | 36.1843 | 6.8134 | 786.5397 | 8.1134 | 1395.5825
7.9206 | 816.0209 | 7.6837 | 2080.3293 | 7.9663 | 22.5913 | 7.9203 | 834.7063 | 7.6862 | 2061.383 | 7.991 | 21.6173 | 7.921 | 826.5098 | 7.6881 | 2035.0316 | 7.9715 | 22.4941 | 7.9206 | 816.0209 | 7.6837 | 2080.3293 | 7.9663 | 22.5913 | 7.9203 | 834.7063 | 7.6862 | 2061.383 | 7.991 | 21.6173 | 7.921 | 826.5098 | 7.6881 | 2035.0316 | 7.9715 | 22.4941 | 7.1503 | 140.2105 | 8.1302 | 1353.9459 | 8.1125 | 1341.1939 | 7.1503 | 140.2105 | 8.1302 | 1353.9459 | 8.1125 | 1341.1939 | 7.6023 | 132.9805 | 8.2517 | 36.1843 | 6.8134 | 786.5397 | 8.1134 | 1395.5825 | 7.6023 | 132.9805 | 8.2517 | 36.1843 | 6.8134 | 786.5397 | 8.1134 | 1395.5825
7.9205 | 864.0222 | 7.6549 | 2202.7016 | 7.9347 | 23.9202 | 7.9201 | 883.8066 | 7.6538 | 2182.6408 | 7.9578 | 22.8889 | 7.9209 | 875.128 | 7.6615 | 2154.7394 | 7.9392 | 23.8173 | 7.9205 | 864.0222 | 7.6549 | 2202.7016 | 7.9347 | 23.9202 | 7.9201 | 883.8066 | 7.6538 | 2182.6408 | 7.9578 | 22.8889 | 7.9209 | 875.128 | 7.6615 | 2154.7394 | 7.9392 | 23.8173 | 7.092 | 148.4581 | 8.0936 | 1433.5898 | 8.0701 | 1420.0876 | 7.092 | 148.4581 | 8.0936 | 1433.5898 | 8.0701 | 1420.0876 | 7.5503 | 140.8029 | 8.2393 | 38.3128 | 6.7761 | 832.8068 | 8.0802 | 1477.6756 | 7.5503 | 140.8029 | 8.2393 | 38.3128 | 6.7761 | 832.8068 | 8.0802 | 1477.6756
7.9205 | 864.0222 | 7.6549 | 2202.7016 | 7.9347 | 23.9202 | 7.9201 | 883.8066 | 7.6538 | 2182.6408 | 7.9578 | 22.8889 | 7.9209 | 875.128 | 7.6615 | 2154.7394 | 7.9392 | 23.8173 | 7.9205 | 864.0222 | 7.6549 | 2202.7016 | 7.9347 | 23.9202 | 7.9201 | 883.8066 | 7.6538 | 2182.6408 | 7.9578 | 22.8889 | 7.9209 | 875.128 | 7.6615 | 2154.7394 | 7.9392 | 23.8173 | 7.092 | 148.4581 | 8.0936 | 1433.5898 | 8.0701 | 1420.0876 | 7.092 | 148.4581 | 8.0936 | 1433.5898 | 8.0701 | 1420.0876 | 7.5503 | 140.8029 | 8.2393 | 38.3128 | 6.7761 | 832.8068 | 8.0802 | 1477.6756 | 7.5503 | 140.8029 | 8.2393 | 38.3128 | 6.7761 | 832.8068 | 8.0802 | 1477.6756
7.9205 | 912.0234 | 7.6218 | 2325.0739 | 7.8994 | 25.2491 | 7.9201 | 932.907 | 7.6234 | 2303.8986 | 7.9294 | 24.1605 | 7.9208 | 923.7463 | 7.6299 | 2274.4471 | 7.9079 | 25.1404 | 7.9205 | 912.0234 | 7.6218 | 2325.0739 | 7.8994 | 25.2491 | 7.9201 | 932.907 | 7.6234 | 2303.8986 | 7.9294 | 24.1605 | 7.9208 | 923.7463 | 7.6299 | 2274.4471 | 7.9079 | 25.1404 | 7.0403 | 156.7058 | 8.0583 | 1513.2336 | 8.031 | 1498.9814 | 7.0403 | 156.7058 | 8.0583 | 1513.2336 | 8.031 | 1498.9814 | 7.4938 | 148.6253 | 8.227 | 40.4413 | 6.7347 | 879.0738 | 8.0394 | 1559.7687 | 7.4938 | 148.6253 | 8.227 | 40.4413 | 6.7347 | 879.0738 | 8.0394 | 1559.7687
7.9205 | 912.0234 | 7.6218 | 2325.0739 | 7.8994 | 25.2491 | 7.9201 | 932.907 | 7.6234 | 2303.8986 | 7.9294 | 24.1605 | 7.9208 | 923.7463 | 7.6299 | 2274.4471 | 7.9079 | 25.1404 | 7.9205 | 912.0234 | 7.6218 | 2325.0739 | 7.8994 | 25.2491 | 7.9201 | 932.907 | 7.6234 | 2303.8986 | 7.9294 | 24.1605 | 7.9208 | 923.7463 | 7.6299 | 2274.4471 | 7.9079 | 25.1404 | 7.0403 | 156.7058 | 8.0583 | 1513.2336 | 8.031 | 1498.9814 | 7.0403 | 156.7058 | 8.0583 | 1513.2336 | 8.031 | 1498.9814 | 7.4938 | 148.6253 | 8.227 | 40.4413 | 6.7347 | 879.0738 | 8.0394 | 1559.7687 | 7.4938 | 148.6253 | 8.227 | 40.4413 | 6.7347 | 879.0738 | 8.0394 | 1559.7687
7.9203 | 960.0246 | 7.5923 | 2447.4462 | 7.8709 | 26.578 | 7.92 | 982.0074 | 7.5883 | 2425.1565 | 7.9007 | 25.4321 | 7.9207 | 972.3645 | 7.6008 | 2394.1548 | 7.8749 | 26.4636 | 7.9203 | 960.0246 | 7.5923 | 2447.4462 | 7.8709 | 26.578 | 7.92 | 982.0074 | 7.5883 | 2425.1565 | 7.9007 | 25.4321 | 7.9207 | 972.3645 | 7.6008 | 2394.1548 | 7.8749 | 26.4636 | 6.9933 | 164.9535 | 8.0202 | 1592.8775 | 7.9914 | 1577.8752 | 6.9933 | 164.9535 | 8.0202 | 1592.8775 | 7.9914 | 1577.8752 | 7.4407 | 156.4477 | 8.2153 | 42.5698 | 6.6944 | 925.3409 | 7.9976 | 1641.8618 | 7.4407 | 156.4477 | 8.2153 | 42.5698 | 6.6944 | 925.3409 | 7.9976 | 1641.8618
7.9203 | 960.0246 | 7.5923 | 2447.4462 | 7.8709 | 26.578 | 7.92 | 982.0074 | 7.5883 | 2425.1565 | 7.9007 | 25.4321 | 7.9207 | 972.3645 | 7.6008 | 2394.1548 | 7.8749 | 26.4636 | 7.9203 | 960.0246 | 7.5923 | 2447.4462 | 7.8709 | 26.578 | 7.92 | 982.0074 | 7.5883 | 2425.1565 | 7.9007 | 25.4321 | 7.9207 | 972.3645 | 7.6008 | 2394.1548 | 7.8749 | 26.4636 | 6.9933 | 164.9535 | 8.0202 | 1592.8775 | 7.9914 | 1577.8752 | 6.9933 | 164.9535 | 8.0202 | 1592.8775 | 7.9914 | 1577.8752 | 7.4407 | 156.4477 | 8.2153 | 42.5698 | 6.6944 | 925.3409 | 7.9976 | 1641.8618 | 7.4407 | 156.4477 | 8.2153 | 42.5698 | 6.6944 | 925.3409 | 7.9976 | 1641.8618
7.9201 | 1008.0259 | 7.5587 | 2569.8185 | 7.834 | 27.9069 | 7.92 | 1031.1077 | 7.5582 | 2546.4143 | 7.8721 | 26.7037 | 7.9207 | 1020.9827 | 7.5719 | 2513.8626 | 7.8408 | 27.7868 | 7.9201 | 1008.0259 | 7.5587 | 2569.8185 | 7.834 | 27.9069 | 7.92 | 1031.1077 | 7.5582 | 2546.4143 | 7.8721 | 26.7037 | 7.9207 | 1020.9827 | 7.5719 | 2513.8626 | 7.8408 | 27.7868 | 6.9421 | 173.2011 | 7.9816 | 1672.5214 | 7.9486 | 1656.7689 | 6.9421 | 173.2011 | 7.9816 | 1672.5214 | 7.9486 | 1656.7689 | 7.3924 | 164.27 | 8.2035 | 44.6982 | 6.6665 | 971.6079 | 7.9552 | 1723.9548 | 7.3924 | 164.27 | 8.2035 | 44.6982 | 6.6665 | 971.6079 | 7.9552 | 1723.9548
7.9201 | 1008.0259 | 7.5587 | 2569.8185 | 7.834 | 27.9069 | 7.92 | 1031.1077 | 7.5582 | 2546.4143 | 7.8721 | 26.7037 | 7.9207 | 1020.9827 | 7.5719 | 2513.8626 | 7.8408 | 27.7868 | 7.9201 | 1008.0259 | 7.5587 | 2569.8185 | 7.834 | 27.9069 | 7.92 | 1031.1077 | 7.5582 | 2546.4143 | 7.8721 | 26.7037 | 7.9207 | 1020.9827 | 7.5719 | 2513.8626 | 7.8408 | 27.7868 | 6.9421 | 173.2011 | 7.9816 | 1672.5214 | 7.9486 | 1656.7689 | 6.9421 | 173.2011 | 7.9816 | 1672.5214 | 7.9486 | 1656.7689 | 7.3924 | 164.27 | 8.2035 | 44.6982 | 6.6665 | 971.6079 | 7.9552 | 1723.9548 | 7.3924 | 164.27 | 8.2035 | 44.6982 | 6.6665 | 971.6079 | 7.9552 | 1723.9548
7.9201 | 1056.0271 | 7.5311 | 2692.1908 | 7.801 | 29.2358 | 7.9199 | 1080.2081 | 7.5322 | 2667.6721 | 7.8381 | 27.9753 | 7.9207 | 1069.6009 | 7.543 | 2633.5703 | 7.8066 | 29.11 | 7.9201 | 1056.0271 | 7.5311 | 2692.1908 | 7.801 | 29.2358 | 7.9199 | 1080.2081 | 7.5322 | 2667.6721 | 7.8381 | 27.9753 | 7.9207 | 1069.6009 | 7.543 | 2633.5703 | 7.8066 | 29.11 | 6.8879 | 181.4488 | 7.9402 | 1752.1653 | 7.9151 | 1735.6627 | 6.8879 | 181.4488 | 7.9402 | 1752.1653 | 7.9151 | 1735.6627 | 7.3409 | 172.0924 | 8.1912 | 46.8267 | 6.6182 | 1017.8749 | 7.9133 | 1806.0479 | 7.3409 | 172.0924 | 8.1912 | 46.8267 | 6.6182 | 1017.8749 | 7.9133 | 1806.0479
7.9201 | 1056.0271 | 7.5311 | 2692.1908 | 7.801 | 29.2358 | 7.9199 | 1080.2081 | 7.5322 | 2667.6721 | 7.8381 | 27.9753 | 7.9207 | 1069.6009 | 7.543 | 2633.5703 | 7.8066 | 29.11 | 7.9201 | 1056.0271 | 7.5311 | 2692.1908 | 7.801 | 29.2358 | 7.9199 | 1080.2081 | 7.5322 | 2667.6721 | 7.8381 | 27.9753 | 7.9207 | 1069.6009 | 7.543 | 2633.5703 | 7.8066 | 29.11 | 6.8879 | 181.4488 | 7.9402 | 1752.1653 | 7.9151 | 1735.6627 | 6.8879 | 181.4488 | 7.9402 | 1752.1653 | 7.9151 | 1735.6627 | 7.3409 | 172.0924 | 8.1912 | 46.8267 | 6.6182 | 1017.8749 | 7.9133 | 1806.0479 | 7.3409 | 172.0924 | 8.1912 | 46.8267 | 6.6182 | 1017.8749 | 7.9133 | 1806.0479
7.9201 | 1104.0283 | 7.5024 | 2814.5631 | 7.766 | 30.5647 | 7.9198 | 1129.3085 | 7.5074 | 2788.9299 | 7.8022 | 29.2469 | 7.9206 | 1118.2192 | 7.5131 | 2753.2781 | 7.7743 | 30.4332 | 7.9201 | 1104.0283 | 7.5024 | 2814.5631 | 7.766 | 30.5647 | 7.9198 | 1129.3085 | 7.5074 | 2788.9299 | 7.8022 | 29.2469 | 7.9206 | 1118.2192 | 7.5131 | 2753.2781 | 7.7743 | 30.4332 | 6.831 | 189.6965 | 7.8953 | 1831.8091 | 7.8753 | 1814.5564 | 6.831 | 189.6965 | 7.8953 | 1831.8091 | 7.8753 | 1814.5564 | 7.281 | 179.9148 | 8.179 | 48.9552 | 6.5773 | 1064.142 | 7.8736 | 1888.141 | 7.281 | 179.9148 | 8.179 | 48.9552 | 6.5773 | 1064.142 | 7.8736 | 1888.141
7.9201 | 1104.0283 | 7.5024 | 2814.5631 | 7.766 | 30.5647 | 7.9198 | 1129.3085 | 7.5074 | 2788.9299 | 7.8022 | 29.2469 | 7.9206 | 1118.2192 | 7.5131 | 2753.2781 | 7.7743 | 30.4332 | 7.9201 | 1104.0283 | 7.5024 | 2814.5631 | 7.766 | 30.5647 | 7.9198 | 1129.3085 | 7.5074 | 2788.9299 | 7.8022 | 29.2469 | 7.9206 | 1118.2192 | 7.5131 | 2753.2781 | 7.7743 | 30.4332 | 6.831 | 189.6965 | 7.8953 | 1831.8091 | 7.8753 | 1814.5564 | 6.831 | 189.6965 | 7.8953 | 1831.8091 | 7.8753 | 1814.5564 | 7.281 | 179.9148 | 8.179 | 48.9552 | 6.5773 | 1064.142 | 7.8736 | 1888.141 | 7.281 | 179.9148 | 8.179 | 48.9552 | 6.5773 | 1064.142 | 7.8736 | 1888.141
7.9201 | 1152.0295 | 7.4774 | 2936.9354 | 7.7325 | 31.8936 | 7.9198 | 1178.4088 | 7.4808 | 2910.1878 | 7.773 | 30.5185 | 7.9206 | 1166.8374 | 7.4845 | 2872.9858 | 7.7378 | 31.7563 | 7.9201 | 1152.0295 | 7.4774 | 2936.9354 | 7.7325 | 31.8936 | 7.9198 | 1178.4088 | 7.4808 | 2910.1878 | 7.773 | 30.5185 | 7.9206 | 1166.8374 | 7.4845 | 2872.9858 | 7.7378 | 31.7563 | 6.7902 | 197.9442 | 7.8591 | 1911.453 | 7.8294 | 1893.4502 | 6.7902 | 197.9442 | 7.8591 | 1911.453 | 7.8294 | 1893.4502 | 7.235 | 187.7372 | 8.1669 | 51.0837 | 6.5452 | 1110.409 | 7.8291 | 1970.2341 | 7.235 | 187.7372 | 8.1669 | 51.0837 | 6.5452 | 1110.409 | 7.8291 | 1970.2341
7.9201 | 1152.0295 | 7.4774 | 2936.9354 | 7.7325 | 31.8936 | 7.9198 | 1178.4088 | 7.4808 | 2910.1878 | 7.773 | 30.5185 | 7.9206 | 1166.8374 | 7.4845 | 2872.9858 | 7.7378 | 31.7563 | 7.9201 | 1152.0295 | 7.4774 | 2936.9354 | 7.7325 | 31.8936 | 7.9198 | 1178.4088 | 7.4808 | 2910.1878 | 7.773 | 30.5185 | 7.9206 | 1166.8374 | 7.4845 | 2872.9858 | 7.7378 | 31.7563 | 6.7902 | 197.9442 | 7.8591 | 1911.453 | 7.8294 | 1893.4502 | 6.7902 | 197.9442 | 7.8591 | 1911.453 | 7.8294 | 1893.4502 | 7.235 | 187.7372 | 8.1669 | 51.0837 | 6.5452 | 1110.409 | 7.8291 | 1970.2341 | 7.235 | 187.7372 | 8.1669 | 51.0837 | 6.5452 | 1110.409 | 7.8291 | 1970.2341
7.9201 | 1200.0308 | 7.4465 | 3059.3077 | 7.7025 | 33.2225 | 7.9198 | 1227.5092 | 7.4518 | 3031.4456 | 7.7374 | 31.7901 | 7.9205 | 1215.4556 | 7.4633 | 2992.6935 | 7.7086 | 33.0795 | 7.9201 | 1200.0308 | 7.4465 | 3059.3077 | 7.7025 | 33.2225 | 7.9198 | 1227.5092 | 7.4518 | 3031.4456 | 7.7374 | 31.7901 | 7.9205 | 1215.4556 | 7.4633 | 2992.6935 | 7.7086 | 33.0795 | 6.7455 | 206.1918 | 7.817 | 1991.0969 | 7.785 | 1972.3439 | 6.7455 | 206.1918 | 7.817 | 1991.0969 | 7.785 | 1972.3439 | 7.1823 | 195.5596 | 8.1557 | 53.2122 | 6.5205 | 1156.6761 | 7.7847 | 2052.3272 | 7.1823 | 195.5596 | 8.1557 | 53.2122 | 6.5205 | 1156.6761 | 7.7847 | 2052.3272
7.9201 | 1200.0308 | 7.4465 | 3059.3077 | 7.7025 | 33.2225 | 7.9198 | 1227.5092 | 7.4518 | 3031.4456 | 7.7374 | 31.7901 | 7.9205 | 1215.4556 | 7.4633 | 2992.6935 | 7.7086 | 33.0795 | 7.9201 | 1200.0308 | 7.4465 | 3059.3077 | 7.7025 | 33.2225 | 7.9198 | 1227.5092 | 7.4518 | 3031.4456 | 7.7374 | 31.7901 | 7.9205 | 1215.4556 | 7.4633 | 2992.6935 | 7.7086 | 33.0795 | 6.7455 | 206.1918 | 7.817 | 1991.0969 | 7.785 | 1972.3439 | 6.7455 | 206.1918 | 7.817 | 1991.0969 | 7.785 | 1972.3439 | 7.1823 | 195.5596 | 8.1557 | 53.2122 | 6.5205 | 1156.6761 | 7.7847 | 2052.3272 | 7.1823 | 195.5596 | 8.1557 | 53.2122 | 6.5205 | 1156.6761 | 7.7847 | 2052.3272
7.9201 | 1248.032 | 7.4128 | 3181.68 | 7.6689 | 34.5514 | 7.9198 | 1276.6096 | 7.4252 | 3152.7034 | 7.7071 | 33.0617 | 7.9202 | 1264.0738 | 7.4339 | 3112.4013 | 7.6726 | 34.4027 | 7.9201 | 1248.032 | 7.4128 | 3181.68 | 7.6689 | 34.5514 | 7.9198 | 1276.6096 | 7.4252 | 3152.7034 | 7.7071 | 33.0617 | 7.9202 | 1264.0738 | 7.4339 | 3112.4013 | 7.6726 | 34.4027 | 6.7013 | 214.4395 | 7.7817 | 2070.7408 | 7.7498 | 2051.2377 | 6.7013 | 214.4395 | 7.7817 | 2070.7408 | 7.7498 | 2051.2377 | 7.1281 | 203.382 | 8.1417 | 55.3407 | 6.4664 | 1202.9431 | 7.7505 | 2134.4203 | 7.1281 | 203.382 | 8.1417 | 55.3407 | 6.4664 | 1202.9431 | 7.7505 | 2134.4203
7.9201 | 1248.032 | 7.4128 | 3181.68 | 7.6689 | 34.5514 | 7.9198 | 1276.6096 | 7.4252 | 3152.7034 | 7.7071 | 33.0617 | 7.9202 | 1264.0738 | 7.4339 | 3112.4013 | 7.6726 | 34.4027 | 7.9201 | 1248.032 | 7.4128 | 3181.68 | 7.6689 | 34.5514 | 7.9198 | 1276.6096 | 7.4252 | 3152.7034 | 7.7071 | 33.0617 | 7.9202 | 1264.0738 | 7.4339 | 3112.4013 | 7.6726 | 34.4027 | 6.7013 | 214.4395 | 7.7817 | 2070.7408 | 7.7498 | 2051.2377 | 6.7013 | 214.4395 | 7.7817 | 2070.7408 | 7.7498 | 2051.2377 | 7.1281 | 203.382 | 8.1417 | 55.3407 | 6.4664 | 1202.9431 | 7.7505 | 2134.4203 | 7.1281 | 203.382 | 8.1417 | 55.3407 | 6.4664 | 1202.9431 | 7.7505 | 2134.4203
7.9201 | 1296.0332 | 7.3795 | 3304.0523 | 7.632 | 35.8803 | 7.9194 | 1325.7099 | 7.3932 | 3273.9612 | 7.6707 | 34.3333 | 7.9202 | 1312.6921 | 7.3964 | 3232.109 | 7.6358 | 35.7259 | 7.9201 | 1296.0332 | 7.3795 | 3304.0523 | 7.632 | 35.8803 | 7.9194 | 1325.7099 | 7.3932 | 3273.9612 | 7.6707 | 34.3333 | 7.9202 | 1312.6921 | 7.3964 | 3232.109 | 7.6358 | 35.7259 | 6.652 | 222.6872 | 7.7438 | 2150.3846 | 7.707 | 2130.1315 | 6.652 | 222.6872 | 7.7438 | 2150.3846 | 7.707 | 2130.1315 | 7.0782 | 211.2043 | 8.1278 | 57.4692 | 6.4385 | 1249.2102 | 7.7123 | 2216.5134 | 7.0782 | 211.2043 | 8.1278 | 57.4692 | 6.4385 | 1249.2102 | 7.7123 | 2216.5134
7.9201 | 1296.0332 | 7.3795 | 3304.0523 | 7.632 | 35.8803 | 7.9194 | 1325.7099 | 7.3932 | 3273.9612 | 7.6707 | 34.3333 | 7.9202 | 1312.6921 | 7.3964 | 3232.109 | 7.6358 | 35.7259 | 7.9201 | 1296.0332 | 7.3795 | 3304.0523 | 7.632 | 35.8803 | 7.9194 | 1325.7099 | 7.3932 | 3273.9612 | 7.6707 | 34.3333 | 7.9202 | 1312.6921 | 7.3964 | 3232.109 | 7.6358 | 35.7259 | 6.652 | 222.6872 | 7.7438 | 2150.3846 | 7.707 | 2130.1315 | 6.652 | 222.6872 | 7.7438 | 2150.3846 | 7.707 | 2130.1315 | 7.0782 | 211.2043 | 8.1278 | 57.4692 | 6.4385 | 1249.2102 | 7.7123 | 2216.5134 | 7.0782 | 211.2043 | 8.1278 | 57.4692 | 6.4385 | 1249.2102 | 7.7123 | 2216.5134
7.9201 | 1344.0345 | 7.349 | 3426.4247 | 7.6029 | 37.2092 | 7.9194 | 1374.8103 | 7.3556 | 3395.219 | 7.6376 | 35.6049 | 7.9202 | 1361.3103 | 7.3674 | 3351.8168 | 7.6048 | 37.0491 | 7.9201 | 1344.0345 | 7.349 | 3426.4247 | 7.6029 | 37.2092 | 7.9194 | 1374.8103 | 7.3556 | 3395.219 | 7.6376 | 35.6049 | 7.9202 | 1361.3103 | 7.3674 | 3351.8168 | 7.6048 | 37.0491 | 6.6142 | 230.9349 | 7.7075 | 2230.0285 | 7.6674 | 2209.0252 | 6.6142 | 230.9349 | 7.7075 | 2230.0285 | 7.6674 | 2209.0252 | 7.0257 | 219.0267 | 8.1155 | 59.5977 | 6.3944 | 1295.4772 | 7.6667 | 2298.6065 | 7.0257 | 219.0267 | 8.1155 | 59.5977 | 6.3944 | 1295.4772 | 7.6667 | 2298.6065
7.9201 | 1344.0345 | 7.349 | 3426.4247 | 7.6029 | 37.2092 | 7.9194 | 1374.8103 | 7.3556 | 3395.219 | 7.6376 | 35.6049 | 7.9202 | 1361.3103 | 7.3674 | 3351.8168 | 7.6048 | 37.0491 | 7.9201 | 1344.0345 | 7.349 | 3426.4247 | 7.6029 | 37.2092 | 7.9194 | 1374.8103 | 7.3556 | 3395.219 | 7.6376 | 35.6049 | 7.9202 | 1361.3103 | 7.3674 | 3351.8168 | 7.6048 | 37.0491 | 6.6142 | 230.9349 | 7.7075 | 2230.0285 | 7.6674 | 2209.0252 | 6.6142 | 230.9349 | 7.7075 | 2230.0285 | 7.6674 | 2209.0252 | 7.0257 | 219.0267 | 8.1155 | 59.5977 | 6.3944 | 1295.4772 | 7.6667 | 2298.6065 | 7.0257 | 219.0267 | 8.1155 | 59.5977 | 6.3944 | 1295.4772 | 7.6667 | 2298.6065
7.9201 | 1392.0357 | 7.3082 | 3548.797 | 7.5677 | 38.5381 | 7.9192 | 1423.9107 | 7.32 | 3516.4769 | 7.607 | 36.8765 | 7.9202 | 1409.9285 | 7.3302 | 3471.5245 | 7.5611 | 38.3723 | 7.9201 | 1392.0357 | 7.3082 | 3548.797 | 7.5677 | 38.5381 | 7.9192 | 1423.9107 | 7.32 | 3516.4769 | 7.607 | 36.8765 | 7.9202 | 1409.9285 | 7.3302 | 3471.5245 | 7.5611 | 38.3723 | 6.5851 | 239.1825 | 7.6695 | 2309.6724 | 7.6249 | 2287.919 | 6.5851 | 239.1825 | 7.6695 | 2309.6724 | 7.6249 | 2287.919 | 6.9806 | 226.8491 | 8.1055 | 61.7262 | 6.3737 | 1341.7442 | 7.6251 | 2380.6995 | 6.9806 | 226.8491 | 8.1055 | 61.7262 | 6.3737 | 1341.7442 | 7.6251 | 2380.6995
7.9201 | 1392.0357 | 7.3082 | 3548.797 | 7.5677 | 38.5381 | 7.9192 | 1423.9107 | 7.32 | 3516.4769 | 7.607 | 36.8765 | 7.9202 | 1409.9285 | 7.3302 | 3471.5245 | 7.5611 | 38.3723 | 7.9201 | 1392.0357 | 7.3082 | 3548.797 | 7.5677 | 38.5381 | 7.9192 | 1423.9107 | 7.32 | 3516.4769 | 7.607 | 36.8765 | 7.9202 | 1409.9285 | 7.3302 | 3471.5245 | 7.5611 | 38.3723 | 6.5851 | 239.1825 | 7.6695 | 2309.6724 | 7.6249 | 2287.919 | 6.5851 | 239.1825 | 7.6695 | 2309.6724 | 7.6249 | 2287.919 | 6.9806 | 226.8491 | 8.1055 | 61.7262 | 6.3737 | 1341.7442 | 7.6251 | 2380.6995 | 6.9806 | 226.8491 | 8.1055 | 61.7262 | 6.3737 | 1341.7442 | 7.6251 | 2380.6995
7.9201 | 1440.0369 | 7.2779 | 3671.1693 | 7.5309 | 39.867 | 7.9192 | 1473.011 | 7.2882 | 3637.7347 | 7.5748 | 38.1482 | 7.9202 | 1458.5467 | 7.2944 | 3591.2323 | 7.5256 | 39.6954 | 7.9201 | 1440.0369 | 7.2779 | 3671.1693 | 7.5309 | 39.867 | 7.9192 | 1473.011 | 7.2882 | 3637.7347 | 7.5748 | 38.1482 | 7.9202 | 1458.5467 | 7.2944 | 3591.2323 | 7.5256 | 39.6954 | 6.5514 | 247.4302 | 7.6243 | 2389.3163 | 7.5868 | 2366.8127 | 6.5514 | 247.4302 | 7.6243 | 2389.3163 | 7.5868 | 2366.8127 | 6.923 | 234.6715 | 8.0941 | 63.8546 | 6.3578 | 1388.0113 | 7.5819 | 2462.7926 | 6.923 | 234.6715 | 8.0941 | 63.8546 | 6.3578 | 1388.0113 | 7.5819 | 2462.7926
7.9201 | 1440.0369 | 7.2779 | 3671.1693 | 7.5309 | 39.867 | 7.9192 | 1473.011 | 7.2882 | 3637.7347 | 7.5748 | 38.1482 | 7.9202 | 1458.5467 | 7.2944 | 3591.2323 | 7.5256 | 39.6954 | 7.9201 | 1440.0369 | 7.2779 | 3671.1693 | 7.5309 | 39.867 | 7.9192 | 1473.011 | 7.2882 | 3637.7347 | 7.5748 | 38.1482 | 7.9202 | 1458.5467 | 7.2944 | 3591.2323 | 7.5256 | 39.6954 | 6.5514 | 247.4302 | 7.6243 | 2389.3163 | 7.5868 | 2366.8127 | 6.5514 | 247.4302 | 7.6243 | 2389.3163 | 7.5868 | 2366.8127 | 6.923 | 234.6715 | 8.0941 | 63.8546 | 6.3578 | 1388.0113 | 7.5819 | 2462.7926 | 6.923 | 234.6715 | 8.0941 | 63.8546 | 6.3578 | 1388.0113 | 7.5819 | 2462.7926
7.9201 | 1488.0382 | 7.2586 | 3793.5416 | 7.4906 | 41.1959 | 7.9192 | 1522.1114 | 7.2604 | 3758.9925 | 7.5409 | 39.4198 | 7.9202 | 1507.165 | 7.2573 | 3710.94 | 7.4943 | 41.0186 | 7.9201 | 1488.0382 | 7.2586 | 3793.5416 | 7.4906 | 41.1959 | 7.9192 | 1522.1114 | 7.2604 | 3758.9925 | 7.5409 | 39.4198 | 7.9202 | 1507.165 | 7.2573 | 3710.94 | 7.4943 | 41.0186 | 6.4771 | 255.6779 | 7.5832 | 2468.9602 | 7.5451 | 2445.7065 | 6.4771 | 255.6779 | 7.5832 | 2468.9602 | 7.5451 | 2445.7065 | 6.8557 | 242.4939 | 8.0795 | 65.9831 | 6.3397 | 1434.2783 | 7.5451 | 2544.8857 | 6.8557 | 242.4939 | 8.0795 | 65.9831 | 6.3397 | 1434.2783 | 7.5451 | 2544.8857
7.9201 | 1488.0382 | 7.2586 | 3793.5416 | 7.4906 | 41.1959 | 7.9192 | 1522.1114 | 7.2604 | 3758.9925 | 7.5409 | 39.4198 | 7.9202 | 1507.165 | 7.2573 | 3710.94 | 7.4943 | 41.0186 | 7.9201 | 1488.0382 | 7.2586 | 3793.5416 | 7.4906 | 41.1959 | 7.9192 | 1522.1114 | 7.2604 | 3758.9925 | 7.5409 | 39.4198 | 7.9202 | 1507.165 | 7.2573 | 3710.94 | 7.4943 | 41.0186 | 6.4771 | 255.6779 | 7.5832 | 2468.9602 | 7.5451 | 2445.7065 | 6.4771 | 255.6779 | 7.5832 | 2468.9602 | 7.5451 | 2445.7065 | 6.8557 | 242.4939 | 8.0795 | 65.9831 | 6.3397 | 1434.2783 | 7.5451 | 2544.8857 | 6.8557 | 242.4939 | 8.0795 | 65.9831 | 6.3397 | 1434.2783 | 7.5451 | 2544.8857
7.9201 | 1536.0394 | 7.2247 | 3915.9139 | 7.4582 | 42.5248 | 7.9192 | 1571.2118 | 7.2218 | 3880.2503 | 7.5101 | 40.6914 | 7.9202 | 1555.7832 | 7.2292 | 3830.6477 | 7.461 | 42.3418 | 7.9201 | 1536.0394 | 7.2247 | 3915.9139 | 7.4582 | 42.5248 | 7.9192 | 1571.2118 | 7.2218 | 3880.2503 | 7.5101 | 40.6914 | 7.9202 | 1555.7832 | 7.2292 | 3830.6477 | 7.461 | 42.3418 | 6.4347 | 263.9256 | 7.5415 | 2548.604 | 7.4975 | 2524.6002 | 6.4347 | 263.9256 | 7.5415 | 2548.604 | 7.4975 | 2524.6002 | 6.8174 | 250.3162 | 8.0664 | 68.1116 | 6.3165 | 1480.5454 | 7.4963 | 2626.9788 | 6.8174 | 250.3162 | 8.0664 | 68.1116 | 6.3165 | 1480.5454 | 7.4963 | 2626.9788
7.9201 | 1536.0394 | 7.2247 | 3915.9139 | 7.4582 | 42.5248 | 7.9192 | 1571.2118 | 7.2218 | 3880.2503 | 7.5101 | 40.6914 | 7.9202 | 1555.7832 | 7.2292 | 3830.6477 | 7.461 | 42.3418 | 7.9201 | 1536.0394 | 7.2247 | 3915.9139 | 7.4582 | 42.5248 | 7.9192 | 1571.2118 | 7.2218 | 3880.2503 | 7.5101 | 40.6914 | 7.9202 | 1555.7832 | 7.2292 | 3830.6477 | 7.461 | 42.3418 | 6.4347 | 263.9256 | 7.5415 | 2548.604 | 7.4975 | 2524.6002 | 6.4347 | 263.9256 | 7.5415 | 2548.604 | 7.4975 | 2524.6002 | 6.8174 | 250.3162 | 8.0664 | 68.1116 | 6.3165 | 1480.5454 | 7.4963 | 2626.9788 | 6.8174 | 250.3162 | 8.0664 | 68.1116 | 6.3165 | 1480.5454 | 7.4963 | 2626.9788
7.9201 | 1584.0406 | 7.1943 | 4038.2862 | 7.4207 | 43.8537 | 7.9192 | 1620.3121 | 7.1909 | 4001.5082 | 7.4765 | 41.963 | 7.9202 | 1604.4014 | 7.1903 | 3950.3555 | 7.4275 | 43.665 | 7.9201 | 1584.0406 | 7.1943 | 4038.2862 | 7.4207 | 43.8537 | 7.9192 | 1620.3121 | 7.1909 | 4001.5082 | 7.4765 | 41.963 | 7.9202 | 1604.4014 | 7.1903 | 3950.3555 | 7.4275 | 43.665 | 6.4 | 272.1732 | 7.5007 | 2628.2479 | 7.4646 | 2603.494 | 6.4 | 272.1732 | 7.5007 | 2628.2479 | 7.4646 | 2603.494 | 6.7856 | 258.1386 | 8.0521 | 70.2401 | 6.2912 | 1526.8124 | 7.4566 | 2709.0719 | 6.7856 | 258.1386 | 8.0521 | 70.2401 | 6.2912 | 1526.8124 | 7.4566 | 2709.0719
7.9201 | 1584.0406 | 7.1943 | 4038.2862 | 7.4207 | 43.8537 | 7.9192 | 1620.3121 | 7.1909 | 4001.5082 | 7.4765 | 41.963 | 7.9202 | 1604.4014 | 7.1903 | 3950.3555 | 7.4275 | 43.665 | 7.9201 | 1584.0406 | 7.1943 | 4038.2862 | 7.4207 | 43.8537 | 7.9192 | 1620.3121 | 7.1909 | 4001.5082 | 7.4765 | 41.963 | 7.9202 | 1604.4014 | 7.1903 | 3950.3555 | 7.4275 | 43.665 | 6.4 | 272.1732 | 7.5007 | 2628.2479 | 7.4646 | 2603.494 | 6.4 | 272.1732 | 7.5007 | 2628.2479 | 7.4646 | 2603.494 | 6.7856 | 258.1386 | 8.0521 | 70.2401 | 6.2912 | 1526.8124 | 7.4566 | 2709.0719 | 6.7856 | 258.1386 | 8.0521 | 70.2401 | 6.2912 | 1526.8124 | 7.4566 | 2709.0719
7.9201 | 1632.0419 | 7.1612 | 4160.6585 | 7.3833 | 45.1825 | 7.9192 | 1669.4125 | 7.1623 | 4122.766 | 7.4414 | 43.2346 | 7.9201 | 1653.0196 | 7.1591 | 4070.0632 | 7.3863 | 44.9882 | 7.9201 | 1632.0419 | 7.1612 | 4160.6585 | 7.3833 | 45.1825 | 7.9192 | 1669.4125 | 7.1623 | 4122.766 | 7.4414 | 43.2346 | 7.9201 | 1653.0196 | 7.1591 | 4070.0632 | 7.3863 | 44.9882 | 6.3451 | 280.4209 | 7.458 | 2707.8918 | 7.4322 | 2682.3878 | 6.3451 | 280.4209 | 7.458 | 2707.8918 | 7.4322 | 2682.3878 | 6.7381 | 265.961 | 8.0402 | 72.3686 | 6.2433 | 1573.0795 | 7.4052 | 2791.165 | 6.7381 | 265.961 | 8.0402 | 72.3686 | 6.2433 | 1573.0795 | 7.4052 | 2791.165
7.9201 | 1632.0419 | 7.1612 | 4160.6585 | 7.3833 | 45.1825 | 7.9192 | 1669.4125 | 7.1623 | 4122.766 | 7.4414 | 43.2346 | 7.9201 | 1653.0196 | 7.1591 | 4070.0632 | 7.3863 | 44.9882 | 7.9201 | 1632.0419 | 7.1612 | 4160.6585 | 7.3833 | 45.1825 | 7.9192 | 1669.4125 | 7.1623 | 4122.766 | 7.4414 | 43.2346 | 7.9201 | 1653.0196 | 7.1591 | 4070.0632 | 7.3863 | 44.9882 | 6.3451 | 280.4209 | 7.458 | 2707.8918 | 7.4322 | 2682.3878 | 6.3451 | 280.4209 | 7.458 | 2707.8918 | 7.4322 | 2682.3878 | 6.7381 | 265.961 | 8.0402 | 72.3686 | 6.2433 | 1573.0795 | 7.4052 | 2791.165 | 6.7381 | 265.961 | 8.0402 | 72.3686 | 6.2433 | 1573.0795 | 7.4052 | 2791.165
7.9201 | 1680.0431 | 7.1265 | 4283.0308 | 7.3518 | 46.5114 | 7.9192 | 1718.5129 | 7.1297 | 4244.0238 | 7.4117 | 44.5062 | 7.9201 | 1701.6379 | 7.1365 | 4189.771 | 7.3535 | 46.3113 | 7.9201 | 1680.0431 | 7.1265 | 4283.0308 | 7.3518 | 46.5114 | 7.9192 | 1718.5129 | 7.1297 | 4244.0238 | 7.4117 | 44.5062 | 7.9201 | 1701.6379 | 7.1365 | 4189.771 | 7.3535 | 46.3113 | 6.3031 | 288.6686 | 7.418 | 2787.5357 | 7.3924 | 2761.2815 | 6.3031 | 288.6686 | 7.418 | 2787.5357 | 7.3924 | 2761.2815 | 6.7048 | 273.7834 | 8.0257 | 74.4971 | 6.1781 | 1619.3465 | 7.3664 | 2873.2581 | 6.7048 | 273.7834 | 8.0257 | 74.4971 | 6.1781 | 1619.3465 | 7.3664 | 2873.2581
7.9201 | 1680.0431 | 7.1265 | 4283.0308 | 7.3518 | 46.5114 | 7.9192 | 1718.5129 | 7.1297 | 4244.0238 | 7.4117 | 44.5062 | 7.9201 | 1701.6379 | 7.1365 | 4189.771 | 7.3535 | 46.3113 | 7.9201 | 1680.0431 | 7.1265 | 4283.0308 | 7.3518 | 46.5114 | 7.9192 | 1718.5129 | 7.1297 | 4244.0238 | 7.4117 | 44.5062 | 7.9201 | 1701.6379 | 7.1365 | 4189.771 | 7.3535 | 46.3113 | 6.3031 | 288.6686 | 7.418 | 2787.5357 | 7.3924 | 2761.2815 | 6.3031 | 288.6686 | 7.418 | 2787.5357 | 7.3924 | 2761.2815 | 6.7048 | 273.7834 | 8.0257 | 74.4971 | 6.1781 | 1619.3465 | 7.3664 | 2873.2581 | 6.7048 | 273.7834 | 8.0257 | 74.4971 | 6.1781 | 1619.3465 | 7.3664 | 2873.2581
7.9201 | 1728.0443 | 7.1023 | 4405.4031 | 7.3171 | 47.8403 | 7.9192 | 1767.6132 | 7.1017 | 4365.2816 | 7.3795 | 45.7778 | 7.92 | 1750.2561 | 7.1064 | 4309.4787 | 7.3253 | 47.6345 | 7.9201 | 1728.0443 | 7.1023 | 4405.4031 | 7.3171 | 47.8403 | 7.9192 | 1767.6132 | 7.1017 | 4365.2816 | 7.3795 | 45.7778 | 7.92 | 1750.2561 | 7.1064 | 4309.4787 | 7.3253 | 47.6345 | 6.2728 | 296.9163 | 7.371 | 2867.1795 | 7.3602 | 2840.1753 | 6.2728 | 296.9163 | 7.371 | 2867.1795 | 7.3602 | 2840.1753 | 6.6301 | 281.6058 | 8.011 | 76.6256 | 6.1471 | 1665.6136 | 7.3221 | 2955.3512 | 6.6301 | 281.6058 | 8.011 | 76.6256 | 6.1471 | 1665.6136 | 7.3221 | 2955.3512
7.9201 | 1728.0443 | 7.1023 | 4405.4031 | 7.3171 | 47.8403 | 7.9192 | 1767.6132 | 7.1017 | 4365.2816 | 7.3795 | 45.7778 | 7.92 | 1750.2561 | 7.1064 | 4309.4787 | 7.3253 | 47.6345 | 7.9201 | 1728.0443 | 7.1023 | 4405.4031 | 7.3171 | 47.8403 | 7.9192 | 1767.6132 | 7.1017 | 4365.2816 | 7.3795 | 45.7778 | 7.92 | 1750.2561 | 7.1064 | 4309.4787 | 7.3253 | 47.6345 | 6.2728 | 296.9163 | 7.371 | 2867.1795 | 7.3602 | 2840.1753 | 6.2728 | 296.9163 | 7.371 | 2867.1795 | 7.3602 | 2840.1753 | 6.6301 | 281.6058 | 8.011 | 76.6256 | 6.1471 | 1665.6136 | 7.3221 | 2955.3512 | 6.6301 | 281.6058 | 8.011 | 76.6256 | 6.1471 | 1665.6136 | 7.3221 | 2955.3512
7.92 | 1776.0456 | 7.0694 | 4527.7754 | 7.2719 | 49.1692 | 7.9192 | 1816.7136 | 7.0589 | 4486.5395 | 7.3436 | 47.0494 | 7.9199 | 1798.8743 | 7.0806 | 4429.1865 | 7.2835 | 48.9577 | 7.92 | 1776.0456 | 7.0694 | 4527.7754 | 7.2719 | 49.1692 | 7.9192 | 1816.7136 | 7.0589 | 4486.5395 | 7.3436 | 47.0494 | 7.9199 | 1798.8743 | 7.0806 | 4429.1865 | 7.2835 | 48.9577 | 6.2407 | 305.1639 | 7.3273 | 2946.8234 | 7.3196 | 2919.069 | 6.2407 | 305.1639 | 7.3273 | 2946.8234 | 7.3196 | 2919.069 | 6.5814 | 289.4282 | 7.9974 | 78.7541 | 6.1035 | 1711.8806 | 7.2855 | 3037.4442 | 6.5814 | 289.4282 | 7.9974 | 78.7541 | 6.1035 | 1711.8806 | 7.2855 | 3037.4442
7.92 | 1776.0456 | 7.0694 | 4527.7754 | 7.2719 | 49.1692 | 7.9192 | 1816.7136 | 7.0589 | 4486.5395 | 7.3436 | 47.0494 | 7.9199 | 1798.8743 | 7.0806 | 4429.1865 | 7.2835 | 48.9577 | 7.92 | 1776.0456 | 7.0694 | 4527.7754 | 7.2719 | 49.1692 | 7.9192 | 1816.7136 | 7.0589 | 4486.5395 | 7.3436 | 47.0494 | 7.9199 | 1798.8743 | 7.0806 | 4429.1865 | 7.2835 | 48.9577 | 6.2407 | 305.1639 | 7.3273 | 2946.8234 | 7.3196 | 2919.069 | 6.2407 | 305.1639 | 7.3273 | 2946.8234 | 7.3196 | 2919.069 | 6.5814 | 289.4282 | 7.9974 | 78.7541 | 6.1035 | 1711.8806 | 7.2855 | 3037.4442 | 6.5814 | 289.4282 | 7.9974 | 78.7541 | 6.1035 | 1711.8806 | 7.2855 | 3037.4442
7.9199 | 1824.0468 | 7.0382 | 4650.1477 | 7.2374 | 50.4981 | 7.9192 | 1865.814 | 7.0241 | 4607.7973 | 7.3151 | 48.321 | 7.9199 | 1847.4925 | 7.0555 | 4548.8942 | 7.2427 | 50.2809 | 7.9199 | 1824.0468 | 7.0382 | 4650.1477 | 7.2374 | 50.4981 | 7.9192 | 1865.814 | 7.0241 | 4607.7973 | 7.3151 | 48.321 | 7.9199 | 1847.4925 | 7.0555 | 4548.8942 | 7.2427 | 50.2809 | 6.193 | 313.4116 | 7.2897 | 3026.4673 | 7.2786 | 2997.9628 | 6.193 | 313.4116 | 7.2897 | 3026.4673 | 7.2786 | 2997.9628 | 6.5381 | 297.2505 | 7.9845 | 80.8825 | 6.0804 | 1758.1476 | 7.2533 | 3119.5373 | 6.5381 | 297.2505 | 7.9845 | 80.8825 | 6.0804 | 1758.1476 | 7.2533 | 3119.5373
7.9199 | 1824.0468 | 7.0382 | 4650.1477 | 7.2374 | 50.4981 | 7.9192 | 1865.814 | 7.0241 | 4607.7973 | 7.3151 | 48.321 | 7.9199 | 1847.4925 | 7.0555 | 4548.8942 | 7.2427 | 50.2809 | 7.9199 | 1824.0468 | 7.0382 | 4650.1477 | 7.2374 | 50.4981 | 7.9192 | 1865.814 | 7.0241 | 4607.7973 | 7.3151 | 48.321 | 7.9199 | 1847.4925 | 7.0555 | 4548.8942 | 7.2427 | 50.2809 | 6.193 | 313.4116 | 7.2897 | 3026.4673 | 7.2786 | 2997.9628 | 6.193 | 313.4116 | 7.2897 | 3026.4673 | 7.2786 | 2997.9628 | 6.5381 | 297.2505 | 7.9845 | 80.8825 | 6.0804 | 1758.1476 | 7.2533 | 3119.5373 | 6.5381 | 297.2505 | 7.9845 | 80.8825 | 6.0804 | 1758.1476 | 7.2533 | 3119.5373
7.9199 | 1872.048 | 7.0097 | 4772.5201 | 7.1963 | 51.827 | 7.9192 | 1914.9143 | 7.0011 | 4729.0551 | 7.2805 | 49.5926 | 7.9199 | 1896.1108 | 7.0321 | 4668.6019 | 7.2048 | 51.6041 | 7.9199 | 1872.048 | 7.0097 | 4772.5201 | 7.1963 | 51.827 | 7.9192 | 1914.9143 | 7.0011 | 4729.0551 | 7.2805 | 49.5926 | 7.9199 | 1896.1108 | 7.0321 | 4668.6019 | 7.2048 | 51.6041 | 6.152 | 321.6593 | 7.2539 | 3106.1112 | 7.2385 | 3076.8566 | 6.152 | 321.6593 | 7.2539 | 3106.1112 | 7.2385 | 3076.8566 | 6.49 | 305.0729 | 7.9682 | 83.011 | 6.0683 | 1804.4147 | 7.2112 | 3201.6304 | 6.49 | 305.0729 | 7.9682 | 83.011 | 6.0683 | 1804.4147 | 7.2112 | 3201.6304
7.9199 | 1872.048 | 7.0097 | 4772.5201 | 7.1963 | 51.827 | 7.9192 | 1914.9143 | 7.0011 | 4729.0551 | 7.2805 | 49.5926 | 7.9199 | 1896.1108 | 7.0321 | 4668.6019 | 7.2048 | 51.6041 | 7.9199 | 1872.048 | 7.0097 | 4772.5201 | 7.1963 | 51.827 | 7.9192 | 1914.9143 | 7.0011 | 4729.0551 | 7.2805 | 49.5926 | 7.9199 | 1896.1108 | 7.0321 | 4668.6019 | 7.2048 | 51.6041 | 6.152 | 321.6593 | 7.2539 | 3106.1112 | 7.2385 | 3076.8566 | 6.152 | 321.6593 | 7.2539 | 3106.1112 | 7.2385 | 3076.8566 | 6.49 | 305.0729 | 7.9682 | 83.011 | 6.0683 | 1804.4147 | 7.2112 | 3201.6304 | 6.49 | 305.0729 | 7.9682 | 83.011 | 6.0683 | 1804.4147 | 7.2112 | 3201.6304
7.9199 | 1920.0492 | 6.9743 | 4894.8924 | 7.1523 | 53.1559 | 7.9192 | 1964.0147 | 6.9777 | 4850.3129 | 7.2332 | 50.8642 | 7.9197 | 1944.729 | 6.9939 | 4788.3097 | 7.1726 | 52.9272 | 7.9199 | 1920.0492 | 6.9743 | 4894.8924 | 7.1523 | 53.1559 | 7.9192 | 1964.0147 | 6.9777 | 4850.3129 | 7.2332 | 50.8642 | 7.9197 | 1944.729 | 6.9939 | 4788.3097 | 7.1726 | 52.9272 | 6.1303 | 329.9069 | 7.2107 | 3185.755 | 7.2079 | 3155.7503 | 6.1303 | 329.9069 | 7.2107 | 3185.755 | 7.2079 | 3155.7503 | 6.4431 | 312.8953 | 7.9522 | 85.1395 | 6.037 | 1850.6817 | 7.1718 | 3283.7235 | 6.4431 | 312.8953 | 7.9522 | 85.1395 | 6.037 | 1850.6817 | 7.1718 | 3283.7235
7.9199 | 1920.0492 | 6.9743 | 4894.8924 | 7.1523 | 53.1559 | 7.9192 | 1964.0147 | 6.9777 | 4850.3129 | 7.2332 | 50.8642 | 7.9197 | 1944.729 | 6.9939 | 4788.3097 | 7.1726 | 52.9272 | 7.9199 | 1920.0492 | 6.9743 | 4894.8924 | 7.1523 | 53.1559 | 7.9192 | 1964.0147 | 6.9777 | 4850.3129 | 7.2332 | 50.8642 | 7.9197 | 1944.729 | 6.9939 | 4788.3097 | 7.1726 | 52.9272 | 6.1303 | 329.9069 | 7.2107 | 3185.755 | 7.2079 | 3155.7503 | 6.1303 | 329.9069 | 7.2107 | 3185.755 | 7.2079 | 3155.7503 | 6.4431 | 312.8953 | 7.9522 | 85.1395 | 6.037 | 1850.6817 | 7.1718 | 3283.7235 | 6.4431 | 312.8953 | 7.9522 | 85.1395 | 6.037 | 1850.6817 | 7.1718 | 3283.7235
7.9197 | 1968.0505 | 6.9401 | 5017.2647 | 7.078 | 54.4848 | 7.9192 | 2013.1151 | 6.9435 | 4971.5707 | 7.1925 | 52.1358 | 7.9197 | 1993.3472 | 6.9668 | 4908.0174 | 7.128 | 54.2504 | 7.9197 | 1968.0505 | 6.9401 | 5017.2647 | 7.078 | 54.4848 | 7.9192 | 2013.1151 | 6.9435 | 4971.5707 | 7.1925 | 52.1358 | 7.9197 | 1993.3472 | 6.9668 | 4908.0174 | 7.128 | 54.2504 | 6.0793 | 338.1546 | 7.1761 | 3265.3989 | 7.1684 | 3234.6441 | 6.0793 | 338.1546 | 7.1761 | 3265.3989 | 7.1684 | 3234.6441 | 6.3933 | 320.7177 | 7.9353 | 87.268 | 6.0077 | 1896.9488 | 7.133 | 3365.8166 | 6.3933 | 320.7177 | 7.9353 | 87.268 | 6.0077 | 1896.9488 | 7.133 | 3365.8166
7.9197 | 1968.0505 | 6.9401 | 5017.2647 | 7.078 | 54.4848 | 7.9192 | 2013.1151 | 6.9435 | 4971.5707 | 7.1925 | 52.1358 | 7.9197 | 1993.3472 | 6.9668 | 4908.0174 | 7.128 | 54.2504 | 7.9197 | 1968.0505 | 6.9401 | 5017.2647 | 7.078 | 54.4848 | 7.9192 | 2013.1151 | 6.9435 | 4971.5707 | 7.1925 | 52.1358 | 7.9197 | 1993.3472 | 6.9668 | 4908.0174 | 7.128 | 54.2504 | 6.0793 | 338.1546 | 7.1761 | 3265.3989 | 7.1684 | 3234.6441 | 6.0793 | 338.1546 | 7.1761 | 3265.3989 | 7.1684 | 3234.6441 | 6.3933 | 320.7177 | 7.9353 | 87.268 | 6.0077 | 1896.9488 | 7.133 | 3365.8166 | 6.3933 | 320.7177 | 7.9353 | 87.268 | 6.0077 | 1896.9488 | 7.133 | 3365.8166
7.9197 | 2016.0517 | 6.9 | 5139.637 | 7.0048 | 55.8137 | 7.9192 | 2062.2154 | 6.9151 | 5092.8286 | 7.1397 | 53.4074 | 7.9197 | 2041.9654 | 6.9345 | 5027.7252 | 7.0455 | 55.5736 | 7.9197 | 2016.0517 | 6.9 | 5139.637 | 7.0048 | 55.8137 | 7.9192 | 2062.2154 | 6.9151 | 5092.8286 | 7.1397 | 53.4074 | 7.9197 | 2041.9654 | 6.9345 | 5027.7252 | 7.0455 | 55.5736 | 6.0569 | 346.4023 | 7.1422 | 3345.0428 | 7.1389 | 3313.5378 | 6.0569 | 346.4023 | 7.1422 | 3345.0428 | 7.1389 | 3313.5378 | 6.3564 | 328.5401 | 7.9216 | 89.3965 | 5.9321 | 1943.2158 | 7.0926 | 3447.9097 | 6.3564 | 328.5401 | 7.9216 | 89.3965 | 5.9321 | 1943.2158 | 7.0926 | 3447.9097
7.9197 | 2016.0517 | 6.9 | 5139.637 | 7.0048 | 55.8137 | 7.9192 | 2062.2154 | 6.9151 | 5092.8286 | 7.1397 | 53.4074 | 7.9197 | 2041.9654 | 6.9345 | 5027.7252 | 7.0455 | 55.5736 | 7.9197 | 2016.0517 | 6.9 | 5139.637 | 7.0048 | 55.8137 | 7.9192 | 2062.2154 | 6.9151 | 5092.8286 | 7.1397 | 53.4074 | 7.9197 | 2041.9654 | 6.9345 | 5027.7252 | 7.0455 | 55.5736 | 6.0569 | 346.4023 | 7.1422 | 3345.0428 | 7.1389 | 3313.5378 | 6.0569 | 346.4023 | 7.1422 | 3345.0428 | 7.1389 | 3313.5378 | 6.3564 | 328.5401 | 7.9216 | 89.3965 | 5.9321 | 1943.2158 | 7.0926 | 3447.9097 | 6.3564 | 328.5401 | 7.9216 | 89.3965 | 5.9321 | 1943.2158 | 7.0926 | 3447.9097
7.9196 | 2064.0529 | 6.8753 | 5262.0093 | 6.9404 | 57.1426 | 7.9192 | 2111.3158 | 6.8738 | 5214.0864 | 7.0948 | 54.679 | 7.9197 | 2090.5837 | 6.905 | 5147.4329 | 6.9643 | 56.8968 | 7.9196 | 2064.0529 | 6.8753 | 5262.0093 | 6.9404 | 57.1426 | 7.9192 | 2111.3158 | 6.8738 | 5214.0864 | 7.0948 | 54.679 | 7.9197 | 2090.5837 | 6.905 | 5147.4329 | 6.9643 | 56.8968 | 6.0441 | 354.65 | 7.107 | 3424.6867 | 7.1022 | 3392.4316 | 6.0441 | 354.65 | 7.107 | 3424.6867 | 7.1022 | 3392.4316 | 6.3165 | 336.3625 | 7.9063 | 91.525 | 5.9181 | 1989.4829 | 7.0458 | 3530.0028 | 6.3165 | 336.3625 | 7.9063 | 91.525 | 5.9181 | 1989.4829 | 7.0458 | 3530.0028
7.9196 | 2064.0529 | 6.8753 | 5262.0093 | 6.9404 | 57.1426 | 7.9192 | 2111.3158 | 6.8738 | 5214.0864 | 7.0948 | 54.679 | 7.9197 | 2090.5837 | 6.905 | 5147.4329 | 6.9643 | 56.8968 | 7.9196 | 2064.0529 | 6.8753 | 5262.0093 | 6.9404 | 57.1426 | 7.9192 | 2111.3158 | 6.8738 | 5214.0864 | 7.0948 | 54.679 | 7.9197 | 2090.5837 | 6.905 | 5147.4329 | 6.9643 | 56.8968 | 6.0441 | 354.65 | 7.107 | 3424.6867 | 7.1022 | 3392.4316 | 6.0441 | 354.65 | 7.107 | 3424.6867 | 7.1022 | 3392.4316 | 6.3165 | 336.3625 | 7.9063 | 91.525 | 5.9181 | 1989.4829 | 7.0458 | 3530.0028 | 6.3165 | 336.3625 | 7.9063 | 91.525 | 5.9181 | 1989.4829 | 7.0458 | 3530.0028
7.9196 | 2112.0542 | 6.8367 | 5384.3816 | 6.8781 | 58.4715 | 7.9192 | 2160.4162 | 6.8492 | 5335.3442 | 7.0268 | 55.9506 | 7.9195 | 2139.2019 | 6.881 | 5267.1406 | 6.8866 | 58.22 | 7.9196 | 2112.0542 | 6.8367 | 5384.3816 | 6.8781 | 58.4715 | 7.9192 | 2160.4162 | 6.8492 | 5335.3442 | 7.0268 | 55.9506 | 7.9195 | 2139.2019 | 6.881 | 5267.1406 | 6.8866 | 58.22 | 6.0283 | 362.8976 | 7.0654 | 3504.3305 | 7.0758 | 3471.3253 | 6.0283 | 362.8976 | 7.0654 | 3504.3305 | 7.0758 | 3471.3253 | 6.2777 | 344.1848 | 7.8896 | 93.6535 | 5.8298 | 2035.7499 | 7.0179 | 3612.0959 | 6.2777 | 344.1848 | 7.8896 | 93.6535 | 5.8298 | 2035.7499 | 7.0179 | 3612.0959
7.9196 | 2112.0542 | 6.8367 | 5384.3816 | 6.8781 | 58.4715 | 7.9192 | 2160.4162 | 6.8492 | 5335.3442 | 7.0268 | 55.9506 | 7.9195 | 2139.2019 | 6.881 | 5267.1406 | 6.8866 | 58.22 | 7.9196 | 2112.0542 | 6.8367 | 5384.3816 | 6.8781 | 58.4715 | 7.9192 | 2160.4162 | 6.8492 | 5335.3442 | 7.0268 | 55.9506 | 7.9195 | 2139.2019 | 6.881 | 5267.1406 | 6.8866 | 58.22 | 6.0283 | 362.8976 | 7.0654 | 3504.3305 | 7.0758 | 3471.3253 | 6.0283 | 362.8976 | 7.0654 | 3504.3305 | 7.0758 | 3471.3253 | 6.2777 | 344.1848 | 7.8896 | 93.6535 | 5.8298 | 2035.7499 | 7.0179 | 3612.0959 | 6.2777 | 344.1848 | 7.8896 | 93.6535 | 5.8298 | 2035.7499 | 7.0179 | 3612.0959
7.9196 | 2160.0554 | 6.8011 | 5506.7539 | 6.8113 | 59.8004 | 7.9192 | 2209.5166 | 6.8042 | 5456.602 | 6.9752 | 57.2222 | 7.9195 | 2187.8201 | 6.8435 | 5386.8484 | 6.7942 | 59.5431 | 7.9196 | 2160.0554 | 6.8011 | 5506.7539 | 6.8113 | 59.8004 | 7.9192 | 2209.5166 | 6.8042 | 5456.602 | 6.9752 | 57.2222 | 7.9195 | 2187.8201 | 6.8435 | 5386.8484 | 6.7942 | 59.5431 | 5.9871 | 371.1453 | 7.0297 | 3583.9744 | 7.0335 | 3550.2191 | 5.9871 | 371.1453 | 7.0297 | 3583.9744 | 7.0335 | 3550.2191 | 6.2383 | 352.0072 | 7.868 | 95.782 | 5.8298 | 2082.0169 | 6.9683 | 3694.189 | 6.2383 | 352.0072 | 7.868 | 95.782 | 5.8298 | 2082.0169 | 6.9683 | 3694.189
7.9196 | 2160.0554 | 6.8011 | 5506.7539 | 6.8113 | 59.8004 | 7.9192 | 2209.5166 | 6.8042 | 5456.602 | 6.9752 | 57.2222 | 7.9195 | 2187.8201 | 6.8435 | 5386.8484 | 6.7942 | 59.5431 | 7.9196 | 2160.0554 | 6.8011 | 5506.7539 | 6.8113 | 59.8004 | 7.9192 | 2209.5166 | 6.8042 | 5456.602 | 6.9752 | 57.2222 | 7.9195 | 2187.8201 | 6.8435 | 5386.8484 | 6.7942 | 59.5431 | 5.9871 | 371.1453 | 7.0297 | 3583.9744 | 7.0335 | 3550.2191 | 5.9871 | 371.1453 | 7.0297 | 3583.9744 | 7.0335 | 3550.2191 | 6.2383 | 352.0072 | 7.868 | 95.782 | 5.8298 | 2082.0169 | 6.9683 | 3694.189 | 6.2383 | 352.0072 | 7.868 | 95.782 | 5.8298 | 2082.0169 | 6.9683 | 3694.189
7.9196 | 2208.0566 | 6.7644 | 5629.1262 | 6.7226 | 61.1293 | 7.9192 | 2258.6169 | 6.7677 | 5577.8599 | 6.8713 | 58.4938 | 7.9195 | 2236.4383 | 6.8159 | 5506.5561 | 6.7334 | 60.8663 | 7.9196 | 2208.0566 | 6.7644 | 5629.1262 | 6.7226 | 61.1293 | 7.9192 | 2258.6169 | 6.7677 | 5577.8599 | 6.8713 | 58.4938 | 7.9195 | 2236.4383 | 6.8159 | 5506.5561 | 6.7334 | 60.8663 | 5.9786 | 379.393 | 6.9912 | 3663.6183 | 6.9936 | 3629.1129 | 5.9786 | 379.393 | 6.9912 | 3663.6183 | 6.9936 | 3629.1129 | 6.2038 | 359.8296 | 7.8502 | 97.9105 | 5.8175 | 2128.284 | 6.9241 | 3776.282 | 6.2038 | 359.8296 | 7.8502 | 97.9105 | 5.8175 | 2128.284 | 6.9241 | 3776.282
7.9196 | 2208.0566 | 6.7644 | 5629.1262 | 6.7226 | 61.1293 | 7.9192 | 2258.6169 | 6.7677 | 5577.8599 | 6.8713 | 58.4938 | 7.9195 | 2236.4383 | 6.8159 | 5506.5561 | 6.7334 | 60.8663 | 7.9196 | 2208.0566 | 6.7644 | 5629.1262 | 6.7226 | 61.1293 | 7.9192 | 2258.6169 | 6.7677 | 5577.8599 | 6.8713 | 58.4938 | 7.9195 | 2236.4383 | 6.8159 | 5506.5561 | 6.7334 | 60.8663 | 5.9786 | 379.393 | 6.9912 | 3663.6183 | 6.9936 | 3629.1129 | 5.9786 | 379.393 | 6.9912 | 3663.6183 | 6.9936 | 3629.1129 | 6.2038 | 359.8296 | 7.8502 | 97.9105 | 5.8175 | 2128.284 | 6.9241 | 3776.282 | 6.2038 | 359.8296 | 7.8502 | 97.9105 | 5.8175 | 2128.284 | 6.9241 | 3776.282
7.9194 | 2256.0579 | 6.7219 | 5751.4985 | 6.6298 | 62.4582 | 7.9192 | 2307.7173 | 6.7413 | 5699.1177 | 6.8007 | 59.7654 | 7.9193 | 2285.0566 | 6.7699 | 5626.2639 | 6.6523 | 62.1895 | 7.9194 | 2256.0579 | 6.7219 | 5751.4985 | 6.6298 | 62.4582 | 7.9192 | 2307.7173 | 6.7413 | 5699.1177 | 6.8007 | 59.7654 | 7.9193 | 2285.0566 | 6.7699 | 5626.2639 | 6.6523 | 62.1895 | 5.9484 | 387.6407 | 6.951 | 3743.2622 | 6.9657 | 3708.0066 | 5.9484 | 387.6407 | 6.951 | 3743.2622 | 6.9657 | 3708.0066 | 6.1796 | 367.652 | 7.8288 | 100.0389 | 5.7556 | 2174.551 | 6.8913 | 3858.3751 | 6.1796 | 367.652 | 7.8288 | 100.0389 | 5.7556 | 2174.551 | 6.8913 | 3858.3751
7.9194 | 2256.0579 | 6.7219 | 5751.4985 | 6.6298 | 62.4582 | 7.9192 | 2307.7173 | 6.7413 | 5699.1177 | 6.8007 | 59.7654 | 7.9193 | 2285.0566 | 6.7699 | 5626.2639 | 6.6523 | 62.1895 | 7.9194 | 2256.0579 | 6.7219 | 5751.4985 | 6.6298 | 62.4582 | 7.9192 | 2307.7173 | 6.7413 | 5699.1177 | 6.8007 | 59.7654 | 7.9193 | 2285.0566 | 6.7699 | 5626.2639 | 6.6523 | 62.1895 | 5.9484 | 387.6407 | 6.951 | 3743.2622 | 6.9657 | 3708.0066 | 5.9484 | 387.6407 | 6.951 | 3743.2622 | 6.9657 | 3708.0066 | 6.1796 | 367.652 | 7.8288 | 100.0389 | 5.7556 | 2174.551 | 6.8913 | 3858.3751 | 6.1796 | 367.652 | 7.8288 | 100.0389 | 5.7556 | 2174.551 | 6.8913 | 3858.3751
7.9194 | 2304.0591 | 6.6973 | 5873.8708 | 6.5258 | 63.7871 | 7.9192 | 2356.8177 | 6.718 | 5820.3755 | 6.7185 | 61.037 | 7.9193 | 2333.6748 | 6.7393 | 5745.9716 | 6.5822 | 63.5127 | 7.9194 | 2304.0591 | 6.6973 | 5873.8708 | 6.5258 | 63.7871 | 7.9192 | 2356.8177 | 6.718 | 5820.3755 | 6.7185 | 61.037 | 7.9193 | 2333.6748 | 6.7393 | 5745.9716 | 6.5822 | 63.5127 | 5.8894 | 395.8883 | 6.912 | 3822.906 | 6.9257 | 3786.9004 | 5.8894 | 395.8883 | 6.912 | 3822.906 | 6.9257 | 3786.9004 | 6.1604 | 375.4744 | 7.8119 | 102.1674 | 5.7203 | 2220.8181 | 6.8631 | 3940.4682 | 6.1604 | 375.4744 | 7.8119 | 102.1674 | 5.7203 | 2220.8181 | 6.8631 | 3940.4682
7.9194 | 2304.0591 | 6.6973 | 5873.8708 | 6.5258 | 63.7871 | 7.9192 | 2356.8177 | 6.718 | 5820.3755 | 6.7185 | 61.037 | 7.9193 | 2333.6748 | 6.7393 | 5745.9716 | 6.5822 | 63.5127 | 7.9194 | 2304.0591 | 6.6973 | 5873.8708 | 6.5258 | 63.7871 | 7.9192 | 2356.8177 | 6.718 | 5820.3755 | 6.7185 | 61.037 | 7.9193 | 2333.6748 | 6.7393 | 5745.9716 | 6.5822 | 63.5127 | 5.8894 | 395.8883 | 6.912 | 3822.906 | 6.9257 | 3786.9004 | 5.8894 | 395.8883 | 6.912 | 3822.906 | 6.9257 | 3786.9004 | 6.1604 | 375.4744 | 7.8119 | 102.1674 | 5.7203 | 2220.8181 | 6.8631 | 3940.4682 | 6.1604 | 375.4744 | 7.8119 | 102.1674 | 5.7203 | 2220.8181 | 6.8631 | 3940.4682
7.9194 | 2352.0603 | 6.6744 | 5996.2431 | 6.4465 | 65.116 | 7.9192 | 2405.918 | 6.6675 | 5941.6333 | 6.6163 | 62.3087 | 7.9193 | 2382.293 | 6.7058 | 5865.6794 | 6.4788 | 64.8359 | 7.9194 | 2352.0603 | 6.6744 | 5996.2431 | 6.4465 | 65.116 | 7.9192 | 2405.918 | 6.6675 | 5941.6333 | 6.6163 | 62.3087 | 7.9193 | 2382.293 | 6.7058 | 5865.6794 | 6.4788 | 64.8359 | 5.8445 | 404.136 | 6.8768 | 3902.5499 | 6.8898 | 3865.7941 | 5.8445 | 404.136 | 6.8768 | 3902.5499 | 6.8898 | 3865.7941 | 6.102 | 383.2968 | 7.7887 | 104.2959 | 5.7203 | 2267.0851 | 6.828 | 4022.5613 | 6.102 | 383.2968 | 7.7887 | 104.2959 | 5.7203 | 2267.0851 | 6.828 | 4022.5613
7.9194 | 2352.0603 | 6.6744 | 5996.2431 | 6.4465 | 65.116 | 7.9192 | 2405.918 | 6.6675 | 5941.6333 | 6.6163 | 62.3087 | 7.9193 | 2382.293 | 6.7058 | 5865.6794 | 6.4788 | 64.8359 | 7.9194 | 2352.0603 | 6.6744 | 5996.2431 | 6.4465 | 65.116 | 7.9192 | 2405.918 | 6.6675 | 5941.6333 | 6.6163 | 62.3087 | 7.9193 | 2382.293 | 6.7058 | 5865.6794 | 6.4788 | 64.8359 | 5.8445 | 404.136 | 6.8768 | 3902.5499 | 6.8898 | 3865.7941 | 5.8445 | 404.136 | 6.8768 | 3902.5499 | 6.8898 | 3865.7941 | 6.102 | 383.2968 | 7.7887 | 104.2959 | 5.7203 | 2267.0851 | 6.828 | 4022.5613 | 6.102 | 383.2968 | 7.7887 | 104.2959 | 5.7203 | 2267.0851 | 6.828 | 4022.5613
7.9194 | 2400.0616 | 6.6454 | 6118.6155 | 6.3685 | 66.4449 | 7.9192 | 2455.0184 | 6.6423 | 6062.8912 | 6.5565 | 63.5803 | 7.9192 | 2430.9112 | 6.6835 | 5985.3871 | 6.3916 | 66.1591 | 7.9194 | 2400.0616 | 6.6454 | 6118.6155 | 6.3685 | 66.4449 | 7.9192 | 2455.0184 | 6.6423 | 6062.8912 | 6.5565 | 63.5803 | 7.9192 | 2430.9112 | 6.6835 | 5985.3871 | 6.3916 | 66.1591 | 5.8334 | 412.3837 | 6.8303 | 3982.1938 | 6.8443 | 3944.6879 | 5.8334 | 412.3837 | 6.8303 | 3982.1938 | 6.8443 | 3944.6879 | 6.0528 | 391.1191 | 7.7707 | 106.4244 | 5.675 | 2313.3522 | 6.8036 | 4104.6544 | 6.0528 | 391.1191 | 7.7707 | 106.4244 | 5.675 | 2313.3522 | 6.8036 | 4104.6544
7.9194 | 2400.0616 | 6.6454 | 6118.6155 | 6.3685 | 66.4449 | 7.9192 | 2455.0184 | 6.6423 | 6062.8912 | 6.5565 | 63.5803 | 7.9192 | 2430.9112 | 6.6835 | 5985.3871 | 6.3916 | 66.1591 | 7.9194 | 2400.0616 | 6.6454 | 6118.6155 | 6.3685 | 66.4449 | 7.9192 | 2455.0184 | 6.6423 | 6062.8912 | 6.5565 | 63.5803 | 7.9192 | 2430.9112 | 6.6835 | 5985.3871 | 6.3916 | 66.1591 | 5.8334 | 412.3837 | 6.8303 | 3982.1938 | 6.8443 | 3944.6879 | 5.8334 | 412.3837 | 6.8303 | 3982.1938 | 6.8443 | 3944.6879 | 6.0528 | 391.1191 | 7.7707 | 106.4244 | 5.675 | 2313.3522 | 6.8036 | 4104.6544 | 6.0528 | 391.1191 | 7.7707 | 106.4244 | 5.675 | 2313.3522 | 6.8036 | 4104.6544
7.9194 | 2448.0628 | 6.613 | 6240.9878 | 6.2257 | 67.7738 | 7.9192 | 2504.1188 | 6.6238 | 6184.149 | 6.4822 | 64.8519 | 7.9192 | 2479.5295 | 6.6558 | 6105.0948 | 6.2432 | 67.4822 | 7.9194 | 2448.0628 | 6.613 | 6240.9878 | 6.2257 | 67.7738 | 7.9192 | 2504.1188 | 6.6238 | 6184.149 | 6.4822 | 64.8519 | 7.9192 | 2479.5295 | 6.6558 | 6105.0948 | 6.2432 | 67.4822 | 5.7844 | 420.6314 | 6.8031 | 4061.8377 | 6.8059 | 4023.5816 | 5.7844 | 420.6314 | 6.8031 | 4061.8377 | 6.8059 | 4023.5816 | 6.0231 | 398.9415 | 7.7454 | 108.5529 | 5.675 | 2359.6192 | 6.7742 | 4186.7475 | 6.0231 | 398.9415 | 7.7454 | 108.5529 | 5.675 | 2359.6192 | 6.7742 | 4186.7475
7.9194 | 2448.0628 | 6.613 | 6240.9878 | 6.2257 | 67.7738 | 7.9192 | 2504.1188 | 6.6238 | 6184.149 | 6.4822 | 64.8519 | 7.9192 | 2479.5295 | 6.6558 | 6105.0948 | 6.2432 | 67.4822 | 7.9194 | 2448.0628 | 6.613 | 6240.9878 | 6.2257 | 67.7738 | 7.9192 | 2504.1188 | 6.6238 | 6184.149 | 6.4822 | 64.8519 | 7.9192 | 2479.5295 | 6.6558 | 6105.0948 | 6.2432 | 67.4822 | 5.7844 | 420.6314 | 6.8031 | 4061.8377 | 6.8059 | 4023.5816 | 5.7844 | 420.6314 | 6.8031 | 4061.8377 | 6.8059 | 4023.5816 | 6.0231 | 398.9415 | 7.7454 | 108.5529 | 5.675 | 2359.6192 | 6.7742 | 4186.7475 | 6.0231 | 398.9415 | 7.7454 | 108.5529 | 5.675 | 2359.6192 | 6.7742 | 4186.7475
7.9194 | 2496.064 | 6.5768 | 6363.3601 | 6.1891 | 69.1027 | 7.9192 | 2553.2191 | 6.5902 | 6305.4068 | 6.3452 | 66.1235 | 7.9192 | 2528.1477 | 6.6177 | 6224.8026 | 6.137 | 68.8054 | 7.9194 | 2496.064 | 6.5768 | 6363.3601 | 6.1891 | 69.1027 | 7.9192 | 2553.2191 | 6.5902 | 6305.4068 | 6.3452 | 66.1235 | 7.9192 | 2528.1477 | 6.6177 | 6224.8026 | 6.137 | 68.8054 | 5.6981 | 428.879 | 6.7765 | 4141.4815 | 6.7785 | 4102.4754 | 5.6981 | 428.879 | 6.7765 | 4141.4815 | 6.7785 | 4102.4754 | 6.0139 | 406.7639 | 7.7196 | 110.6814 | 5.6437 | 2405.8862 | 6.7463 | 4268.8406 | 6.0139 | 406.7639 | 7.7196 | 110.6814 | 5.6437 | 2405.8862 | 6.7463 | 4268.8406
7.9194 | 2496.064 | 6.5768 | 6363.3601 | 6.1891 | 69.1027 | 7.9192 | 2553.2191 | 6.5902 | 6305.4068 | 6.3452 | 66.1235 | 7.9192 | 2528.1477 | 6.6177 | 6224.8026 | 6.137 | 68.8054 | 7.9194 | 2496.064 | 6.5768 | 6363.3601 | 6.1891 | 69.1027 | 7.9192 | 2553.2191 | 6.5902 | 6305.4068 | 6.3452 | 66.1235 | 7.9192 | 2528.1477 | 6.6177 | 6224.8026 | 6.137 | 68.8054 | 5.6981 | 428.879 | 6.7765 | 4141.4815 | 6.7785 | 4102.4754 | 5.6981 | 428.879 | 6.7765 | 4141.4815 | 6.7785 | 4102.4754 | 6.0139 | 406.7639 | 7.7196 | 110.6814 | 5.6437 | 2405.8862 | 6.7463 | 4268.8406 | 6.0139 | 406.7639 | 7.7196 | 110.6814 | 5.6437 | 2405.8862 | 6.7463 | 4268.8406
7.9194 | 2544.0652 | 6.5408 | 6485.7324 | 6.0823 | 70.4316 | 7.9192 | 2602.3195 | 6.5482 | 6426.6646 | 6.2713 | 67.3951 | 7.9192 | 2576.7659 | 6.5627 | 6344.5103 | 5.9607 | 70.1286 | 7.9194 | 2544.0652 | 6.5408 | 6485.7324 | 6.0823 | 70.4316 | 7.9192 | 2602.3195 | 6.5482 | 6426.6646 | 6.2713 | 67.3951 | 7.9192 | 2576.7659 | 6.5627 | 6344.5103 | 5.9607 | 70.1286 | 5.6672 | 437.1267 | 6.7534 | 4221.1254 | 6.755 | 4181.3692 | 5.6672 | 437.1267 | 6.7534 | 4221.1254 | 6.755 | 4181.3692 | 5.9952 | 414.5863 | 7.6915 | 112.8099 | 5.5866 | 2452.1533 | 6.7098 | 4350.9337 | 5.9952 | 414.5863 | 7.6915 | 112.8099 | 5.5866 | 2452.1533 | 6.7098 | 4350.9337
7.9194 | 2544.0652 | 6.5408 | 6485.7324 | 6.0823 | 70.4316 | 7.9192 | 2602.3195 | 6.5482 | 6426.6646 | 6.2713 | 67.3951 | 7.9192 | 2576.7659 | 6.5627 | 6344.5103 | 5.9607 | 70.1286 | 7.9194 | 2544.0652 | 6.5408 | 6485.7324 | 6.0823 | 70.4316 | 7.9192 | 2602.3195 | 6.5482 | 6426.6646 | 6.2713 | 67.3951 | 7.9192 | 2576.7659 | 6.5627 | 6344.5103 | 5.9607 | 70.1286 | 5.6672 | 437.1267 | 6.7534 | 4221.1254 | 6.755 | 4181.3692 | 5.6672 | 437.1267 | 6.7534 | 4221.1254 | 6.755 | 4181.3692 | 5.9952 | 414.5863 | 7.6915 | 112.8099 | 5.5866 | 2452.1533 | 6.7098 | 4350.9337 | 5.9952 | 414.5863 | 7.6915 | 112.8099 | 5.5866 | 2452.1533 | 6.7098 | 4350.9337
7.9194 | 2592.0665 | 6.5 | 6608.1047 | 5.9851 | 71.7605 | 7.9192 | 2651.4199 | 6.5178 | 6547.9224 | 6.2259 | 68.6667 | 7.9191 | 2625.3841 | 6.5238 | 6464.2181 | 5.8884 | 71.4518 | 7.9194 | 2592.0665 | 6.5 | 6608.1047 | 5.9851 | 71.7605 | 7.9192 | 2651.4199 | 6.5178 | 6547.9224 | 6.2259 | 68.6667 | 7.9191 | 2625.3841 | 6.5238 | 6464.2181 | 5.8884 | 71.4518 | 5.6127 | 445.3744 | 6.7251 | 4300.7693 | 6.7348 | 4260.2629 | 5.6127 | 445.3744 | 6.7251 | 4300.7693 | 6.7348 | 4260.2629 | 5.9593 | 422.4087 | 7.6582 | 114.9384 | 5.5549 | 2498.4203 | 6.6825 | 4433.0267 | 5.9593 | 422.4087 | 7.6582 | 114.9384 | 5.5549 | 2498.4203 | 6.6825 | 4433.0267
7.9194 | 2592.0665 | 6.5 | 6608.1047 | 5.9851 | 71.7605 | 7.9192 | 2651.4199 | 6.5178 | 6547.9224 | 6.2259 | 68.6667 | 7.9191 | 2625.3841 | 6.5238 | 6464.2181 | 5.8884 | 71.4518 | 7.9194 | 2592.0665 | 6.5 | 6608.1047 | 5.9851 | 71.7605 | 7.9192 | 2651.4199 | 6.5178 | 6547.9224 | 6.2259 | 68.6667 | 7.9191 | 2625.3841 | 6.5238 | 6464.2181 | 5.8884 | 71.4518 | 5.6127 | 445.3744 | 6.7251 | 4300.7693 | 6.7348 | 4260.2629 | 5.6127 | 445.3744 | 6.7251 | 4300.7693 | 6.7348 | 4260.2629 | 5.9593 | 422.4087 | 7.6582 | 114.9384 | 5.5549 | 2498.4203 | 6.6825 | 4433.0267 | 5.9593 | 422.4087 | 7.6582 | 114.9384 | 5.5549 | 2498.4203 | 6.6825 | 4433.0267
7.9194 | 2640.0677 | 6.4693 | 6730.477 | 5.8444 | 73.0894 | 7.9192 | 2700.5202 | 6.4957 | 6669.1803 | 6.1666 | 69.9383 | 7.9191 | 2674.0024 | 6.5083 | 6583.9258 | 5.8228 | 72.775 | 7.9194 | 2640.0677 | 6.4693 | 6730.477 | 5.8444 | 73.0894 | 7.9192 | 2700.5202 | 6.4957 | 6669.1803 | 6.1666 | 69.9383 | 7.9191 | 2674.0024 | 6.5083 | 6583.9258 | 5.8228 | 72.775 | 5.5268 | 453.6221 | 6.6944 | 4380.4132 | 6.7003 | 4339.1567 | 5.5268 | 453.6221 | 6.6944 | 4380.4132 | 6.7003 | 4339.1567 | 5.9336 | 430.2311 | 7.6361 | 117.0668 | 5.5314 | 2544.6874 | 6.6505 | 4515.1198 | 5.9336 | 430.2311 | 7.6361 | 117.0668 | 5.5314 | 2544.6874 | 6.6505 | 4515.1198
7.9194 | 2640.0677 | 6.4693 | 6730.477 | 5.8444 | 73.0894 | 7.9192 | 2700.5202 | 6.4957 | 6669.1803 | 6.1666 | 69.9383 | 7.9191 | 2674.0024 | 6.5083 | 6583.9258 | 5.8228 | 72.775 | 7.9194 | 2640.0677 | 6.4693 | 6730.477 | 5.8444 | 73.0894 | 7.9192 | 2700.5202 | 6.4957 | 6669.1803 | 6.1666 | 69.9383 | 7.9191 | 2674.0024 | 6.5083 | 6583.9258 | 5.8228 | 72.775 | 5.5268 | 453.6221 | 6.6944 | 4380.4132 | 6.7003 | 4339.1567 | 5.5268 | 453.6221 | 6.6944 | 4380.4132 | 6.7003 | 4339.1567 | 5.9336 | 430.2311 | 7.6361 | 117.0668 | 5.5314 | 2544.6874 | 6.6505 | 4515.1198 | 5.9336 | 430.2311 | 7.6361 | 117.0668 | 5.5314 | 2544.6874 | 6.6505 | 4515.1198
7.9194 | 2688.0689 | 6.4279 | 6852.8493 | 5.7358 | 74.4183 | 7.9192 | 2749.6206 | 6.4603 | 6790.4381 | 6.0403 | 71.2099 | 7.9191 | 2722.6206 | 6.461 | 6703.6336 | 5.7335 | 74.0981 | 7.9194 | 2688.0689 | 6.4279 | 6852.8493 | 5.7358 | 74.4183 | 7.9192 | 2749.6206 | 6.4603 | 6790.4381 | 6.0403 | 71.2099 | 7.9191 | 2722.6206 | 6.461 | 6703.6336 | 5.7335 | 74.0981 | 5.5014 | 461.8697 | 6.6679 | 4460.0571 | 6.6774 | 4418.0504 | 5.5014 | 461.8697 | 6.6679 | 4460.0571 | 6.6774 | 4418.0504 | 5.901 | 438.0534 | 7.6095 | 119.1953 | 5.4593 | 2590.9544 | 6.622 | 4597.2129 | 5.901 | 438.0534 | 7.6095 | 119.1953 | 5.4593 | 2590.9544 | 6.622 | 4597.2129
7.9194 | 2688.0689 | 6.4279 | 6852.8493 | 5.7358 | 74.4183 | 7.9192 | 2749.6206 | 6.4603 | 6790.4381 | 6.0403 | 71.2099 | 7.9191 | 2722.6206 | 6.461 | 6703.6336 | 5.7335 | 74.0981 | 7.9194 | 2688.0689 | 6.4279 | 6852.8493 | 5.7358 | 74.4183 | 7.9192 | 2749.6206 | 6.4603 | 6790.4381 | 6.0403 | 71.2099 | 7.9191 | 2722.6206 | 6.461 | 6703.6336 | 5.7335 | 74.0981 | 5.5014 | 461.8697 | 6.6679 | 4460.0571 | 6.6774 | 4418.0504 | 5.5014 | 461.8697 | 6.6679 | 4460.0571 | 6.6774 | 4418.0504 | 5.901 | 438.0534 | 7.6095 | 119.1953 | 5.4593 | 2590.9544 | 6.622 | 4597.2129 | 5.901 | 438.0534 | 7.6095 | 119.1953 | 5.4593 | 2590.9544 | 6.622 | 4597.2129
7.9194 | 2736.0702 | 6.3807 | 6975.2216 | 5.6649 | 75.7472 | 7.9192 | 2798.721 | 6.3993 | 6911.6959 | 5.9485 | 72.4815 | 7.9191 | 2771.2388 | 6.4143 | 6823.3413 | 5.6434 | 75.4213 | 7.9194 | 2736.0702 | 6.3807 | 6975.2216 | 5.6649 | 75.7472 | 7.9192 | 2798.721 | 6.3993 | 6911.6959 | 5.9485 | 72.4815 | 7.9191 | 2771.2388 | 6.4143 | 6823.3413 | 5.6434 | 75.4213 | 5.4626 | 470.1174 | 6.6499 | 4539.7009 | 6.6505 | 4496.9442 | 5.4626 | 470.1174 | 6.6499 | 4539.7009 | 6.6505 | 4496.9442 | 5.8516 | 445.8758 | 7.5854 | 121.3238 | 5.4297 | 2637.2215 | 6.5773 | 4679.306 | 5.8516 | 445.8758 | 7.5854 | 121.3238 | 5.4297 | 2637.2215 | 6.5773 | 4679.306
7.9194 | 2736.0702 | 6.3807 | 6975.2216 | 5.6649 | 75.7472 | 7.9192 | 2798.721 | 6.3993 | 6911.6959 | 5.9485 | 72.4815 | 7.9191 | 2771.2388 | 6.4143 | 6823.3413 | 5.6434 | 75.4213 | 7.9194 | 2736.0702 | 6.3807 | 6975.2216 | 5.6649 | 75.7472 | 7.9192 | 2798.721 | 6.3993 | 6911.6959 | 5.9485 | 72.4815 | 7.9191 | 2771.2388 | 6.4143 | 6823.3413 | 5.6434 | 75.4213 | 5.4626 | 470.1174 | 6.6499 | 4539.7009 | 6.6505 | 4496.9442 | 5.4626 | 470.1174 | 6.6499 | 4539.7009 | 6.6505 | 4496.9442 | 5.8516 | 445.8758 | 7.5854 | 121.3238 | 5.4297 | 2637.2215 | 6.5773 | 4679.306 | 5.8516 | 445.8758 | 7.5854 | 121.3238 | 5.4297 | 2637.2215 | 6.5773 | 4679.306
7.9194 | 2784.0714 | 6.3129 | 7097.5939 | 5.5389 | 77.0761 | 7.9192 | 2847.8213 | 6.3471 | 7032.9537 | 5.8379 | 73.7531 | 7.9191 | 2819.857 | 6.3768 | 6943.049 | 5.5966 | 76.7445 | 7.9194 | 2784.0714 | 6.3129 | 7097.5939 | 5.5389 | 77.0761 | 7.9192 | 2847.8213 | 6.3471 | 7032.9537 | 5.8379 | 73.7531 | 7.9191 | 2819.857 | 6.3768 | 6943.049 | 5.5966 | 76.7445 | 5.3769 | 478.3651 | 6.6229 | 4619.3448 | 6.6249 | 4575.8379 | 5.3769 | 478.3651 | 6.6229 | 4619.3448 | 6.6249 | 4575.8379 | 5.8246 | 453.6982 | 7.5561 | 123.4523 | 5.3365 | 2683.4885 | 6.5423 | 4761.3991 | 5.8246 | 453.6982 | 7.5561 | 123.4523 | 5.3365 | 2683.4885 | 6.5423 | 4761.3991
7.9194 | 2784.0714 | 6.3129 | 7097.5939 | 5.5389 | 77.0761 | 7.9192 | 2847.8213 | 6.3471 | 7032.9537 | 5.8379 | 73.7531 | 7.9191 | 2819.857 | 6.3768 | 6943.049 | 5.5966 | 76.7445 | 7.9194 | 2784.0714 | 6.3129 | 7097.5939 | 5.5389 | 77.0761 | 7.9192 | 2847.8213 | 6.3471 | 7032.9537 | 5.8379 | 73.7531 | 7.9191 | 2819.857 | 6.3768 | 6943.049 | 5.5966 | 76.7445 | 5.3769 | 478.3651 | 6.6229 | 4619.3448 | 6.6249 | 4575.8379 | 5.3769 | 478.3651 | 6.6229 | 4619.3448 | 6.6249 | 4575.8379 | 5.8246 | 453.6982 | 7.5561 | 123.4523 | 5.3365 | 2683.4885 | 6.5423 | 4761.3991 | 5.8246 | 453.6982 | 7.5561 | 123.4523 | 5.3365 | 2683.4885 | 6.5423 | 4761.3991
7.9194 | 2832.0726 | 6.2455 | 7219.9662 | 5.4821 | 78.405 | 7.9192 | 2896.9217 | 6.277 | 7154.2116 | 5.7465 | 75.0247 | 7.9191 | 2868.4753 | 6.3327 | 7062.7568 | 5.5783 | 78.0677 | 7.9194 | 2832.0726 | 6.2455 | 7219.9662 | 5.4821 | 78.405 | 7.9192 | 2896.9217 | 6.277 | 7154.2116 | 5.7465 | 75.0247 | 7.9191 | 2868.4753 | 6.3327 | 7062.7568 | 5.5783 | 78.0677 | 5.3409 | 486.6127 | 6.5806 | 4698.9887 | 6.5711 | 4654.7317 | 5.3409 | 486.6127 | 6.5806 | 4698.9887 | 6.5711 | 4654.7317 | 5.7879 | 461.5206 | 7.5287 | 125.5808 | 5.3365 | 2729.7555 | 6.4977 | 4843.4922 | 5.7879 | 461.5206 | 7.5287 | 125.5808 | 5.3365 | 2729.7555 | 6.4977 | 4843.4922
7.9194 | 2832.0726 | 6.2455 | 7219.9662 | 5.4821 | 78.405 | 7.9192 | 2896.9217 | 6.277 | 7154.2116 | 5.7465 | 75.0247 | 7.9191 | 2868.4753 | 6.3327 | 7062.7568 | 5.5783 | 78.0677 | 7.9194 | 2832.0726 | 6.2455 | 7219.9662 | 5.4821 | 78.405 | 7.9192 | 2896.9217 | 6.277 | 7154.2116 | 5.7465 | 75.0247 | 7.9191 | 2868.4753 | 6.3327 | 7062.7568 | 5.5783 | 78.0677 | 5.3409 | 486.6127 | 6.5806 | 4698.9887 | 6.5711 | 4654.7317 | 5.3409 | 486.6127 | 6.5806 | 4698.9887 | 6.5711 | 4654.7317 | 5.7879 | 461.5206 | 7.5287 | 125.5808 | 5.3365 | 2729.7555 | 6.4977 | 4843.4922 | 5.7879 | 461.5206 | 7.5287 | 125.5808 | 5.3365 | 2729.7555 | 6.4977 | 4843.4922
7.9193 | 2880.0739 | 6.2029 | 7342.3385 | 5.4352 | 79.7339 | 7.9192 | 2946.0221 | 6.2421 | 7275.4694 | 5.6165 | 76.2963 | 7.9191 | 2917.0935 | 6.278 | 7182.4645 | 5.4492 | 79.3909 | 7.9193 | 2880.0739 | 6.2029 | 7342.3385 | 5.4352 | 79.7339 | 7.9192 | 2946.0221 | 6.2421 | 7275.4694 | 5.6165 | 76.2963 | 7.9191 | 2917.0935 | 6.278 | 7182.4645 | 5.4492 | 79.3909 | 5.2882 | 494.8604 | 6.5549 | 4778.6326 | 6.5406 | 4733.6255 | 5.2882 | 494.8604 | 6.5549 | 4778.6326 | 6.5406 | 4733.6255 | 5.7006 | 469.343 | 7.5047 | 127.7093 | 5.3365 | 2776.0226 | 6.478 | 4925.5853 | 5.7006 | 469.343 | 7.5047 | 127.7093 | 5.3365 | 2776.0226 | 6.478 | 4925.5853
7.9193 | 2880.0739 | 6.2029 | 7342.3385 | 5.4352 | 79.7339 | 7.9192 | 2946.0221 | 6.2421 | 7275.4694 | 5.6165 | 76.2963 | 7.9191 | 2917.0935 | 6.278 | 7182.4645 | 5.4492 | 79.3909 | 7.9193 | 2880.0739 | 6.2029 | 7342.3385 | 5.4352 | 79.7339 | 7.9192 | 2946.0221 | 6.2421 | 7275.4694 | 5.6165 | 76.2963 | 7.9191 | 2917.0935 | 6.278 | 7182.4645 | 5.4492 | 79.3909 | 5.2882 | 494.8604 | 6.5549 | 4778.6326 | 6.5406 | 4733.6255 | 5.2882 | 494.8604 | 6.5549 | 4778.6326 | 6.5406 | 4733.6255 | 5.7006 | 469.343 | 7.5047 | 127.7093 | 5.3365 | 2776.0226 | 6.478 | 4925.5853 | 5.7006 | 469.343 | 7.5047 | 127.7093 | 5.3365 | 2776.0226 | 6.478 | 4925.5853
7.9193 | 2928.0751 | 6.1594 | 7464.7108 | 5.2677 | 81.0628 | 7.9192 | 2995.1224 | 6.1924 | 7396.7272 | 5.5385 | 77.5679 | 7.9191 | 2965.7117 | 6.2201 | 7302.1723 | 5.4087 | 80.714 | 7.9193 | 2928.0751 | 6.1594 | 7464.7108 | 5.2677 | 81.0628 | 7.9192 | 2995.1224 | 6.1924 | 7396.7272 | 5.5385 | 77.5679 | 7.9191 | 2965.7117 | 6.2201 | 7302.1723 | 5.4087 | 80.714 | 5.1747 | 503.1081 | 6.5043 | 4858.2764 | 6.5019 | 4812.5192 | 5.1747 | 503.1081 | 6.5043 | 4858.2764 | 6.5019 | 4812.5192 | 5.6528 | 477.1653 | 7.4797 | 129.8378 | 5.2116 | 2822.2896 | 6.4425 | 5007.6784 | 5.6528 | 477.1653 | 7.4797 | 129.8378 | 5.2116 | 2822.2896 | 6.4425 | 5007.6784
7.9193 | 2928.0751 | 6.1594 | 7464.7108 | 5.2677 | 81.0628 | 7.9192 | 2995.1224 | 6.1924 | 7396.7272 | 5.5385 | 77.5679 | 7.9191 | 2965.7117 | 6.2201 | 7302.1723 | 5.4087 | 80.714 | 7.9193 | 2928.0751 | 6.1594 | 7464.7108 | 5.2677 | 81.0628 | 7.9192 | 2995.1224 | 6.1924 | 7396.7272 | 5.5385 | 77.5679 | 7.9191 | 2965.7117 | 6.2201 | 7302.1723 | 5.4087 | 80.714 | 5.1747 | 503.1081 | 6.5043 | 4858.2764 | 6.5019 | 4812.5192 | 5.1747 | 503.1081 | 6.5043 | 4858.2764 | 6.5019 | 4812.5192 | 5.6528 | 477.1653 | 7.4797 | 129.8378 | 5.2116 | 2822.2896 | 6.4425 | 5007.6784 | 5.6528 | 477.1653 | 7.4797 | 129.8378 | 5.2116 | 2822.2896 | 6.4425 | 5007.6784
7.9193 | 2976.0763 | 6.1221 | 7587.0832 | 5.2402 | 82.3917 | 7.9192 | 3044.2228 | 6.1482 | 7517.985 | 5.5005 | 78.8395 | 7.919 | 3014.3299 | 6.1751 | 7421.88 | 5.2541 | 82.0372 | 7.9193 | 2976.0763 | 6.1221 | 7587.0832 | 5.2402 | 82.3917 | 7.9192 | 3044.2228 | 6.1482 | 7517.985 | 5.5005 | 78.8395 | 7.919 | 3014.3299 | 6.1751 | 7421.88 | 5.2541 | 82.0372 | 5.1401 | 511.3558 | 6.4692 | 4937.9203 | 6.4826 | 4891.413 | 5.1401 | 511.3558 | 6.4692 | 4937.9203 | 6.4826 | 4891.413 | 5.6065 | 484.9877 | 7.4521 | 131.9663 | 5.2116 | 2868.5567 | 6.4034 | 5089.7714 | 5.6065 | 484.9877 | 7.4521 | 131.9663 | 5.2116 | 2868.5567 | 6.4034 | 5089.7714
7.9193 | 2976.0763 | 6.1221 | 7587.0832 | 5.2402 | 82.3917 | 7.9192 | 3044.2228 | 6.1482 | 7517.985 | 5.5005 | 78.8395 | 7.919 | 3014.3299 | 6.1751 | 7421.88 | 5.2541 | 82.0372 | 7.9193 | 2976.0763 | 6.1221 | 7587.0832 | 5.2402 | 82.3917 | 7.9192 | 3044.2228 | 6.1482 | 7517.985 | 5.5005 | 78.8395 | 7.919 | 3014.3299 | 6.1751 | 7421.88 | 5.2541 | 82.0372 | 5.1401 | 511.3558 | 6.4692 | 4937.9203 | 6.4826 | 4891.413 | 5.1401 | 511.3558 | 6.4692 | 4937.9203 | 6.4826 | 4891.413 | 5.6065 | 484.9877 | 7.4521 | 131.9663 | 5.2116 | 2868.5567 | 6.4034 | 5089.7714 | 5.6065 | 484.9877 | 7.4521 | 131.9663 | 5.2116 | 2868.5567 | 6.4034 | 5089.7714
7.9193 | 3024.0776 | 6.0874 | 7709.4555 | 5.1857 | 83.7206 | 7.9192 | 3093.3232 | 6.127 | 7639.2428 | 5.4691 | 80.1111 | 7.919 | 3062.9482 | 6.1282 | 7541.5877 | 5.0383 | 83.3604 | 7.9193 | 3024.0776 | 6.0874 | 7709.4555 | 5.1857 | 83.7206 | 7.9192 | 3093.3232 | 6.127 | 7639.2428 | 5.4691 | 80.1111 | 7.919 | 3062.9482 | 6.1282 | 7541.5877 | 5.0383 | 83.3604 | 5.0006 | 519.6034 | 6.4349 | 5017.5642 | 6.4593 | 4970.3067 | 5.0006 | 519.6034 | 6.4349 | 5017.5642 | 6.4593 | 4970.3067 | 5.5526 | 492.8101 | 7.4301 | 134.0947 | 5.2116 | 2914.8237 | 6.3788 | 5171.8645 | 5.5526 | 492.8101 | 7.4301 | 134.0947 | 5.2116 | 2914.8237 | 6.3788 | 5171.8645
7.9193 | 3024.0776 | 6.0874 | 7709.4555 | 5.1857 | 83.7206 | 7.9192 | 3093.3232 | 6.127 | 7639.2428 | 5.4691 | 80.1111 | 7.919 | 3062.9482 | 6.1282 | 7541.5877 | 5.0383 | 83.3604 | 7.9193 | 3024.0776 | 6.0874 | 7709.4555 | 5.1857 | 83.7206 | 7.9192 | 3093.3232 | 6.127 | 7639.2428 | 5.4691 | 80.1111 | 7.919 | 3062.9482 | 6.1282 | 7541.5877 | 5.0383 | 83.3604 | 5.0006 | 519.6034 | 6.4349 | 5017.5642 | 6.4593 | 4970.3067 | 5.0006 | 519.6034 | 6.4349 | 5017.5642 | 6.4593 | 4970.3067 | 5.5526 | 492.8101 | 7.4301 | 134.0947 | 5.2116 | 2914.8237 | 6.3788 | 5171.8645 | 5.5526 | 492.8101 | 7.4301 | 134.0947 | 5.2116 | 2914.8237 | 6.3788 | 5171.8645
7.9193 | 3072.0788 | 6.056 | 7831.8278 | 5.1596 | 85.0495 | 7.9192 | 3142.4235 | 6.0664 | 7760.5007 | 5.3962 | 81.3827 | 7.919 | 3111.5664 | 6.082 | 7661.2955 | 5.0175 | 84.6836 | 7.9193 | 3072.0788 | 6.056 | 7831.8278 | 5.1596 | 85.0495 | 7.9192 | 3142.4235 | 6.0664 | 7760.5007 | 5.3962 | 81.3827 | 7.919 | 3111.5664 | 6.082 | 7661.2955 | 5.0175 | 84.6836 | 5.0006 | 527.8511 | 6.4061 | 5097.2081 | 6.4072 | 5049.2005 | 5.0006 | 527.8511 | 6.4061 | 5097.2081 | 6.4072 | 5049.2005 | 5.5489 | 500.6325 | 7.4061 | 136.2232 | 5.2116 | 2961.0908 | 6.364 | 5253.9576 | 5.5489 | 500.6325 | 7.4061 | 136.2232 | 5.2116 | 2961.0908 | 6.364 | 5253.9576
7.9193 | 3072.0788 | 6.056 | 7831.8278 | 5.1596 | 85.0495 | 7.9192 | 3142.4235 | 6.0664 | 7760.5007 | 5.3962 | 81.3827 | 7.919 | 3111.5664 | 6.082 | 7661.2955 | 5.0175 | 84.6836 | 7.9193 | 3072.0788 | 6.056 | 7831.8278 | 5.1596 | 85.0495 | 7.9192 | 3142.4235 | 6.0664 | 7760.5007 | 5.3962 | 81.3827 | 7.919 | 3111.5664 | 6.082 | 7661.2955 | 5.0175 | 84.6836 | 5.0006 | 527.8511 | 6.4061 | 5097.2081 | 6.4072 | 5049.2005 | 5.0006 | 527.8511 | 6.4061 | 5097.2081 | 6.4072 | 5049.2005 | 5.5489 | 500.6325 | 7.4061 | 136.2232 | 5.2116 | 2961.0908 | 6.364 | 5253.9576 | 5.5489 | 500.6325 | 7.4061 | 136.2232 | 5.2116 | 2961.0908 | 6.364 | 5253.9576
7.9193 | 3120.08 | 6.0191 | 7954.2001 | 5.1411 | 86.3784 | 7.9192 | 3191.5239 | 6.0203 | 7881.7585 | 5.2216 | 82.6543 | 7.9188 | 3160.1846 | 6.0491 | 7781.0032 | 4.9017 | 86.0068 | 7.9193 | 3120.08 | 6.0191 | 7954.2001 | 5.1411 | 86.3784 | 7.9192 | 3191.5239 | 6.0203 | 7881.7585 | 5.2216 | 82.6543 | 7.9188 | 3160.1846 | 6.0491 | 7781.0032 | 4.9017 | 86.0068 | 4.8633 | 536.0988 | 6.3822 | 5176.8519 | 6.3776 | 5128.0943 | 4.8633 | 536.0988 | 6.3822 | 5176.8519 | 6.3776 | 5128.0943 | 5.4823 | 508.4549 | 7.3859 | 138.3517 | 5.2116 | 3007.3578 | 6.3396 | 5336.0507 | 5.4823 | 508.4549 | 7.3859 | 138.3517 | 5.2116 | 3007.3578 | 6.3396 | 5336.0507
7.9193 | 3120.08 | 6.0191 | 7954.2001 | 5.1411 | 86.3784 | 7.9192 | 3191.5239 | 6.0203 | 7881.7585 | 5.2216 | 82.6543 | 7.9188 | 3160.1846 | 6.0491 | 7781.0032 | 4.9017 | 86.0068 | 7.9193 | 3120.08 | 6.0191 | 7954.2001 | 5.1411 | 86.3784 | 7.9192 | 3191.5239 | 6.0203 | 7881.7585 | 5.2216 | 82.6543 | 7.9188 | 3160.1846 | 6.0491 | 7781.0032 | 4.9017 | 86.0068 | 4.8633 | 536.0988 | 6.3822 | 5176.8519 | 6.3776 | 5128.0943 | 4.8633 | 536.0988 | 6.3822 | 5176.8519 | 6.3776 | 5128.0943 | 5.4823 | 508.4549 | 7.3859 | 138.3517 | 5.2116 | 3007.3578 | 6.3396 | 5336.0507 | 5.4823 | 508.4549 | 7.3859 | 138.3517 | 5.2116 | 3007.3578 | 6.3396 | 5336.0507
7.9193 | 3168.0813 | 5.982 | 8076.5724 | 5.0085 | 87.7073 | 7.9192 | 3240.6243 | 5.983 | 8003.0163 | 5.0804 | 83.9259 | 7.9188 | 3208.8028 | 6.0188 | 7900.711 | 4.8731 | 87.33 | 7.9193 | 3168.0813 | 5.982 | 8076.5724 | 5.0085 | 87.7073 | 7.9192 | 3240.6243 | 5.983 | 8003.0163 | 5.0804 | 83.9259 | 7.9188 | 3208.8028 | 6.0188 | 7900.711 | 4.8731 | 87.33 | 4.7891 | 544.3465 | 6.3597 | 5256.4958 | 6.3542 | 5206.988 | 4.7891 | 544.3465 | 6.3597 | 5256.4958 | 6.3542 | 5206.988 | 5.4346 | 516.2773 | 7.3706 | 140.4802 | 5.1324 | 3053.6248 | 6.3053 | 5418.1438 | 5.4346 | 516.2773 | 7.3706 | 140.4802 | 5.1324 | 3053.6248 | 6.3053 | 5418.1438
7.9193 | 3168.0813 | 5.982 | 8076.5724 | 5.0085 | 87.7073 | 7.9192 | 3240.6243 | 5.983 | 8003.0163 | 5.0804 | 83.9259 | 7.9188 | 3208.8028 | 6.0188 | 7900.711 | 4.8731 | 87.33 | 7.9193 | 3168.0813 | 5.982 | 8076.5724 | 5.0085 | 87.7073 | 7.9192 | 3240.6243 | 5.983 | 8003.0163 | 5.0804 | 83.9259 | 7.9188 | 3208.8028 | 6.0188 | 7900.711 | 4.8731 | 87.33 | 4.7891 | 544.3465 | 6.3597 | 5256.4958 | 6.3542 | 5206.988 | 4.7891 | 544.3465 | 6.3597 | 5256.4958 | 6.3542 | 5206.988 | 5.4346 | 516.2773 | 7.3706 | 140.4802 | 5.1324 | 3053.6248 | 6.3053 | 5418.1438 | 5.4346 | 516.2773 | 7.3706 | 140.4802 | 5.1324 | 3053.6248 | 6.3053 | 5418.1438
7.9193 | 3216.0825 | 5.9556 | 8198.9447 | 4.8068 | 89.0362 | 7.9192 | 3289.7246 | 5.9216 | 8124.2741 | 5.0504 | 85.1975 | 7.9188 | 3257.4211 | 5.9965 | 8020.4187 | 4.8109 | 88.6531 | 7.9193 | 3216.0825 | 5.9556 | 8198.9447 | 4.8068 | 89.0362 | 7.9192 | 3289.7246 | 5.9216 | 8124.2741 | 5.0504 | 85.1975 | 7.9188 | 3257.4211 | 5.9965 | 8020.4187 | 4.8109 | 88.6531 | 4.7891 | 552.5941 | 6.3386 | 5336.1397 | 6.3375 | 5285.8818 | 4.7891 | 552.5941 | 6.3386 | 5336.1397 | 6.3375 | 5285.8818 | 5.4343 | 524.0996 | 7.3517 | 142.6087 | 5.1324 | 3099.8919 | 6.2849 | 5500.2369 | 5.4343 | 524.0996 | 7.3517 | 142.6087 | 5.1324 | 3099.8919 | 6.2849 | 5500.2369
7.9193 | 3216.0825 | 5.9556 | 8198.9447 | 4.8068 | 89.0362 | 7.9192 | 3289.7246 | 5.9216 | 8124.2741 | 5.0504 | 85.1975 | 7.9188 | 3257.4211 | 5.9965 | 8020.4187 | 4.8109 | 88.6531 | 7.9193 | 3216.0825 | 5.9556 | 8198.9447 | 4.8068 | 89.0362 | 7.9192 | 3289.7246 | 5.9216 | 8124.2741 | 5.0504 | 85.1975 | 7.9188 | 3257.4211 | 5.9965 | 8020.4187 | 4.8109 | 88.6531 | 4.7891 | 552.5941 | 6.3386 | 5336.1397 | 6.3375 | 5285.8818 | 4.7891 | 552.5941 | 6.3386 | 5336.1397 | 6.3375 | 5285.8818 | 5.4343 | 524.0996 | 7.3517 | 142.6087 | 5.1324 | 3099.8919 | 6.2849 | 5500.2369 | 5.4343 | 524.0996 | 7.3517 | 142.6087 | 5.1324 | 3099.8919 | 6.2849 | 5500.2369
7.9191 | 3264.0837 | 5.914 | 8321.317 | 4.7721 | 90.3651 | 7.9192 | 3338.825 | 5.8968 | 8245.532 | 5.019 | 86.4691 | 7.9188 | 3306.0393 | 5.9728 | 8140.1265 | 4.7801 | 89.9763 | 7.9191 | 3264.0837 | 5.914 | 8321.317 | 4.7721 | 90.3651 | 7.9192 | 3338.825 | 5.8968 | 8245.532 | 5.019 | 86.4691 | 7.9188 | 3306.0393 | 5.9728 | 8140.1265 | 4.7801 | 89.9763 | 4.5866 | 560.8418 | 6.3065 | 5415.7836 | 6.3176 | 5364.7755 | 4.5866 | 560.8418 | 6.3065 | 5415.7836 | 6.3176 | 5364.7755 | 5.3136 | 531.922 | 7.3314 | 144.7372 | 5.1324 | 3146.1589 | 6.2651 | 5582.33 | 5.3136 | 531.922 | 7.3314 | 144.7372 | 5.1324 | 3146.1589 | 6.2651 | 5582.33
7.9191 | 3264.0837 | 5.914 | 8321.317 | 4.7721 | 90.3651 | 7.9192 | 3338.825 | 5.8968 | 8245.532 | 5.019 | 86.4691 | 7.9188 | 3306.0393 | 5.9728 | 8140.1265 | 4.7801 | 89.9763 | 7.9191 | 3264.0837 | 5.914 | 8321.317 | 4.7721 | 90.3651 | 7.9192 | 3338.825 | 5.8968 | 8245.532 | 5.019 | 86.4691 | 7.9188 | 3306.0393 | 5.9728 | 8140.1265 | 4.7801 | 89.9763 | 4.5866 | 560.8418 | 6.3065 | 5415.7836 | 6.3176 | 5364.7755 | 4.5866 | 560.8418 | 6.3065 | 5415.7836 | 6.3176 | 5364.7755 | 5.3136 | 531.922 | 7.3314 | 144.7372 | 5.1324 | 3146.1589 | 6.2651 | 5582.33 | 5.3136 | 531.922 | 7.3314 | 144.7372 | 5.1324 | 3146.1589 | 6.2651 | 5582.33
7.9191 | 3312.0849 | 5.8467 | 8443.6893 | 4.7552 | 91.694 | 7.9192 | 3387.9254 | 5.8291 | 8366.7898 | 4.8506 | 87.7408 | 7.9188 | 3354.6575 | 5.8998 | 8259.8342 | 4.7011 | 91.2995 | 7.9191 | 3312.0849 | 5.8467 | 8443.6893 | 4.7552 | 91.694 | 7.9192 | 3387.9254 | 5.8291 | 8366.7898 | 4.8506 | 87.7408 | 7.9188 | 3354.6575 | 5.8998 | 8259.8342 | 4.7011 | 91.2995 | 4.0595 | 569.0895 | 6.2613 | 5495.4274 | 6.2868 | 5443.6693 | 4.0595 | 569.0895 | 6.2613 | 5495.4274 | 6.2868 | 5443.6693 | 5.2298 | 539.7444 | 7.3187 | 146.8657 | 5.1324 | 3192.426 | 6.2183 | 5664.4231 | 5.2298 | 539.7444 | 7.3187 | 146.8657 | 5.1324 | 3192.426 | 6.2183 | 5664.4231
7.9191 | 3312.0849 | 5.8467 | 8443.6893 | 4.7552 | 91.694 | 7.9192 | 3387.9254 | 5.8291 | 8366.7898 | 4.8506 | 87.7408 | 7.9188 | 3354.6575 | 5.8998 | 8259.8342 | 4.7011 | 91.2995 | 7.9191 | 3312.0849 | 5.8467 | 8443.6893 | 4.7552 | 91.694 | 7.9192 | 3387.9254 | 5.8291 | 8366.7898 | 4.8506 | 87.7408 | 7.9188 | 3354.6575 | 5.8998 | 8259.8342 | 4.7011 | 91.2995 | 4.0595 | 569.0895 | 6.2613 | 5495.4274 | 6.2868 | 5443.6693 | 4.0595 | 569.0895 | 6.2613 | 5495.4274 | 6.2868 | 5443.6693 | 5.2298 | 539.7444 | 7.3187 | 146.8657 | 5.1324 | 3192.426 | 6.2183 | 5664.4231 | 5.2298 | 539.7444 | 7.3187 | 146.8657 | 5.1324 | 3192.426 | 6.2183 | 5664.4231
7.9191 | 3360.0862 | 5.828 | 8566.0616 | 4.7333 | 93.0229 | 7.9192 | 3437.0257 | 5.8219 | 8488.0476 | 4.8049 | 89.0124 | 7.9187 | 3403.2757 | 5.8916 | 8379.5419 | 4.6389 | 92.6227 | 7.9191 | 3360.0862 | 5.828 | 8566.0616 | 4.7333 | 93.0229 | 7.9192 | 3437.0257 | 5.8219 | 8488.0476 | 4.8049 | 89.0124 | 7.9187 | 3403.2757 | 5.8916 | 8379.5419 | 4.6389 | 92.6227 | 4.0595 | 577.3372 | 6.2519 | 5575.0713 | 6.2754 | 5522.563 | 4.0595 | 577.3372 | 6.2519 | 5575.0713 | 6.2754 | 5522.563 | 5.1963 | 547.5668 | 7.3023 | 148.9942 | 5.1324 | 3238.693 | 6.2035 | 5746.5161 | 5.1963 | 547.5668 | 7.3023 | 148.9942 | 5.1324 | 3238.693 | 6.2035 | 5746.5161
7.9191 | 3360.0862 | 5.828 | 8566.0616 | 4.7333 | 93.0229 | 7.9192 | 3437.0257 | 5.8219 | 8488.0476 | 4.8049 | 89.0124 | 7.9187 | 3403.2757 | 5.8916 | 8379.5419 | 4.6389 | 92.6227 | 7.9191 | 3360.0862 | 5.828 | 8566.0616 | 4.7333 | 93.0229 | 7.9192 | 3437.0257 | 5.8219 | 8488.0476 | 4.8049 | 89.0124 | 7.9187 | 3403.2757 | 5.8916 | 8379.5419 | 4.6389 | 92.6227 | 4.0595 | 577.3372 | 6.2519 | 5575.0713 | 6.2754 | 5522.563 | 4.0595 | 577.3372 | 6.2519 | 5575.0713 | 6.2754 | 5522.563 | 5.1963 | 547.5668 | 7.3023 | 148.9942 | 5.1324 | 3238.693 | 6.2035 | 5746.5161 | 5.1963 | 547.5668 | 7.3023 | 148.9942 | 5.1324 | 3238.693 | 6.2035 | 5746.5161
7.9191 | 3408.0874 | 5.8025 | 8688.4339 | 4.6395 | 94.3518 | 7.9192 | 3486.1261 | 5.7714 | 8609.3054 | 4.7879 | 90.284 | 7.9187 | 3451.894 | 5.8463 | 8499.2497 | 4.5148 | 93.9459 | 7.9191 | 3408.0874 | 5.8025 | 8688.4339 | 4.6395 | 94.3518 | 7.9192 | 3486.1261 | 5.7714 | 8609.3054 | 4.7879 | 90.284 | 7.9187 | 3451.894 | 5.8463 | 8499.2497 | 4.5148 | 93.9459 | 4.0595 | 585.5848 | 6.224 | 5654.7152 | 6.2623 | 5601.4568 | 4.0595 | 585.5848 | 6.224 | 5654.7152 | 6.2623 | 5601.4568 | 5.1792 | 555.3892 | 7.2772 | 151.1227 | 5.1324 | 3284.9601 | 6.1853 | 5828.6092 | 5.1792 | 555.3892 | 7.2772 | 151.1227 | 5.1324 | 3284.9601 | 6.1853 | 5828.6092
7.9191 | 3408.0874 | 5.8025 | 8688.4339 | 4.6395 | 94.3518 | 7.9192 | 3486.1261 | 5.7714 | 8609.3054 | 4.7879 | 90.284 | 7.9187 | 3451.894 | 5.8463 | 8499.2497 | 4.5148 | 93.9459 | 7.9191 | 3408.0874 | 5.8025 | 8688.4339 | 4.6395 | 94.3518 | 7.9192 | 3486.1261 | 5.7714 | 8609.3054 | 4.7879 | 90.284 | 7.9187 | 3451.894 | 5.8463 | 8499.2497 | 4.5148 | 93.9459 | 4.0595 | 585.5848 | 6.224 | 5654.7152 | 6.2623 | 5601.4568 | 4.0595 | 585.5848 | 6.224 | 5654.7152 | 6.2623 | 5601.4568 | 5.1792 | 555.3892 | 7.2772 | 151.1227 | 5.1324 | 3284.9601 | 6.1853 | 5828.6092 | 5.1792 | 555.3892 | 7.2772 | 151.1227 | 5.1324 | 3284.9601 | 6.1853 | 5828.6092
7.9191 | 3456.0886 | 5.7544 | 8810.8062 | 4.5951 | 95.6807 | 7.919 | 3535.2265 | 5.7285 | 8730.5633 | 4.711 | 91.5556 | 7.9187 | 3500.5122 | 5.8 | 8618.9574 | 4.3913 | 95.269 | 7.9191 | 3456.0886 | 5.7544 | 8810.8062 | 4.5951 | 95.6807 | 7.919 | 3535.2265 | 5.7285 | 8730.5633 | 4.711 | 91.5556 | 7.9187 | 3500.5122 | 5.8 | 8618.9574 | 4.3913 | 95.269 | 4.0595 | 593.8325 | 6.1789 | 5734.3591 | 6.2392 | 5680.3506 | 4.0595 | 593.8325 | 6.1789 | 5734.3591 | 6.2392 | 5680.3506 | 5.0892 | 563.2116 | 7.2619 | 153.2511 | 5.1324 | 3331.2271 | 6.1648 | 5910.7023 | 5.0892 | 563.2116 | 7.2619 | 153.2511 | 5.1324 | 3331.2271 | 6.1648 | 5910.7023
7.9191 | 3456.0886 | 5.7544 | 8810.8062 | 4.5951 | 95.6807 | 7.919 | 3535.2265 | 5.7285 | 8730.5633 | 4.711 | 91.5556 | 7.9187 | 3500.5122 | 5.8 | 8618.9574 | 4.3913 | 95.269 | 7.9191 | 3456.0886 | 5.7544 | 8810.8062 | 4.5951 | 95.6807 | 7.919 | 3535.2265 | 5.7285 | 8730.5633 | 4.711 | 91.5556 | 7.9187 | 3500.5122 | 5.8 | 8618.9574 | 4.3913 | 95.269 | 4.0595 | 593.8325 | 6.1789 | 5734.3591 | 6.2392 | 5680.3506 | 4.0595 | 593.8325 | 6.1789 | 5734.3591 | 6.2392 | 5680.3506 | 5.0892 | 563.2116 | 7.2619 | 153.2511 | 5.1324 | 3331.2271 | 6.1648 | 5910.7023 | 5.0892 | 563.2116 | 7.2619 | 153.2511 | 5.1324 | 3331.2271 | 6.1648 | 5910.7023
7.9189 | 3504.0899 | 5.6891 | 8933.1786 | 4.5611 | 97.0096 | 7.919 | 3584.3268 | 5.6849 | 8851.8211 | 4.634 | 92.8272 | 7.9187 | 3549.1304 | 5.7787 | 8738.6652 | 4.3565 | 96.5922 | 7.9189 | 3504.0899 | 5.6891 | 8933.1786 | 4.5611 | 97.0096 | 7.919 | 3584.3268 | 5.6849 | 8851.8211 | 4.634 | 92.8272 | 7.9187 | 3549.1304 | 5.7787 | 8738.6652 | 4.3565 | 96.5922 | 4.0595 | 602.0802 | 6.17 | 5814.0029 | 6.2019 | 5759.2443 | 4.0595 | 602.0802 | 6.17 | 5814.0029 | 6.2019 | 5759.2443 | 5.0892 | 571.0339 | 7.2502 | 155.3796 | 5.0355 | 3377.4941 | 6.14 | 5992.7954 | 5.0892 | 571.0339 | 7.2502 | 155.3796 | 5.0355 | 3377.4941 | 6.14 | 5992.7954
7.9189 | 3504.0899 | 5.6891 | 8933.1786 | 4.5611 | 97.0096 | 7.919 | 3584.3268 | 5.6849 | 8851.8211 | 4.634 | 92.8272 | 7.9187 | 3549.1304 | 5.7787 | 8738.6652 | 4.3565 | 96.5922 | 7.9189 | 3504.0899 | 5.6891 | 8933.1786 | 4.5611 | 97.0096 | 7.919 | 3584.3268 | 5.6849 | 8851.8211 | 4.634 | 92.8272 | 7.9187 | 3549.1304 | 5.7787 | 8738.6652 | 4.3565 | 96.5922 | 4.0595 | 602.0802 | 6.17 | 5814.0029 | 6.2019 | 5759.2443 | 4.0595 | 602.0802 | 6.17 | 5814.0029 | 6.2019 | 5759.2443 | 5.0892 | 571.0339 | 7.2502 | 155.3796 | 5.0355 | 3377.4941 | 6.14 | 5992.7954 | 5.0892 | 571.0339 | 7.2502 | 155.3796 | 5.0355 | 3377.4941 | 6.14 | 5992.7954
7.9188 | 3552.0911 | 5.6185 | 9055.5509 | 4.4357 | 98.3385 | 7.919 | 3633.4272 | 5.6006 | 8973.0789 | 4.4911 | 94.0988 | 7.9187 | 3597.7486 | 5.7293 | 8858.3729 | 4.3491 | 97.9154 | 7.9188 | 3552.0911 | 5.6185 | 9055.5509 | 4.4357 | 98.3385 | 7.919 | 3633.4272 | 5.6006 | 8973.0789 | 4.4911 | 94.0988 | 7.9187 | 3597.7486 | 5.7293 | 8858.3729 | 4.3491 | 97.9154 |  |  | 6.1582 | 5893.6468 | 6.1845 | 5838.1381 |  |  | 6.1582 | 5893.6468 | 6.1845 | 5838.1381 | 4.9533 | 578.8563 | 7.2227 | 157.5081 | 5.0355 | 3423.7612 | 6.118 | 6074.8885 | 4.9533 | 578.8563 | 7.2227 | 157.5081 | 5.0355 | 3423.7612 | 6.118 | 6074.8885
7.9188 | 3552.0911 | 5.6185 | 9055.5509 | 4.4357 | 98.3385 | 7.919 | 3633.4272 | 5.6006 | 8973.0789 | 4.4911 | 94.0988 | 7.9187 | 3597.7486 | 5.7293 | 8858.3729 | 4.3491 | 97.9154 | 7.9188 | 3552.0911 | 5.6185 | 9055.5509 | 4.4357 | 98.3385 | 7.919 | 3633.4272 | 5.6006 | 8973.0789 | 4.4911 | 94.0988 | 7.9187 | 3597.7486 | 5.7293 | 8858.3729 | 4.3491 | 97.9154 |  |  | 6.1582 | 5893.6468 | 6.1845 | 5838.1381 |  |  | 6.1582 | 5893.6468 | 6.1845 | 5838.1381 | 4.9533 | 578.8563 | 7.2227 | 157.5081 | 5.0355 | 3423.7612 | 6.118 | 6074.8885 | 4.9533 | 578.8563 | 7.2227 | 157.5081 | 5.0355 | 3423.7612 | 6.118 | 6074.8885
7.9188 | 3600.0923 | 5.5764 | 9177.9232 | 4.3661 | 99.6674 | 7.919 | 3682.5276 | 5.5672 | 9094.3367 | 4.4663 | 95.3704 | 7.9187 | 3646.3669 | 5.659 | 8978.0806 | 4.2691 | 99.2386 | 7.9188 | 3600.0923 | 5.5764 | 9177.9232 | 4.3661 | 99.6674 | 7.919 | 3682.5276 | 5.5672 | 9094.3367 | 4.4663 | 95.3704 | 7.9187 | 3646.3669 | 5.659 | 8978.0806 | 4.2691 | 99.2386 |  |  | 6.1338 | 5973.2907 | 6.1738 | 5917.0318 |  |  | 6.1338 | 5973.2907 | 6.1738 | 5917.0318 | 4.9533 | 586.6787 | 7.1926 | 159.6366 | 5.0355 | 3470.0282 | 6.089 | 6156.9816 | 4.9533 | 586.6787 | 7.1926 | 159.6366 | 5.0355 | 3470.0282 | 6.089 | 6156.9816
7.9188 | 3600.0923 | 5.5764 | 9177.9232 | 4.3661 | 99.6674 | 7.919 | 3682.5276 | 5.5672 | 9094.3367 | 4.4663 | 95.3704 | 7.9187 | 3646.3669 | 5.659 | 8978.0806 | 4.2691 | 99.2386 | 7.9188 | 3600.0923 | 5.5764 | 9177.9232 | 4.3661 | 99.6674 | 7.919 | 3682.5276 | 5.5672 | 9094.3367 | 4.4663 | 95.3704 | 7.9187 | 3646.3669 | 5.659 | 8978.0806 | 4.2691 | 99.2386 |  |  | 6.1338 | 5973.2907 | 6.1738 | 5917.0318 |  |  | 6.1338 | 5973.2907 | 6.1738 | 5917.0318 | 4.9533 | 586.6787 | 7.1926 | 159.6366 | 5.0355 | 3470.0282 | 6.089 | 6156.9816 | 4.9533 | 586.6787 | 7.1926 | 159.6366 | 5.0355 | 3470.0282 | 6.089 | 6156.9816
7.9187 | 3648.0936 | 5.5361 | 9300.2955 | 4.3342 | 100.9963 | 7.9189 | 3731.628 | 5.4917 | 9215.5945 | 4.4572 | 96.642 | 7.9187 | 3694.9851 | 5.5569 | 9097.7884 | 4.2171 | 100.5618 | 7.9187 | 3648.0936 | 5.5361 | 9300.2955 | 4.3342 | 100.9963 | 7.9189 | 3731.628 | 5.4917 | 9215.5945 | 4.4572 | 96.642 | 7.9187 | 3694.9851 | 5.5569 | 9097.7884 | 4.2171 | 100.5618 |  |  | 6.1065 | 6052.9346 | 6.123 | 5995.9256 |  |  | 6.1065 | 6052.9346 | 6.123 | 5995.9256 | 4.9533 | 594.5011 | 7.1741 | 161.7651 | 5.0355 | 3516.2953 | 6.0564 | 6239.0747 | 4.9533 | 594.5011 | 7.1741 | 161.7651 | 5.0355 | 3516.2953 | 6.0564 | 6239.0747
7.9187 | 3648.0936 | 5.5361 | 9300.2955 | 4.3342 | 100.9963 | 7.9189 | 3731.628 | 5.4917 | 9215.5945 | 4.4572 | 96.642 | 7.9187 | 3694.9851 | 5.5569 | 9097.7884 | 4.2171 | 100.5618 | 7.9187 | 3648.0936 | 5.5361 | 9300.2955 | 4.3342 | 100.9963 | 7.9189 | 3731.628 | 5.4917 | 9215.5945 | 4.4572 | 96.642 | 7.9187 | 3694.9851 | 5.5569 | 9097.7884 | 4.2171 | 100.5618 |  |  | 6.1065 | 6052.9346 | 6.123 | 5995.9256 |  |  | 6.1065 | 6052.9346 | 6.123 | 5995.9256 | 4.9533 | 594.5011 | 7.1741 | 161.7651 | 5.0355 | 3516.2953 | 6.0564 | 6239.0747 | 4.9533 | 594.5011 | 7.1741 | 161.7651 | 5.0355 | 3516.2953 | 6.0564 | 6239.0747
7.9187 | 3696.0948 | 5.498 | 9422.6678 | 4.2894 | 102.3252 | 7.9189 | 3780.7283 | 5.4504 | 9336.8524 | 4.376 | 97.9136 | 7.9185 | 3743.6033 | 5.5208 | 9217.4961 | 4.2059 | 101.8849 | 7.9187 | 3696.0948 | 5.498 | 9422.6678 | 4.2894 | 102.3252 | 7.9189 | 3780.7283 | 5.4504 | 9336.8524 | 4.376 | 97.9136 | 7.9185 | 3743.6033 | 5.5208 | 9217.4961 | 4.2059 | 101.8849 |  |  | 6.0763 | 6132.5784 | 6.0979 | 6074.8193 |  |  | 6.0763 | 6132.5784 | 6.0979 | 6074.8193 | 4.8177 | 602.3235 | 7.1573 | 163.8936 | 4.9105 | 3562.5623 | 6.0303 | 6321.1678 | 4.8177 | 602.3235 | 7.1573 | 163.8936 | 4.9105 | 3562.5623 | 6.0303 | 6321.1678
7.9187 | 3696.0948 | 5.498 | 9422.6678 | 4.2894 | 102.3252 | 7.9189 | 3780.7283 | 5.4504 | 9336.8524 | 4.376 | 97.9136 | 7.9185 | 3743.6033 | 5.5208 | 9217.4961 | 4.2059 | 101.8849 | 7.9187 | 3696.0948 | 5.498 | 9422.6678 | 4.2894 | 102.3252 | 7.9189 | 3780.7283 | 5.4504 | 9336.8524 | 4.376 | 97.9136 | 7.9185 | 3743.6033 | 5.5208 | 9217.4961 | 4.2059 | 101.8849 |  |  | 6.0763 | 6132.5784 | 6.0979 | 6074.8193 |  |  | 6.0763 | 6132.5784 | 6.0979 | 6074.8193 | 4.8177 | 602.3235 | 7.1573 | 163.8936 | 4.9105 | 3562.5623 | 6.0303 | 6321.1678 | 4.8177 | 602.3235 | 7.1573 | 163.8936 | 4.9105 | 3562.5623 | 6.0303 | 6321.1678
7.9187 | 3744.096 | 5.3903 | 9545.0401 | 4.2602 | 103.6541 | 7.9189 | 3829.8287 | 5.3755 | 9458.1102 | 4.314 | 99.1852 | 7.9185 | 3792.2215 | 5.4365 | 9337.2039 | 4.1929 | 103.2081 | 7.9187 | 3744.096 | 5.3903 | 9545.0401 | 4.2602 | 103.6541 | 7.9189 | 3829.8287 | 5.3755 | 9458.1102 | 4.314 | 99.1852 | 7.9185 | 3792.2215 | 5.4365 | 9337.2039 | 4.1929 | 103.2081 |  |  | 6.0501 | 6212.2223 | 6.0741 | 6153.7131 |  |  | 6.0501 | 6212.2223 | 6.0741 | 6153.7131 | 4.5866 | 610.1459 | 7.1453 | 166.0221 | 4.9105 | 3608.8294 | 5.9932 | 6403.2608 | 4.5866 | 610.1459 | 7.1453 | 166.0221 | 4.9105 | 3608.8294 | 5.9932 | 6403.2608
7.9187 | 3744.096 | 5.3903 | 9545.0401 | 4.2602 | 103.6541 | 7.9189 | 3829.8287 | 5.3755 | 9458.1102 | 4.314 | 99.1852 | 7.9185 | 3792.2215 | 5.4365 | 9337.2039 | 4.1929 | 103.2081 | 7.9187 | 3744.096 | 5.3903 | 9545.0401 | 4.2602 | 103.6541 | 7.9189 | 3829.8287 | 5.3755 | 9458.1102 | 4.314 | 99.1852 | 7.9185 | 3792.2215 | 5.4365 | 9337.2039 | 4.1929 | 103.2081 |  |  | 6.0501 | 6212.2223 | 6.0741 | 6153.7131 |  |  | 6.0501 | 6212.2223 | 6.0741 | 6153.7131 | 4.5866 | 610.1459 | 7.1453 | 166.0221 | 4.9105 | 3608.8294 | 5.9932 | 6403.2608 | 4.5866 | 610.1459 | 7.1453 | 166.0221 | 4.9105 | 3608.8294 | 5.9932 | 6403.2608
7.9187 | 3792.0973 | 5.3465 | 9667.4124 | 4.1831 | 104.983 | 7.9189 | 3878.9291 | 5.3638 | 9579.368 | 4.2626 | 100.4568 | 7.9184 | 3840.8398 | 5.3973 | 9456.9116 | 4.0765 | 104.5313 | 7.9187 | 3792.0973 | 5.3465 | 9667.4124 | 4.1831 | 104.983 | 7.9189 | 3878.9291 | 5.3638 | 9579.368 | 4.2626 | 100.4568 | 7.9184 | 3840.8398 | 5.3973 | 9456.9116 | 4.0765 | 104.5313 |  |  | 6.0426 | 6291.8662 | 6.0239 | 6232.6069 |  |  | 6.0426 | 6291.8662 | 6.0239 | 6232.6069 | 4.5866 | 617.9682 | 7.128 | 168.1506 | 4.9105 | 3655.0964 | 5.9825 | 6485.3539 | 4.5866 | 617.9682 | 7.128 | 168.1506 | 4.9105 | 3655.0964 | 5.9825 | 6485.3539
7.9187 | 3792.0973 | 5.3465 | 9667.4124 | 4.1831 | 104.983 | 7.9189 | 3878.9291 | 5.3638 | 9579.368 | 4.2626 | 100.4568 | 7.9184 | 3840.8398 | 5.3973 | 9456.9116 | 4.0765 | 104.5313 | 7.9187 | 3792.0973 | 5.3465 | 9667.4124 | 4.1831 | 104.983 | 7.9189 | 3878.9291 | 5.3638 | 9579.368 | 4.2626 | 100.4568 | 7.9184 | 3840.8398 | 5.3973 | 9456.9116 | 4.0765 | 104.5313 |  |  | 6.0426 | 6291.8662 | 6.0239 | 6232.6069 |  |  | 6.0426 | 6291.8662 | 6.0239 | 6232.6069 | 4.5866 | 617.9682 | 7.128 | 168.1506 | 4.9105 | 3655.0964 | 5.9825 | 6485.3539 | 4.5866 | 617.9682 | 7.128 | 168.1506 | 4.9105 | 3655.0964 | 5.9825 | 6485.3539
7.9187 | 3840.0985 | 5.3366 | 9789.7847 | 4.1145 | 106.3119 | 7.9187 | 3928.0294 | 5.3009 | 9700.6258 | 4.2446 | 101.7284 | 7.9184 | 3889.458 | 5.322 | 9576.6194 | 4.0229 | 105.8545 | 7.9187 | 3840.0985 | 5.3366 | 9789.7847 | 4.1145 | 106.3119 | 7.9187 | 3928.0294 | 5.3009 | 9700.6258 | 4.2446 | 101.7284 | 7.9184 | 3889.458 | 5.322 | 9576.6194 | 4.0229 | 105.8545 |  |  | 6.0058 | 6371.5101 | 6.0175 | 6311.5006 |  |  | 6.0058 | 6371.5101 | 6.0175 | 6311.5006 | 4.5866 | 625.7906 | 7.1124 | 170.279 | 4.9105 | 3701.3634 | 5.9452 | 6567.447 | 4.5866 | 625.7906 | 7.1124 | 170.279 | 4.9105 | 3701.3634 | 5.9452 | 6567.447
7.9187 | 3840.0985 | 5.3366 | 9789.7847 | 4.1145 | 106.3119 | 7.9187 | 3928.0294 | 5.3009 | 9700.6258 | 4.2446 | 101.7284 | 7.9184 | 3889.458 | 5.322 | 9576.6194 | 4.0229 | 105.8545 | 7.9187 | 3840.0985 | 5.3366 | 9789.7847 | 4.1145 | 106.3119 | 7.9187 | 3928.0294 | 5.3009 | 9700.6258 | 4.2446 | 101.7284 | 7.9184 | 3889.458 | 5.322 | 9576.6194 | 4.0229 | 105.8545 |  |  | 6.0058 | 6371.5101 | 6.0175 | 6311.5006 |  |  | 6.0058 | 6371.5101 | 6.0175 | 6311.5006 | 4.5866 | 625.7906 | 7.1124 | 170.279 | 4.9105 | 3701.3634 | 5.9452 | 6567.447 | 4.5866 | 625.7906 | 7.1124 | 170.279 | 4.9105 | 3701.3634 | 5.9452 | 6567.447
7.9187 | 3888.0997 | 5.2982 | 9912.157 | 4.081 | 107.6408 | 7.9186 | 3977.1298 | 5.2588 | 9821.8837 | 4.204 | 103 | 7.9184 | 3938.0762 | 5.2787 | 9696.3271 | 3.8264 | 107.1777 | 7.9187 | 3888.0997 | 5.2982 | 9912.157 | 4.081 | 107.6408 | 7.9186 | 3977.1298 | 5.2588 | 9821.8837 | 4.204 | 103 | 7.9184 | 3938.0762 | 5.2787 | 9696.3271 | 3.8264 | 107.1777 |  |  | 5.9685 | 6451.1539 | 6.0025 | 6390.3944 |  |  | 5.9685 | 6451.1539 | 6.0025 | 6390.3944 | 4.0595 | 633.613 | 7.1046 | 172.4075 | 4.9105 | 3747.6305 | 5.875 | 6649.5401 | 4.0595 | 633.613 | 7.1046 | 172.4075 | 4.9105 | 3747.6305 | 5.875 | 6649.5401
7.9187 | 3888.0997 | 5.2982 | 9912.157 | 4.081 | 107.6408 | 7.9186 | 3977.1298 | 5.2588 | 9821.8837 | 4.204 | 103 | 7.9184 | 3938.0762 | 5.2787 | 9696.3271 | 3.8264 | 107.1777 | 7.9187 | 3888.0997 | 5.2982 | 9912.157 | 4.081 | 107.6408 | 7.9186 | 3977.1298 | 5.2588 | 9821.8837 | 4.204 | 103 | 7.9184 | 3938.0762 | 5.2787 | 9696.3271 | 3.8264 | 107.1777 |  |  | 5.9685 | 6451.1539 | 6.0025 | 6390.3944 |  |  | 5.9685 | 6451.1539 | 6.0025 | 6390.3944 | 4.0595 | 633.613 | 7.1046 | 172.4075 | 4.9105 | 3747.6305 | 5.875 | 6649.5401 | 4.0595 | 633.613 | 7.1046 | 172.4075 | 4.9105 | 3747.6305 | 5.875 | 6649.5401
7.9187 | 3936.101 | 5.2134 | 10034.5293 | 4.0291 | 108.9697 | 7.9186 | 4026.2302 | 5.2395 | 9943.1415 | 4.1576 | 104.2716 | 7.9184 | 3986.6944 | 5.2093 | 9816.0348 | 3.7908 | 108.5009 | 7.9187 | 3936.101 | 5.2134 | 10034.5293 | 4.0291 | 108.9697 | 7.9186 | 4026.2302 | 5.2395 | 9943.1415 | 4.1576 | 104.2716 | 7.9184 | 3986.6944 | 5.2093 | 9816.0348 | 3.7908 | 108.5009 |  |  | 5.9386 | 6530.7978 | 5.9802 | 6469.2881 |  |  | 5.9386 | 6530.7978 | 5.9802 | 6469.2881 |  |  | 7.0896 | 174.536 | 4.4334 | 3793.8975 | 5.8499 | 6731.6332 |  |  | 7.0896 | 174.536 | 4.4334 | 3793.8975 | 5.8499 | 6731.6332
7.9187 | 3936.101 | 5.2134 | 10034.5293 | 4.0291 | 108.9697 | 7.9186 | 4026.2302 | 5.2395 | 9943.1415 | 4.1576 | 104.2716 | 7.9184 | 3986.6944 | 5.2093 | 9816.0348 | 3.7908 | 108.5009 | 7.9187 | 3936.101 | 5.2134 | 10034.5293 | 4.0291 | 108.9697 | 7.9186 | 4026.2302 | 5.2395 | 9943.1415 | 4.1576 | 104.2716 | 7.9184 | 3986.6944 | 5.2093 | 9816.0348 | 3.7908 | 108.5009 |  |  | 5.9386 | 6530.7978 | 5.9802 | 6469.2881 |  |  | 5.9386 | 6530.7978 | 5.9802 | 6469.2881 |  |  | 7.0896 | 174.536 | 4.4334 | 3793.8975 | 5.8499 | 6731.6332 |  |  | 7.0896 | 174.536 | 4.4334 | 3793.8975 | 5.8499 | 6731.6332
7.9187 | 3984.1022 | 5.1413 | 10156.9016 | 3.9494 | 110.2986 | 7.9186 | 4075.3305 | 5.1911 | 10064.3993 | 4.0797 | 105.5432 | 7.9184 | 4035.3127 | 5.1484 | 9935.7426 | 3.7854 | 109.824 | 7.9187 | 3984.1022 | 5.1413 | 10156.9016 | 3.9494 | 110.2986 | 7.9186 | 4075.3305 | 5.1911 | 10064.3993 | 4.0797 | 105.5432 | 7.9184 | 4035.3127 | 5.1484 | 9935.7426 | 3.7854 | 109.824 |  |  | 5.9041 | 6610.4417 | 5.9188 | 6548.1819 |  |  | 5.9041 | 6610.4417 | 5.9188 | 6548.1819 |  |  | 7.0728 | 176.6645 | 4.7345 | 3768.8593 | 5.8271 | 6813.7263 |  |  | 7.0728 | 176.6645 | 4.7345 | 3768.8593 | 5.8271 | 6813.7263
7.9187 | 3984.1022 | 5.1413 | 10156.9016 | 3.9494 | 110.2986 | 7.9186 | 4075.3305 | 5.1911 | 10064.3993 | 4.0797 | 105.5432 | 7.9184 | 4035.3127 | 5.1484 | 9935.7426 | 3.7854 | 109.824 | 7.9187 | 3984.1022 | 5.1413 | 10156.9016 | 3.9494 | 110.2986 | 7.9186 | 4075.3305 | 5.1911 | 10064.3993 | 4.0797 | 105.5432 | 7.9184 | 4035.3127 | 5.1484 | 9935.7426 | 3.7854 | 109.824 |  |  | 5.9041 | 6610.4417 | 5.9188 | 6548.1819 |  |  | 5.9041 | 6610.4417 | 5.9188 | 6548.1819 |  |  | 7.0728 | 176.6645 | 4.7345 | 3768.8593 | 5.8271 | 6813.7263 |  |  | 7.0728 | 176.6645 | 4.7345 | 3768.8593 | 5.8271 | 6813.7263
7.9187 | 4032.1034 | 5.0955 | 10279.274 | 3.8481 | 111.6275 | 7.9186 | 4124.4309 | 5.092 | 10185.6571 | 3.998 | 106.8148 | 7.9184 | 4083.9309 | 5.1418 | 10055.4503 | 3.7745 | 111.1472 | 7.9187 | 4032.1034 | 5.0955 | 10279.274 | 3.8481 | 111.6275 | 7.9186 | 4124.4309 | 5.092 | 10185.6571 | 3.998 | 106.8148 | 7.9184 | 4083.9309 | 5.1418 | 10055.4503 | 3.7745 | 111.1472 |  |  | 5.8631 | 6690.0856 | 5.8929 | 6627.0756 |  |  | 5.8631 | 6690.0856 | 5.8929 | 6627.0756 |  |  | 7.052 | 178.793 | 4.4334 | 3814.2673 | 5.8233 | 6895.8194 |  |  | 7.052 | 178.793 | 4.4334 | 3814.2673 | 5.8233 | 6895.8194
7.9187 | 4032.1034 | 5.0955 | 10279.274 | 3.8481 | 111.6275 | 7.9186 | 4124.4309 | 5.092 | 10185.6571 | 3.998 | 106.8148 | 7.9184 | 4083.9309 | 5.1418 | 10055.4503 | 3.7745 | 111.1472 | 7.9187 | 4032.1034 | 5.0955 | 10279.274 | 3.8481 | 111.6275 | 7.9186 | 4124.4309 | 5.092 | 10185.6571 | 3.998 | 106.8148 | 7.9184 | 4083.9309 | 5.1418 | 10055.4503 | 3.7745 | 111.1472 |  |  | 5.8631 | 6690.0856 | 5.8929 | 6627.0756 |  |  | 5.8631 | 6690.0856 | 5.8929 | 6627.0756 |  |  | 7.052 | 178.793 | 4.4334 | 3814.2673 | 5.8233 | 6895.8194 |  |  | 7.052 | 178.793 | 4.4334 | 3814.2673 | 5.8233 | 6895.8194
7.9187 | 4080.1046 | 5.0189 | 10401.6463 | 3.8326 | 112.9564 | 7.9186 | 4173.5313 | 5.0685 | 10306.915 | 3.9314 | 108.0864 | 7.9184 | 4132.5491 | 5.0835 | 10175.1581 | 3.7185 | 112.4704 | 7.9187 | 4080.1046 | 5.0189 | 10401.6463 | 3.8326 | 112.9564 | 7.9186 | 4173.5313 | 5.0685 | 10306.915 | 3.9314 | 108.0864 | 7.9184 | 4132.5491 | 5.0835 | 10175.1581 | 3.7185 | 112.4704 |  |  | 5.8314 | 6769.7295 | 5.8312 | 6705.9694 |  |  | 5.8314 | 6769.7295 | 5.8312 | 6705.9694 |  |  | 7.0447 | 180.9215 |  |  | 5.8002 | 6977.9125 |  |  | 7.0447 | 180.9215 |  |  | 5.8002 | 6977.9125
7.9187 | 4080.1046 | 5.0189 | 10401.6463 | 3.8326 | 112.9564 | 7.9186 | 4173.5313 | 5.0685 | 10306.915 | 3.9314 | 108.0864 | 7.9184 | 4132.5491 | 5.0835 | 10175.1581 | 3.7185 | 112.4704 | 7.9187 | 4080.1046 | 5.0189 | 10401.6463 | 3.8326 | 112.9564 | 7.9186 | 4173.5313 | 5.0685 | 10306.915 | 3.9314 | 108.0864 | 7.9184 | 4132.5491 | 5.0835 | 10175.1581 | 3.7185 | 112.4704 |  |  | 5.8314 | 6769.7295 | 5.8312 | 6705.9694 |  |  | 5.8314 | 6769.7295 | 5.8312 | 6705.9694 |  |  | 7.0447 | 180.9215 |  |  | 5.8002 | 6977.9125 |  |  | 7.0447 | 180.9215 |  |  | 5.8002 | 6977.9125
7.9187 | 4128.1059 | 4.9859 | 10524.0186 | 3.7464 | 114.2853 | 7.9185 | 4222.6316 | 5.0463 | 10428.1728 | 3.9025 | 109.358 | 7.9184 | 4181.1673 | 5.0764 | 10294.8658 | 3.6353 | 113.7936 | 7.9187 | 4128.1059 | 4.9859 | 10524.0186 | 3.7464 | 114.2853 | 7.9185 | 4222.6316 | 5.0463 | 10428.1728 | 3.9025 | 109.358 | 7.9184 | 4181.1673 | 5.0764 | 10294.8658 | 3.6353 | 113.7936 |  |  | 5.7988 | 6849.3733 | 5.7812 | 6784.8632 |  |  | 5.7988 | 6849.3733 | 5.7812 | 6784.8632 |  |  | 7.0252 | 183.05 |  |  | 5.7759 | 7060.0056 |  |  | 7.0252 | 183.05 |  |  | 5.7759 | 7060.0056
7.9187 | 4128.1059 | 4.9859 | 10524.0186 | 3.7464 | 114.2853 | 7.9185 | 4222.6316 | 5.0463 | 10428.1728 | 3.9025 | 109.358 | 7.9184 | 4181.1673 | 5.0764 | 10294.8658 | 3.6353 | 113.7936 | 7.9187 | 4128.1059 | 4.9859 | 10524.0186 | 3.7464 | 114.2853 | 7.9185 | 4222.6316 | 5.0463 | 10428.1728 | 3.9025 | 109.358 | 7.9184 | 4181.1673 | 5.0764 | 10294.8658 | 3.6353 | 113.7936 |  |  | 5.7988 | 6849.3733 | 5.7812 | 6784.8632 |  |  | 5.7988 | 6849.3733 | 5.7812 | 6784.8632 |  |  | 7.0252 | 183.05 |  |  | 5.7759 | 7060.0056 |  |  | 7.0252 | 183.05 |  |  | 5.7759 | 7060.0056
7.9187 | 4176.1071 | 4.9309 | 10646.3909 | 3.7252 | 115.6142 | 7.9184 | 4271.732 | 5.0368 | 10549.4306 | 3.8383 | 110.6296 | 7.9184 | 4229.7855 | 4.8742 | 10414.5736 | 3.563 | 115.1168 | 7.9187 | 4176.1071 | 4.9309 | 10646.3909 | 3.7252 | 115.6142 | 7.9184 | 4271.732 | 5.0368 | 10549.4306 | 3.8383 | 110.6296 | 7.9184 | 4229.7855 | 4.8742 | 10414.5736 | 3.563 | 115.1168 |  |  | 5.7927 | 6929.0172 | 5.7625 | 6863.7569 |  |  | 5.7927 | 6929.0172 | 5.7625 | 6863.7569 |  |  | 7.0068 | 185.1785 |  |  | 5.7348 | 7142.0986 |  |  | 7.0068 | 185.1785 |  |  | 5.7348 | 7142.0986
7.9187 | 4176.1071 | 4.9309 | 10646.3909 | 3.7252 | 115.6142 | 7.9184 | 4271.732 | 5.0368 | 10549.4306 | 3.8383 | 110.6296 | 7.9184 | 4229.7855 | 4.8742 | 10414.5736 | 3.563 | 115.1168 | 7.9187 | 4176.1071 | 4.9309 | 10646.3909 | 3.7252 | 115.6142 | 7.9184 | 4271.732 | 5.0368 | 10549.4306 | 3.8383 | 110.6296 | 7.9184 | 4229.7855 | 4.8742 | 10414.5736 | 3.563 | 115.1168 |  |  | 5.7927 | 6929.0172 | 5.7625 | 6863.7569 |  |  | 5.7927 | 6929.0172 | 5.7625 | 6863.7569 |  |  | 7.0068 | 185.1785 |  |  | 5.7348 | 7142.0986 |  |  | 7.0068 | 185.1785 |  |  | 5.7348 | 7142.0986
7.9187 | 4224.1083 | 4.8806 | 10768.7632 | 3.6947 | 116.9431 | 7.9184 | 4320.8324 | 4.9647 | 10670.6884 | 3.7517 | 111.9012 | 7.9184 | 4278.4038 | 4.8535 | 10534.2813 | 3.5493 | 116.4399 | 7.9187 | 4224.1083 | 4.8806 | 10768.7632 | 3.6947 | 116.9431 | 7.9184 | 4320.8324 | 4.9647 | 10670.6884 | 3.7517 | 111.9012 | 7.9184 | 4278.4038 | 4.8535 | 10534.2813 | 3.5493 | 116.4399 |  |  | 5.7838 | 7008.6611 | 5.7374 | 6942.6507 |  |  | 5.7838 | 7008.6611 | 5.7374 | 6942.6507 |  |  | 6.9914 | 187.3069 |  |  | 5.6936 | 7224.1917 |  |  | 6.9914 | 187.3069 |  |  | 5.6936 | 7224.1917
7.9187 | 4224.1083 | 4.8806 | 10768.7632 | 3.6947 | 116.9431 | 7.9184 | 4320.8324 | 4.9647 | 10670.6884 | 3.7517 | 111.9012 | 7.9184 | 4278.4038 | 4.8535 | 10534.2813 | 3.5493 | 116.4399 | 7.9187 | 4224.1083 | 4.8806 | 10768.7632 | 3.6947 | 116.9431 | 7.9184 | 4320.8324 | 4.9647 | 10670.6884 | 3.7517 | 111.9012 | 7.9184 | 4278.4038 | 4.8535 | 10534.2813 | 3.5493 | 116.4399 |  |  | 5.7838 | 7008.6611 | 5.7374 | 6942.6507 |  |  | 5.7838 | 7008.6611 | 5.7374 | 6942.6507 |  |  | 6.9914 | 187.3069 |  |  | 5.6936 | 7224.1917 |  |  | 6.9914 | 187.3069 |  |  | 5.6936 | 7224.1917
7.9185 | 4272.1096 | 4.819 | 10891.1355 | 3.6707 | 118.272 | 7.9184 | 4369.9327 | 4.9643 | 10791.9462 | 3.6958 | 113.1729 | 7.9184 | 4327.022 | 4.8156 | 10653.989 | 3.5278 | 117.7631 | 7.9185 | 4272.1096 | 4.819 | 10891.1355 | 3.6707 | 118.272 | 7.9184 | 4369.9327 | 4.9643 | 10791.9462 | 3.6958 | 113.1729 | 7.9184 | 4327.022 | 4.8156 | 10653.989 | 3.5278 | 117.7631 |  |  | 5.7554 | 7088.305 | 5.7188 | 7021.5444 |  |  | 5.7554 | 7088.305 | 5.7188 | 7021.5444 |  |  | 6.9766 | 189.4354 |  |  | 5.681 | 7306.2848 |  |  | 6.9766 | 189.4354 |  |  | 5.681 | 7306.2848
7.9185 | 4272.1096 | 4.819 | 10891.1355 | 3.6707 | 118.272 | 7.9184 | 4369.9327 | 4.9643 | 10791.9462 | 3.6958 | 113.1729 | 7.9184 | 4327.022 | 4.8156 | 10653.989 | 3.5278 | 117.7631 | 7.9185 | 4272.1096 | 4.819 | 10891.1355 | 3.6707 | 118.272 | 7.9184 | 4369.9327 | 4.9643 | 10791.9462 | 3.6958 | 113.1729 | 7.9184 | 4327.022 | 4.8156 | 10653.989 | 3.5278 | 117.7631 |  |  | 5.7554 | 7088.305 | 5.7188 | 7021.5444 |  |  | 5.7554 | 7088.305 | 5.7188 | 7021.5444 |  |  | 6.9766 | 189.4354 |  |  | 5.681 | 7306.2848 |  |  | 6.9766 | 189.4354 |  |  | 5.681 | 7306.2848
7.9185 | 4320.1108 | 4.7721 | 11013.5078 | 3.5095 | 119.6009 | 7.9184 | 4419.0331 | 4.8794 | 10913.2041 | 3.6594 | 114.4445 | 7.9184 | 4375.6402 | 4.7088 | 10773.6968 | 3.473 | 119.0863 | 7.9185 | 4320.1108 | 4.7721 | 11013.5078 | 3.5095 | 119.6009 | 7.9184 | 4419.0331 | 4.8794 | 10913.2041 | 3.6594 | 114.4445 | 7.9184 | 4375.6402 | 4.7088 | 10773.6968 | 3.473 | 119.0863 |  |  | 5.7318 | 7167.9488 | 5.7047 | 7100.4382 |  |  | 5.7318 | 7167.9488 | 5.7047 | 7100.4382 |  |  | 6.9536 | 191.5639 |  |  | 5.6787 | 7388.3779 |  |  | 6.9536 | 191.5639 |  |  | 5.6787 | 7388.3779
7.9185 | 4320.1108 | 4.7721 | 11013.5078 | 3.5095 | 119.6009 | 7.9184 | 4419.0331 | 4.8794 | 10913.2041 | 3.6594 | 114.4445 | 7.9184 | 4375.6402 | 4.7088 | 10773.6968 | 3.473 | 119.0863 | 7.9185 | 4320.1108 | 4.7721 | 11013.5078 | 3.5095 | 119.6009 | 7.9184 | 4419.0331 | 4.8794 | 10913.2041 | 3.6594 | 114.4445 | 7.9184 | 4375.6402 | 4.7088 | 10773.6968 | 3.473 | 119.0863 |  |  | 5.7318 | 7167.9488 | 5.7047 | 7100.4382 |  |  | 5.7318 | 7167.9488 | 5.7047 | 7100.4382 |  |  | 6.9536 | 191.5639 |  |  | 5.6787 | 7388.3779 |  |  | 6.9536 | 191.5639 |  |  | 5.6787 | 7388.3779
7.9185 | 4368.112 | 4.6785 | 11135.8801 | 3.5095 | 120.9298 | 7.9184 | 4468.1335 | 4.8177 | 11034.4619 | 3.6217 | 115.7161 | 7.9182 | 4424.2584 | 4.6927 | 10893.4045 | 3.473 | 120.4095 | 7.9185 | 4368.112 | 4.6785 | 11135.8801 | 3.5095 | 120.9298 | 7.9184 | 4468.1335 | 4.8177 | 11034.4619 | 3.6217 | 115.7161 | 7.9182 | 4424.2584 | 4.6927 | 10893.4045 | 3.473 | 120.4095 |  |  | 5.6985 | 7247.5927 | 5.696 | 7179.332 |  |  | 5.6985 | 7247.5927 | 5.696 | 7179.332 |  |  | 6.9359 | 193.6924 |  |  | 5.6361 | 7470.471 |  |  | 6.9359 | 193.6924 |  |  | 5.6361 | 7470.471
7.9185 | 4368.112 | 4.6785 | 11135.8801 | 3.5095 | 120.9298 | 7.9184 | 4468.1335 | 4.8177 | 11034.4619 | 3.6217 | 115.7161 | 7.9182 | 4424.2584 | 4.6927 | 10893.4045 | 3.473 | 120.4095 | 7.9185 | 4368.112 | 4.6785 | 11135.8801 | 3.5095 | 120.9298 | 7.9184 | 4468.1335 | 4.8177 | 11034.4619 | 3.6217 | 115.7161 | 7.9182 | 4424.2584 | 4.6927 | 10893.4045 | 3.473 | 120.4095 |  |  | 5.6985 | 7247.5927 | 5.696 | 7179.332 |  |  | 5.6985 | 7247.5927 | 5.696 | 7179.332 |  |  | 6.9359 | 193.6924 |  |  | 5.6361 | 7470.471 |  |  | 6.9359 | 193.6924 |  |  | 5.6361 | 7470.471
7.9185 | 4416.1133 | 4.6778 | 11258.2524 | 3.3868 | 122.2587 | 7.9183 | 4517.2338 | 4.8168 | 11155.7197 | 3.6057 | 116.9877 | 7.9182 | 4472.8767 | 4.6863 | 11013.1123 | 3.4322 | 121.7327 | 7.9185 | 4416.1133 | 4.6778 | 11258.2524 | 3.3868 | 122.2587 | 7.9183 | 4517.2338 | 4.8168 | 11155.7197 | 3.6057 | 116.9877 | 7.9182 | 4472.8767 | 4.6863 | 11013.1123 | 3.4322 | 121.7327 |  |  | 5.6832 | 7327.2366 | 5.6846 | 7258.2257 |  |  | 5.6832 | 7327.2366 | 5.6846 | 7258.2257 |  |  | 6.9112 | 195.8209 |  |  | 5.6339 | 7552.5641 |  |  | 6.9112 | 195.8209 |  |  | 5.6339 | 7552.5641
7.9185 | 4416.1133 | 4.6778 | 11258.2524 | 3.3868 | 122.2587 | 7.9183 | 4517.2338 | 4.8168 | 11155.7197 | 3.6057 | 116.9877 | 7.9182 | 4472.8767 | 4.6863 | 11013.1123 | 3.4322 | 121.7327 | 7.9185 | 4416.1133 | 4.6778 | 11258.2524 | 3.3868 | 122.2587 | 7.9183 | 4517.2338 | 4.8168 | 11155.7197 | 3.6057 | 116.9877 | 7.9182 | 4472.8767 | 4.6863 | 11013.1123 | 3.4322 | 121.7327 |  |  | 5.6832 | 7327.2366 | 5.6846 | 7258.2257 |  |  | 5.6832 | 7327.2366 | 5.6846 | 7258.2257 |  |  | 6.9112 | 195.8209 |  |  | 5.6339 | 7552.5641 |  |  | 6.9112 | 195.8209 |  |  | 5.6339 | 7552.5641
7.9185 | 4464.1145 | 4.675 | 11380.6247 | 3.2891 | 123.5876 | 7.9183 | 4566.3342 | 4.6972 | 11276.9775 | 3.5446 | 118.2593 | 7.9182 | 4521.4949 | 4.6791 | 11132.82 | 3.4136 | 123.0558 | 7.9185 | 4464.1145 | 4.675 | 11380.6247 | 3.2891 | 123.5876 | 7.9183 | 4566.3342 | 4.6972 | 11276.9775 | 3.5446 | 118.2593 | 7.9182 | 4521.4949 | 4.6791 | 11132.82 | 3.4136 | 123.0558 |  |  | 5.676 | 7406.8805 | 5.6816 | 7337.1195 |  |  | 5.676 | 7406.8805 | 5.6816 | 7337.1195 |  |  | 6.889 | 197.9494 |  |  | 5.5922 | 7634.6572 |  |  | 6.889 | 197.9494 |  |  | 5.5922 | 7634.6572
7.9185 | 4464.1145 | 4.675 | 11380.6247 | 3.2891 | 123.5876 | 7.9183 | 4566.3342 | 4.6972 | 11276.9775 | 3.5446 | 118.2593 | 7.9182 | 4521.4949 | 4.6791 | 11132.82 | 3.4136 | 123.0558 | 7.9185 | 4464.1145 | 4.675 | 11380.6247 | 3.2891 | 123.5876 | 7.9183 | 4566.3342 | 4.6972 | 11276.9775 | 3.5446 | 118.2593 | 7.9182 | 4521.4949 | 4.6791 | 11132.82 | 3.4136 | 123.0558 |  |  | 5.676 | 7406.8805 | 5.6816 | 7337.1195 |  |  | 5.676 | 7406.8805 | 5.6816 | 7337.1195 |  |  | 6.889 | 197.9494 |  |  | 5.5922 | 7634.6572 |  |  | 6.889 | 197.9494 |  |  | 5.5922 | 7634.6572
7.9185 | 4512.1157 | 4.644 | 11502.997 | 3.2153 | 124.9165 | 7.9183 | 4615.4346 | 4.6822 | 11398.2354 | 3.5278 | 119.5309 | 7.9182 | 4570.1131 | 4.6734 | 11252.5277 | 3.294 | 124.379 | 7.9185 | 4512.1157 | 4.644 | 11502.997 | 3.2153 | 124.9165 | 7.9183 | 4615.4346 | 4.6822 | 11398.2354 | 3.5278 | 119.5309 | 7.9182 | 4570.1131 | 4.6734 | 11252.5277 | 3.294 | 124.379 |  |  | 5.6229 | 7486.5243 | 5.6776 | 7416.0132 |  |  | 5.6229 | 7486.5243 | 5.6776 | 7416.0132 |  |  | 6.8777 | 200.0779 |  |  | 5.562 | 7716.7503 |  |  | 6.8777 | 200.0779 |  |  | 5.562 | 7716.7503
7.9185 | 4512.1157 | 4.644 | 11502.997 | 3.2153 | 124.9165 | 7.9183 | 4615.4346 | 4.6822 | 11398.2354 | 3.5278 | 119.5309 | 7.9182 | 4570.1131 | 4.6734 | 11252.5277 | 3.294 | 124.379 | 7.9185 | 4512.1157 | 4.644 | 11502.997 | 3.2153 | 124.9165 | 7.9183 | 4615.4346 | 4.6822 | 11398.2354 | 3.5278 | 119.5309 | 7.9182 | 4570.1131 | 4.6734 | 11252.5277 | 3.294 | 124.379 |  |  | 5.6229 | 7486.5243 | 5.6776 | 7416.0132 |  |  | 5.6229 | 7486.5243 | 5.6776 | 7416.0132 |  |  | 6.8777 | 200.0779 |  |  | 5.562 | 7716.7503 |  |  | 6.8777 | 200.0779 |  |  | 5.562 | 7716.7503
7.9185 | 4560.117 | 4.6308 | 11625.3694 | 3.2153 | 126.2454 | 7.9183 | 4664.5349 | 4.6653 | 11519.4932 | 3.4651 | 120.8025 | 7.9182 | 4618.7313 | 4.5871 | 11372.2355 | 3.1803 | 125.7022 | 7.9185 | 4560.117 | 4.6308 | 11625.3694 | 3.2153 | 126.2454 | 7.9183 | 4664.5349 | 4.6653 | 11519.4932 | 3.4651 | 120.8025 | 7.9182 | 4618.7313 | 4.5871 | 11372.2355 | 3.1803 | 125.7022 |  |  | 5.606 | 7566.1682 | 5.6491 | 7494.907 |  |  | 5.606 | 7566.1682 | 5.6491 | 7494.907 |  |  | 6.8688 | 202.2064 |  |  | 5.547 | 7798.8433 |  |  | 6.8688 | 202.2064 |  |  | 5.547 | 7798.8433
7.9185 | 4560.117 | 4.6308 | 11625.3694 | 3.2153 | 126.2454 | 7.9183 | 4664.5349 | 4.6653 | 11519.4932 | 3.4651 | 120.8025 | 7.9182 | 4618.7313 | 4.5871 | 11372.2355 | 3.1803 | 125.7022 | 7.9185 | 4560.117 | 4.6308 | 11625.3694 | 3.2153 | 126.2454 | 7.9183 | 4664.5349 | 4.6653 | 11519.4932 | 3.4651 | 120.8025 | 7.9182 | 4618.7313 | 4.5871 | 11372.2355 | 3.1803 | 125.7022 |  |  | 5.606 | 7566.1682 | 5.6491 | 7494.907 |  |  | 5.606 | 7566.1682 | 5.6491 | 7494.907 |  |  | 6.8688 | 202.2064 |  |  | 5.547 | 7798.8433 |  |  | 6.8688 | 202.2064 |  |  | 5.547 | 7798.8433
7.9185 | 4608.1182 | 4.629 | 11747.7417 |  |  | 7.9181 | 4713.6353 | 4.6034 | 11640.751 | 3.3496 | 122.0741 | 7.9182 | 4667.3496 | 4.5488 | 11491.9432 | 3.1803 | 127.0254 | 7.9185 | 4608.1182 | 4.629 | 11747.7417 |  |  | 7.9181 | 4713.6353 | 4.6034 | 11640.751 | 3.3496 | 122.0741 | 7.9182 | 4667.3496 | 4.5488 | 11491.9432 | 3.1803 | 127.0254 |  |  | 5.5903 | 7645.8121 | 5.6328 | 7573.8007 |  |  | 5.5903 | 7645.8121 | 5.6328 | 7573.8007 |  |  | 6.8406 | 204.3349 |  |  | 5.5421 | 7880.9364 |  |  | 6.8406 | 204.3349 |  |  | 5.5421 | 7880.9364
7.9185 | 4608.1182 | 4.629 | 11747.7417 |  |  | 7.9181 | 4713.6353 | 4.6034 | 11640.751 | 3.3496 | 122.0741 | 7.9182 | 4667.3496 | 4.5488 | 11491.9432 | 3.1803 | 127.0254 | 7.9185 | 4608.1182 | 4.629 | 11747.7417 |  |  | 7.9181 | 4713.6353 | 4.6034 | 11640.751 | 3.3496 | 122.0741 | 7.9182 | 4667.3496 | 4.5488 | 11491.9432 | 3.1803 | 127.0254 |  |  | 5.5903 | 7645.8121 | 5.6328 | 7573.8007 |  |  | 5.5903 | 7645.8121 | 5.6328 | 7573.8007 |  |  | 6.8406 | 204.3349 |  |  | 5.5421 | 7880.9364 |  |  | 6.8406 | 204.3349 |  |  | 5.5421 | 7880.9364
7.9185 | 4656.1194 | 4.5436 | 11870.114 |  |  | 7.9181 | 4762.7357 | 4.5307 | 11762.0088 | 3.3496 | 123.3457 | 7.918 | 4715.9678 | 4.3161 | 11611.651 | 3.0411 | 128.3486 | 7.9185 | 4656.1194 | 4.5436 | 11870.114 |  |  | 7.9181 | 4762.7357 | 4.5307 | 11762.0088 | 3.3496 | 123.3457 | 7.918 | 4715.9678 | 4.3161 | 11611.651 | 3.0411 | 128.3486 |  |  | 5.5733 | 7725.456 | 5.6288 | 7652.6945 |  |  | 5.5733 | 7725.456 | 5.6288 | 7652.6945 |  |  | 6.8157 | 206.4633 |  |  | 5.5089 | 7963.0295 |  |  | 6.8157 | 206.4633 |  |  | 5.5089 | 7963.0295
7.9185 | 4656.1194 | 4.5436 | 11870.114 |  |  | 7.9181 | 4762.7357 | 4.5307 | 11762.0088 | 3.3496 | 123.3457 | 7.918 | 4715.9678 | 4.3161 | 11611.651 | 3.0411 | 128.3486 | 7.9185 | 4656.1194 | 4.5436 | 11870.114 |  |  | 7.9181 | 4762.7357 | 4.5307 | 11762.0088 | 3.3496 | 123.3457 | 7.918 | 4715.9678 | 4.3161 | 11611.651 | 3.0411 | 128.3486 |  |  | 5.5733 | 7725.456 | 5.6288 | 7652.6945 |  |  | 5.5733 | 7725.456 | 5.6288 | 7652.6945 |  |  | 6.8157 | 206.4633 |  |  | 5.5089 | 7963.0295 |  |  | 6.8157 | 206.4633 |  |  | 5.5089 | 7963.0295
7.9185 | 4704.1206 | 4.5291 | 11992.4863 |  |  | 7.9181 | 4811.836 | 4.2903 | 11883.2667 | 3.307 | 124.6173 | 7.9176 | 4764.586 | 3.8987 | 11731.3587 | 3.1298 | 123.4835 | 7.9185 | 4704.1206 | 4.5291 | 11992.4863 |  |  | 7.9181 | 4811.836 | 4.2903 | 11883.2667 | 3.307 | 124.6173 | 7.9176 | 4764.586 | 3.8987 | 11731.3587 | 3.1298 | 123.4835 |  |  | 5.5643 | 7805.0998 | 5.5713 | 7731.5883 |  |  | 5.5643 | 7805.0998 | 5.5713 | 7731.5883 |  |  | 6.8007 | 208.5918 |  |  | 5.4795 | 8045.1226 |  |  | 6.8007 | 208.5918 |  |  | 5.4795 | 8045.1226
7.9185 | 4704.1206 | 4.5291 | 11992.4863 |  |  | 7.9181 | 4811.836 | 4.2903 | 11883.2667 | 3.307 | 124.6173 | 7.9176 | 4764.586 | 3.8987 | 11731.3587 | 3.1298 | 123.4835 | 7.9185 | 4704.1206 | 4.5291 | 11992.4863 |  |  | 7.9181 | 4811.836 | 4.2903 | 11883.2667 | 3.307 | 124.6173 | 7.9176 | 4764.586 | 3.8987 | 11731.3587 | 3.1298 | 123.4835 |  |  | 5.5643 | 7805.0998 | 5.5713 | 7731.5883 |  |  | 5.5643 | 7805.0998 | 5.5713 | 7731.5883 |  |  | 6.8007 | 208.5918 |  |  | 5.4795 | 8045.1226 |  |  | 6.8007 | 208.5918 |  |  | 5.4795 | 8045.1226
7.9183 | 4752.1219 | 4.5291 | 12114.8586 |  |  | 7.9181 | 4860.9364 | 4.274 | 12004.5245 | 3.0111 | 125.8889 | 7.9176 | 4813.2042 | 3.4714 | 11851.0665 | 3.1174 | 124.7436 | 7.9183 | 4752.1219 | 4.5291 | 12114.8586 |  |  | 7.9181 | 4860.9364 | 4.274 | 12004.5245 | 3.0111 | 125.8889 | 7.9176 | 4813.2042 | 3.4714 | 11851.0665 | 3.1174 | 124.7436 |  |  | 5.5336 | 7884.7437 | 5.5693 | 7810.482 |  |  | 5.5336 | 7884.7437 | 5.5693 | 7810.482 |  |  | 6.7795 | 210.7203 |  |  | 5.4209 | 8127.2157 |  |  | 6.7795 | 210.7203 |  |  | 5.4209 | 8127.2157
7.9183 | 4752.1219 | 4.5291 | 12114.8586 |  |  | 7.9181 | 4860.9364 | 4.274 | 12004.5245 | 3.0111 | 125.8889 | 7.9176 | 4813.2042 | 3.4714 | 11851.0665 | 3.1174 | 124.7436 | 7.9183 | 4752.1219 | 4.5291 | 12114.8586 |  |  | 7.9181 | 4860.9364 | 4.274 | 12004.5245 | 3.0111 | 125.8889 | 7.9176 | 4813.2042 | 3.4714 | 11851.0665 | 3.1174 | 124.7436 |  |  | 5.5336 | 7884.7437 | 5.5693 | 7810.482 |  |  | 5.5336 | 7884.7437 | 5.5693 | 7810.482 |  |  | 6.7795 | 210.7203 |  |  | 5.4209 | 8127.2157 |  |  | 6.7795 | 210.7203 |  |  | 5.4209 | 8127.2157
7.9183 | 4800.1231 | 4.2646 | 12237.2309 |  |  | 7.9181 | 4910.0368 | 3.7983 | 12125.7823 |  |  | 7.9176 | 4861.8225 | 3.2583 | 11970.7742 |  |  | 7.9183 | 4800.1231 | 4.2646 | 12237.2309 |  |  | 7.9181 | 4910.0368 | 3.7983 | 12125.7823 |  |  | 7.9176 | 4861.8225 | 3.2583 | 11970.7742 |  |  |  |  | 5.5153 | 7964.3876 | 5.5254 | 7889.3758 |  |  | 5.5153 | 7964.3876 | 5.5254 | 7889.3758 |  |  | 6.7655 | 212.8488 |  |  | 5.4154 | 8209.3088 |  |  | 6.7655 | 212.8488 |  |  | 5.4154 | 8209.3088
7.9183 | 4800.1231 | 4.2646 | 12237.2309 |  |  | 7.9181 | 4910.0368 | 3.7983 | 12125.7823 |  |  | 7.9176 | 4861.8225 | 3.2583 | 11970.7742 |  |  | 7.9183 | 4800.1231 | 4.2646 | 12237.2309 |  |  | 7.9181 | 4910.0368 | 3.7983 | 12125.7823 |  |  | 7.9176 | 4861.8225 | 3.2583 | 11970.7742 |  |  |  |  | 5.5153 | 7964.3876 | 5.5254 | 7889.3758 |  |  | 5.5153 | 7964.3876 | 5.5254 | 7889.3758 |  |  | 6.7655 | 212.8488 |  |  | 5.4154 | 8209.3088 |  |  | 6.7655 | 212.8488 |  |  | 5.4154 | 8209.3088
7.9182 | 4848.1243 | 4.2614 | 12359.6032 |  |  | 7.9181 | 4959.1371 | 3.5244 | 12247.0401 |  |  | 7.9176 | 4910.4407 | 3.1893 | 12090.4819 |  |  | 7.9182 | 4848.1243 | 4.2614 | 12359.6032 |  |  | 7.9181 | 4959.1371 | 3.5244 | 12247.0401 |  |  | 7.9176 | 4910.4407 | 3.1893 | 12090.4819 |  |  |  |  | 5.4641 | 8044.0315 | 5.4805 | 7968.2695 |  |  | 5.4641 | 8044.0315 | 5.4805 | 7968.2695 |  |  | 6.7345 | 214.9773 |  |  | 5.3497 | 8291.4019 |  |  | 6.7345 | 214.9773 |  |  | 5.3497 | 8291.4019
7.9182 | 4848.1243 | 4.2614 | 12359.6032 |  |  | 7.9181 | 4959.1371 | 3.5244 | 12247.0401 |  |  | 7.9176 | 4910.4407 | 3.1893 | 12090.4819 |  |  | 7.9182 | 4848.1243 | 4.2614 | 12359.6032 |  |  | 7.9181 | 4959.1371 | 3.5244 | 12247.0401 |  |  | 7.9176 | 4910.4407 | 3.1893 | 12090.4819 |  |  |  |  | 5.4641 | 8044.0315 | 5.4805 | 7968.2695 |  |  | 5.4641 | 8044.0315 | 5.4805 | 7968.2695 |  |  | 6.7345 | 214.9773 |  |  | 5.3497 | 8291.4019 |  |  | 6.7345 | 214.9773 |  |  | 5.3497 | 8291.4019
7.9182 | 4896.1256 | 3.8043 | 12481.9755 |  |  | 7.918 | 5008.2375 | 3.5016 | 12368.2979 |  |  | 7.9176 | 4959.0589 | 3.1384 | 12210.1897 |  |  | 7.9182 | 4896.1256 | 3.8043 | 12481.9755 |  |  | 7.918 | 5008.2375 | 3.5016 | 12368.2979 |  |  | 7.9176 | 4959.0589 | 3.1384 | 12210.1897 |  |  |  |  | 5.4349 | 8123.6753 | 5.4793 | 8047.1633 |  |  | 5.4349 | 8123.6753 | 5.4793 | 8047.1633 |  |  | 6.7068 | 217.1058 |  |  | 5.3262 | 8373.495 |  |  | 6.7068 | 217.1058 |  |  | 5.3262 | 8373.495
7.9182 | 4896.1256 | 3.8043 | 12481.9755 |  |  | 7.918 | 5008.2375 | 3.5016 | 12368.2979 |  |  | 7.9176 | 4959.0589 | 3.1384 | 12210.1897 |  |  | 7.9182 | 4896.1256 | 3.8043 | 12481.9755 |  |  | 7.918 | 5008.2375 | 3.5016 | 12368.2979 |  |  | 7.9176 | 4959.0589 | 3.1384 | 12210.1897 |  |  |  |  | 5.4349 | 8123.6753 | 5.4793 | 8047.1633 |  |  | 5.4349 | 8123.6753 | 5.4793 | 8047.1633 |  |  | 6.7068 | 217.1058 |  |  | 5.3262 | 8373.495 |  |  | 6.7068 | 217.1058 |  |  | 5.3262 | 8373.495
7.9182 | 4944.1268 | 3.682 | 12604.3478 |  |  | 7.918 | 5057.3379 | 3.5016 | 12489.5558 |  |  | 7.9176 | 5007.6771 | 3.4435 | 12320.2994 |  |  | 7.9182 | 4944.1268 | 3.682 | 12604.3478 |  |  | 7.918 | 5057.3379 | 3.5016 | 12489.5558 |  |  | 7.9176 | 5007.6771 | 3.4435 | 12320.2994 |  |  |  |  | 5.3725 | 8203.3192 | 5.4145 | 8126.057 |  |  | 5.3725 | 8203.3192 | 5.4145 | 8126.057 |  |  | 6.6869 | 219.2343 |  |  | 5.3245 | 8455.588 |  |  | 6.6869 | 219.2343 |  |  | 5.3245 | 8455.588
7.9182 | 4944.1268 | 3.682 | 12604.3478 |  |  | 7.918 | 5057.3379 | 3.5016 | 12489.5558 |  |  | 7.9176 | 5007.6771 | 3.4435 | 12320.2994 |  |  | 7.9182 | 4944.1268 | 3.682 | 12604.3478 |  |  | 7.918 | 5057.3379 | 3.5016 | 12489.5558 |  |  | 7.9176 | 5007.6771 | 3.4435 | 12320.2994 |  |  |  |  | 5.3725 | 8203.3192 | 5.4145 | 8126.057 |  |  | 5.3725 | 8203.3192 | 5.4145 | 8126.057 |  |  | 6.6869 | 219.2343 |  |  | 5.3245 | 8455.588 |  |  | 6.6869 | 219.2343 |  |  | 5.3245 | 8455.588
7.9182 | 4992.128 | 3.682 | 12726.7201 |  |  | 7.918 | 5106.4383 | 3.4829 | 12610.8136 |  |  | 7.9176 | 5056.2954 | 3.3329 | 12439.9139 |  |  | 7.9182 | 4992.128 | 3.682 | 12726.7201 |  |  | 7.918 | 5106.4383 | 3.4829 | 12610.8136 |  |  | 7.9176 | 5056.2954 | 3.3329 | 12439.9139 |  |  |  |  | 5.3607 | 8282.9631 | 5.3526 | 8204.9508 |  |  | 5.3607 | 8282.9631 | 5.3526 | 8204.9508 |  |  | 6.6353 | 221.3628 |  |  | 5.3168 | 8537.6811 |  |  | 6.6353 | 221.3628 |  |  | 5.3168 | 8537.6811
7.9182 | 4992.128 | 3.682 | 12726.7201 |  |  | 7.918 | 5106.4383 | 3.4829 | 12610.8136 |  |  | 7.9176 | 5056.2954 | 3.3329 | 12439.9139 |  |  | 7.9182 | 4992.128 | 3.682 | 12726.7201 |  |  | 7.918 | 5106.4383 | 3.4829 | 12610.8136 |  |  | 7.9176 | 5056.2954 | 3.3329 | 12439.9139 |  |  |  |  | 5.3607 | 8282.9631 | 5.3526 | 8204.9508 |  |  | 5.3607 | 8282.9631 | 5.3526 | 8204.9508 |  |  | 6.6353 | 221.3628 |  |  | 5.3168 | 8537.6811 |  |  | 6.6353 | 221.3628 |  |  | 5.3168 | 8537.6811
7.9182 | 5040.1293 | 3.6698 | 12849.0924 |  |  | 7.918 | 5155.5386 | 3.4635 | 12732.0714 |  |  | 7.9176 | 5104.9136 |  |  |  |  | 7.9182 | 5040.1293 | 3.6698 | 12849.0924 |  |  | 7.918 | 5155.5386 | 3.4635 | 12732.0714 |  |  | 7.9176 | 5104.9136 | [6 empty] | 5.338 | 8362.607 | 5.318 | 8283.8446 |  |  | 5.338 | 8362.607 | 5.318 | 8283.8446 |  |  | 6.5958 | 223.4912 |  |  | 5.2533 | 8619.7742 |  |  | 6.5958 | 223.4912 |  |  | 5.2533 | 8619.7742
7.9182 | 5040.1293 | 3.6698 | 12849.0924 |  |  | 7.918 | 5155.5386 | 3.4635 | 12732.0714 |  |  | 7.9176 | 5104.9136 |  |  |  |  | 7.9182 | 5040.1293 | 3.6698 | 12849.0924 |  |  | 7.918 | 5155.5386 | 3.4635 | 12732.0714 |  |  | 7.9176 | 5104.9136 | [6 empty] | 5.338 | 8362.607 | 5.318 | 8283.8446 |  |  | 5.338 | 8362.607 | 5.318 | 8283.8446 |  |  | 6.5958 | 223.4912 |  |  | 5.2533 | 8619.7742 |  |  | 6.5958 | 223.4912 |  |  | 5.2533 | 8619.7742
7.9182 | 5088.1305 | 3.6698 | 12971.4648 |  |  | 7.918 | 5204.639 | 3.083 | 12853.3292 |  |  | 7.9176 | 5153.5318 |  |  |  |  | 7.9182 | 5088.1305 | 3.6698 | 12971.4648 |  |  | 7.918 | 5204.639 | 3.083 | 12853.3292 |  |  | 7.9176 | 5153.5318 | [6 empty] | 5.3189 | 8442.2508 | 5.2932 | 8362.7383 |  |  | 5.3189 | 8442.2508 | 5.2932 | 8362.7383 |  |  | 6.5266 | 225.6197 |  |  | 5.2384 | 8701.8673 |  |  | 6.5266 | 225.6197 |  |  | 5.2384 | 8701.8673
7.9182 | 5088.1305 | 3.6698 | 12971.4648 |  |  | 7.918 | 5204.639 | 3.083 | 12853.3292 |  |  | 7.9176 | 5153.5318 |  |  |  |  | 7.9182 | 5088.1305 | 3.6698 | 12971.4648 |  |  | 7.918 | 5204.639 | 3.083 | 12853.3292 |  |  | 7.9176 | 5153.5318 | [6 empty] | 5.3189 | 8442.2508 | 5.2932 | 8362.7383 |  |  | 5.3189 | 8442.2508 | 5.2932 | 8362.7383 |  |  | 6.5266 | 225.6197 |  |  | 5.2384 | 8701.8673 |  |  | 6.5266 | 225.6197 |  |  | 5.2384 | 8701.8673
7.9182 | 5136.1317 | 3.6698 | 13093.8371 |  |  | 7.918 | 5253.7394 | 3.0601 | 13139.131 |  |  | 7.9176 | 5202.15 |  |  |  |  | 7.9182 | 5136.1317 | 3.6698 | 13093.8371 |  |  | 7.918 | 5253.7394 | 3.0601 | 13139.131 |  |  | 7.9176 | 5202.15 | [6 empty] | 5.3165 | 8521.8947 | 5.2908 | 8441.6321 |  |  | 5.3165 | 8521.8947 | 5.2908 | 8441.6321 |  |  | 6.4106 | 227.7482 |  |  | 5.2348 | 8783.9604 |  |  | 6.4106 | 227.7482 |  |  | 5.2348 | 8783.9604
7.9182 | 5136.1317 | 3.6698 | 13093.8371 |  |  | 7.918 | 5253.7394 | 3.0601 | 13139.131 |  |  | 7.9176 | 5202.15 |  |  |  |  | 7.9182 | 5136.1317 | 3.6698 | 13093.8371 |  |  | 7.918 | 5253.7394 | 3.0601 | 13139.131 |  |  | 7.9176 | 5202.15 | [6 empty] | 5.3165 | 8521.8947 | 5.2908 | 8441.6321 |  |  | 5.3165 | 8521.8947 | 5.2908 | 8441.6321 |  |  | 6.4106 | 227.7482 |  |  | 5.2348 | 8783.9604 |  |  | 6.4106 | 227.7482 |  |  | 5.2348 | 8783.9604
7.9181 | 5184.133 | 3.2713 | 13216.2094 |  |  | 7.918 | 5302.8397 | 3.0601 | 13261.9266 |  |  | 7.9176 | 5250.7683 |  |  |  |  | 7.9181 | 5184.133 | 3.2713 | 13216.2094 |  |  | 7.918 | 5302.8397 | 3.0601 | 13261.9266 |  |  | 7.9176 | 5250.7683 | [6 empty] | 5.3165 | 8601.5386 | 5.2682 | 8520.5258 |  |  | 5.3165 | 8601.5386 | 5.2682 | 8520.5258 |  |  | 6.3623 | 229.8767 |  |  | 5.2288 | 8866.0535 |  |  | 6.3623 | 229.8767 |  |  | 5.2288 | 8866.0535
7.9181 | 5184.133 | 3.2713 | 13216.2094 |  |  | 7.918 | 5302.8397 | 3.0601 | 13261.9266 |  |  | 7.9176 | 5250.7683 |  |  |  |  | 7.9181 | 5184.133 | 3.2713 | 13216.2094 |  |  | 7.918 | 5302.8397 | 3.0601 | 13261.9266 |  |  | 7.9176 | 5250.7683 | [6 empty] | 5.3165 | 8601.5386 | 5.2682 | 8520.5258 |  |  | 5.3165 | 8601.5386 | 5.2682 | 8520.5258 |  |  | 6.3623 | 229.8767 |  |  | 5.2288 | 8866.0535 |  |  | 6.3623 | 229.8767 |  |  | 5.2288 | 8866.0535
7.9181 | 5232.1342 | 3.1077 | 13338.5817 |  |  | 7.918 | 5351.9401 | 3.0601 | 13384.7223 |  |  | 7.9176 | 5299.3865 |  |  |  |  | 7.9181 | 5232.1342 | 3.1077 | 13338.5817 |  |  | 7.918 | 5351.9401 | 3.0601 | 13384.7223 |  |  | 7.9176 | 5299.3865 | [6 empty] | 5.2495 | 8681.1825 | 5.2222 | 8599.4196 |  |  | 5.2495 | 8681.1825 | 5.2222 | 8599.4196 |  |  | 6.3549 | 232.0052 |  |  | 5.2279 | 8948.1466 |  |  | 6.3549 | 232.0052 |  |  | 5.2279 | 8948.1466
7.9181 | 5232.1342 | 3.1077 | 13338.5817 |  |  | 7.918 | 5351.9401 | 3.0601 | 13384.7223 |  |  | 7.9176 | 5299.3865 |  |  |  |  | 7.9181 | 5232.1342 | 3.1077 | 13338.5817 |  |  | 7.918 | 5351.9401 | 3.0601 | 13384.7223 |  |  | 7.9176 | 5299.3865 | [6 empty] | 5.2495 | 8681.1825 | 5.2222 | 8599.4196 |  |  | 5.2495 | 8681.1825 | 5.2222 | 8599.4196 |  |  | 6.3549 | 232.0052 |  |  | 5.2279 | 8948.1466 |  |  | 6.3549 | 232.0052 |  |  | 5.2279 | 8948.1466
7.918 | 5280.1354 | 3.1077 | 13460.954 |  |  | 7.918 | 5401.0405 | 3.0601 | 13507.5179 |  |  | 7.9176 | 5348.0047 |  |  |  |  | 7.918 | 5280.1354 | 3.1077 | 13460.954 |  |  | 7.918 | 5401.0405 | 3.0601 | 13507.5179 |  |  | 7.9176 | 5348.0047 | [6 empty] | 5.2345 | 8760.8263 | 5.2 | 8678.3133 |  |  | 5.2345 | 8760.8263 | 5.2 | 8678.3133 |  |  | 6.2889 | 234.1337 |  |  | 5.2111 | 9030.2397 |  |  | 6.2889 | 234.1337 |  |  | 5.2111 | 9030.2397
7.918 | 5280.1354 | 3.1077 | 13460.954 |  |  | 7.918 | 5401.0405 | 3.0601 | 13507.5179 |  |  | 7.9176 | 5348.0047 |  |  |  |  | 7.918 | 5280.1354 | 3.1077 | 13460.954 |  |  | 7.918 | 5401.0405 | 3.0601 | 13507.5179 |  |  | 7.9176 | 5348.0047 | [6 empty] | 5.2345 | 8760.8263 | 5.2 | 8678.3133 |  |  | 5.2345 | 8760.8263 | 5.2 | 8678.3133 |  |  | 6.2889 | 234.1337 |  |  | 5.2111 | 9030.2397 |  |  | 6.2889 | 234.1337 |  |  | 5.2111 | 9030.2397
7.918 | 5328.1367 | 3.1077 | 13583.3263 |  |  | 7.918 | 5450.1408 | 3.0601 | 13630.3135 |  |  | 7.9175 | 5396.6229 |  |  |  |  | 7.918 | 5328.1367 | 3.1077 | 13583.3263 |  |  | 7.918 | 5450.1408 | 3.0601 | 13630.3135 |  |  | 7.9175 | 5396.6229 | [6 empty] | 5.2328 | 8840.4702 | 5.1736 | 8757.2071 |  |  | 5.2328 | 8840.4702 | 5.1736 | 8757.2071 |  |  | 6.2375 | 236.2622 |  |  | 5.1955 | 9112.3327 |  |  | 6.2375 | 236.2622 |  |  | 5.1955 | 9112.3327
7.918 | 5328.1367 | 3.1077 | 13583.3263 |  |  | 7.918 | 5450.1408 | 3.0601 | 13630.3135 |  |  | 7.9175 | 5396.6229 |  |  |  |  | 7.918 | 5328.1367 | 3.1077 | 13583.3263 |  |  | 7.918 | 5450.1408 | 3.0601 | 13630.3135 |  |  | 7.9175 | 5396.6229 | [6 empty] | 5.2328 | 8840.4702 | 5.1736 | 8757.2071 |  |  | 5.2328 | 8840.4702 | 5.1736 | 8757.2071 |  |  | 6.2375 | 236.2622 |  |  | 5.1955 | 9112.3327 |  |  | 6.2375 | 236.2622 |  |  | 5.1955 | 9112.3327
7.9178 | 5376.1379 | 3.1077 | 13705.6986 |  |  | 7.918 | 5499.2412 | 3.0601 | 13753.1091 |  |  | 7.9175 | 5445.2412 |  |  |  |  | 7.9178 | 5376.1379 | 3.1077 | 13705.6986 |  |  | 7.918 | 5499.2412 | 3.0601 | 13753.1091 |  |  | 7.9175 | 5445.2412 | [6 empty] | 5.2274 | 8920.1141 | 5.1632 | 8836.1009 |  |  | 5.2274 | 8920.1141 | 5.1632 | 8836.1009 |  |  | 6.1908 | 238.3907 |  |  | 5.1625 | 9194.4258 |  |  | 6.1908 | 238.3907 |  |  | 5.1625 | 9194.4258
7.9178 | 5376.1379 | 3.1077 | 13705.6986 |  |  | 7.918 | 5499.2412 | 3.0601 | 13753.1091 |  |  | 7.9175 | 5445.2412 |  |  |  |  | 7.9178 | 5376.1379 | 3.1077 | 13705.6986 |  |  | 7.918 | 5499.2412 | 3.0601 | 13753.1091 |  |  | 7.9175 | 5445.2412 | [6 empty] | 5.2274 | 8920.1141 | 5.1632 | 8836.1009 |  |  | 5.2274 | 8920.1141 | 5.1632 | 8836.1009 |  |  | 6.1908 | 238.3907 |  |  | 5.1625 | 9194.4258 |  |  | 6.1908 | 238.3907 |  |  | 5.1625 | 9194.4258
7.9176 | 5424.1391 | 3.1077 | 13828.0709 |  |  | 7.918 | 5548.3416 |  |  |  |  | 7.9175 | 5493.8594 |  |  |  |  | 7.9176 | 5424.1391 | 3.1077 | 13828.0709 |  |  | 7.918 | 5548.3416 |  |  |  |  | 7.9175 | 5493.8594 | [6 empty] | 5.2113 | 8999.758 | 5.1595 | 8914.9946 |  |  | 5.2113 | 8999.758 | 5.1595 | 8914.9946 |  |  | 6.1792 | 240.5191 |  |  | 5.1191 | 9276.5189 |  |  | 6.1792 | 240.5191 |  |  | 5.1191 | 9276.5189
7.9176 | 5424.1391 | 3.1077 | 13828.0709 |  |  | 7.918 | 5548.3416 |  |  |  |  | 7.9175 | 5493.8594 |  |  |  |  | 7.9176 | 5424.1391 | 3.1077 | 13828.0709 |  |  | 7.918 | 5548.3416 |  |  |  |  | 7.9175 | 5493.8594 | [6 empty] | 5.2113 | 8999.758 | 5.1595 | 8914.9946 |  |  | 5.2113 | 8999.758 | 5.1595 | 8914.9946 |  |  | 6.1792 | 240.5191 |  |  | 5.1191 | 9276.5189 |  |  | 6.1792 | 240.5191 |  |  | 5.1191 | 9276.5189
7.9174 | 5472.1403 | 3.0601 | 13950.4432 |  |  | 7.9179 | 5597.4419 |  |  |  |  | 7.9175 | 5542.4776 |  |  |  |  | 7.9174 | 5472.1403 | 3.0601 | 13950.4432 |  |  | 7.9179 | 5597.4419 |  |  |  |  | 7.9175 | 5542.4776 | [6 empty] | 5.1958 | 9079.4019 | 5.1453 | 8993.8884 |  |  | 5.1958 | 9079.4019 | 5.1453 | 8993.8884 |  |  | 6.1072 | 242.6476 |  |  | 5.1089 | 9358.612 |  |  | 6.1072 | 242.6476 |  |  | 5.1089 | 9358.612
7.9174 | 5472.1403 | 3.0601 | 13950.4432 |  |  | 7.9179 | 5597.4419 |  |  |  |  | 7.9175 | 5542.4776 |  |  |  |  | 7.9174 | 5472.1403 | 3.0601 | 13950.4432 |  |  | 7.9179 | 5597.4419 |  |  |  |  | 7.9175 | 5542.4776 | [6 empty] | 5.1958 | 9079.4019 | 5.1453 | 8993.8884 |  |  | 5.1958 | 9079.4019 | 5.1453 | 8993.8884 |  |  | 6.1072 | 242.6476 |  |  | 5.1089 | 9358.612 |  |  | 6.1072 | 242.6476 |  |  | 5.1089 | 9358.612
7.9174 | 5520.1416 | 3.0601 | 14072.8155 |  |  | 7.9179 | 5646.5423 |  |  |  |  | 7.9175 | 5591.0958 |  |  |  |  | 7.9174 | 5520.1416 | 3.0601 | 14072.8155 |  |  | 7.9179 | 5646.5423 |  |  |  |  | 7.9175 | 5591.0958 | [6 empty] | 5.1894 | 9159.0457 | 5.1243 | 9072.7821 |  |  | 5.1894 | 9159.0457 | 5.1243 | 9072.7821 |  |  | 6.0552 | 244.7761 |  |  | 5.1087 | 9440.7051 |  |  | 6.0552 | 244.7761 |  |  | 5.1087 | 9440.7051
7.9174 | 5520.1416 | 3.0601 | 14072.8155 |  |  | 7.9179 | 5646.5423 |  |  |  |  | 7.9175 | 5591.0958 |  |  |  |  | 7.9174 | 5520.1416 | 3.0601 | 14072.8155 |  |  | 7.9179 | 5646.5423 |  |  |  |  | 7.9175 | 5591.0958 | [6 empty] | 5.1894 | 9159.0457 | 5.1243 | 9072.7821 |  |  | 5.1894 | 9159.0457 | 5.1243 | 9072.7821 |  |  | 6.0552 | 244.7761 |  |  | 5.1087 | 9440.7051 |  |  | 6.0552 | 244.7761 |  |  | 5.1087 | 9440.7051
7.9174 | 5568.1428 | 3.0601 | 14195.1878 |  |  | 7.9179 | 5695.6427 |  |  |  |  | 7.9173 | 5639.7141 |  |  |  |  | 7.9174 | 5568.1428 | 3.0601 | 14195.1878 |  |  | 7.9179 | 5695.6427 |  |  |  |  | 7.9173 | 5639.7141 | [6 empty] | 5.1886 | 9238.6896 | 5.1104 | 9151.6759 |  |  | 5.1886 | 9238.6896 | 5.1104 | 9151.6759 |  |  | 6.0107 | 246.9046 |  |  | 5.0286 | 9522.7982 |  |  | 6.0107 | 246.9046 |  |  | 5.0286 | 9522.7982
7.9174 | 5568.1428 | 3.0601 | 14195.1878 |  |  | 7.9179 | 5695.6427 |  |  |  |  | 7.9173 | 5639.7141 |  |  |  |  | 7.9174 | 5568.1428 | 3.0601 | 14195.1878 |  |  | 7.9179 | 5695.6427 |  |  |  |  | 7.9173 | 5639.7141 | [6 empty] | 5.1886 | 9238.6896 | 5.1104 | 9151.6759 |  |  | 5.1886 | 9238.6896 | 5.1104 | 9151.6759 |  |  | 6.0107 | 246.9046 |  |  | 5.0286 | 9522.7982 |  |  | 6.0107 | 246.9046 |  |  | 5.0286 | 9522.7982
7.9174 | 5616.144 |  |  |  |  | 7.9179 | 5744.743 |  |  |  |  | 7.9173 | 5688.3323 |  |  |  |  | 7.9174 | 5616.144 |  |  |  |  | 7.9179 | 5744.743 |  |  |  |  | 7.9173 | 5688.3323 | [6 empty] | 5.1156 | 9318.3335 | 5.0632 | 9230.5697 |  |  | 5.1156 | 9318.3335 | 5.0632 | 9230.5697 |  |  | 5.9606 | 249.0331 |  |  | 4.9743 | 9604.8913 |  |  | 5.9606 | 249.0331 |  |  | 4.9743 | 9604.8913
7.9174 | 5616.144 |  |  |  |  | 7.9179 | 5744.743 |  |  |  |  | 7.9173 | 5688.3323 |  |  |  |  | 7.9174 | 5616.144 |  |  |  |  | 7.9179 | 5744.743 |  |  |  |  | 7.9173 | 5688.3323 | [6 empty] | 5.1156 | 9318.3335 | 5.0632 | 9230.5697 |  |  | 5.1156 | 9318.3335 | 5.0632 | 9230.5697 |  |  | 5.9606 | 249.0331 |  |  | 4.9743 | 9604.8913 |  |  | 5.9606 | 249.0331 |  |  | 4.9743 | 9604.8913
7.9174 | 5664.1453 |  |  |  |  | 7.9178 | 5793.8434 |  |  |  |  | 7.9173 | 5736.9505 |  |  |  |  | 7.9174 | 5664.1453 |  |  |  |  | 7.9178 | 5793.8434 |  |  |  |  | 7.9173 | 5736.9505 | [6 empty] | 5.1123 | 9397.9774 | 4.951 | 9309.4634 |  |  | 5.1123 | 9397.9774 | 4.951 | 9309.4634 |  |  | 5.9423 | 251.1616 |  |  | 4.9608 | 9686.9844 |  |  | 5.9423 | 251.1616 |  |  | 4.9608 | 9686.9844
7.9174 | 5664.1453 |  |  |  |  | 7.9178 | 5793.8434 |  |  |  |  | 7.9173 | 5736.9505 |  |  |  |  | 7.9174 | 5664.1453 |  |  |  |  | 7.9178 | 5793.8434 |  |  |  |  | 7.9173 | 5736.9505 | [6 empty] | 5.1123 | 9397.9774 | 4.951 | 9309.4634 |  |  | 5.1123 | 9397.9774 | 4.951 | 9309.4634 |  |  | 5.9423 | 251.1616 |  |  | 4.9608 | 9686.9844 |  |  | 5.9423 | 251.1616 |  |  | 4.9608 | 9686.9844
7.9174 | 5712.1465 |  |  |  |  | 7.9177 | 5842.9438 |  |  |  |  | 7.9173 | 5785.5687 |  |  |  |  | 7.9174 | 5712.1465 |  |  |  |  | 7.9177 | 5842.9438 |  |  |  |  | 7.9173 | 5785.5687 | [6 empty] | 5.1025 | 9477.6212 | 4.9187 | 9388.3572 |  |  | 5.1025 | 9477.6212 | 4.9187 | 9388.3572 |  |  | 5.9045 | 253.2901 |  |  | 4.9332 | 9769.0774 |  |  | 5.9045 | 253.2901 |  |  | 4.9332 | 9769.0774
7.9174 | 5712.1465 |  |  |  |  | 7.9177 | 5842.9438 |  |  |  |  | 7.9173 | 5785.5687 |  |  |  |  | 7.9174 | 5712.1465 |  |  |  |  | 7.9177 | 5842.9438 |  |  |  |  | 7.9173 | 5785.5687 | [6 empty] | 5.1025 | 9477.6212 | 4.9187 | 9388.3572 |  |  | 5.1025 | 9477.6212 | 4.9187 | 9388.3572 |  |  | 5.9045 | 253.2901 |  |  | 4.9332 | 9769.0774 |  |  | 5.9045 | 253.2901 |  |  | 4.9332 | 9769.0774
7.9174 | 5760.1477 |  |  |  |  | 7.9176 | 5892.0441 |  |  |  |  | 7.9171 | 5834.187 |  |  |  |  | 7.9174 | 5760.1477 |  |  |  |  | 7.9176 | 5892.0441 |  |  |  |  | 7.9171 | 5834.187 | [6 empty] | 5.1024 | 9557.2651 | 4.9183 | 9467.2509 |  |  | 5.1024 | 9557.2651 | 4.9183 | 9467.2509 |  |  | 5.7745 | 255.4186 |  |  | 4.9332 | 9851.1705 |  |  | 5.7745 | 255.4186 |  |  | 4.9332 | 9851.1705
7.9174 | 5760.1477 |  |  |  |  | 7.9176 | 5892.0441 |  |  |  |  | 7.9171 | 5834.187 |  |  |  |  | 7.9174 | 5760.1477 |  |  |  |  | 7.9176 | 5892.0441 |  |  |  |  | 7.9171 | 5834.187 | [6 empty] | 5.1024 | 9557.2651 | 4.9183 | 9467.2509 |  |  | 5.1024 | 9557.2651 | 4.9183 | 9467.2509 |  |  | 5.7745 | 255.4186 |  |  | 4.9332 | 9851.1705 |  |  | 5.7745 | 255.4186 |  |  | 4.9332 | 9851.1705
7.9171 | 5808.149 |  |  |  |  | 7.9173 | 5941.1445 |  |  |  |  | 7.917 | 5882.8052 |  |  |  |  | 7.9171 | 5808.149 |  |  |  |  | 7.9173 | 5941.1445 |  |  |  |  | 7.917 | 5882.8052 | [6 empty] | 5.0463 | 9636.909 | 4.9123 | 9546.1447 |  |  | 5.0463 | 9636.909 | 4.9123 | 9546.1447 |  |  | 5.6928 | 257.5471 |  |  | 4.9276 | 9933.2636 |  |  | 5.6928 | 257.5471 |  |  | 4.9276 | 9933.2636
7.9171 | 5808.149 |  |  |  |  | 7.9173 | 5941.1445 |  |  |  |  | 7.917 | 5882.8052 |  |  |  |  | 7.9171 | 5808.149 |  |  |  |  | 7.9173 | 5941.1445 |  |  |  |  | 7.917 | 5882.8052 | [6 empty] | 5.0463 | 9636.909 | 4.9123 | 9546.1447 |  |  | 5.0463 | 9636.909 | 4.9123 | 9546.1447 |  |  | 5.6928 | 257.5471 |  |  | 4.9276 | 9933.2636 |  |  | 5.6928 | 257.5471 |  |  | 4.9276 | 9933.2636
7.917 | 5856.1502 |  |  |  |  | 7.9169 | 5990.2449 |  |  |  |  | 7.917 | 5931.4234 |  |  |  |  | 7.917 | 5856.1502 |  |  |  |  | 7.9169 | 5990.2449 |  |  |  |  | 7.917 | 5931.4234 | [6 empty] | 4.9867 | 9716.5529 | 4.908 | 9625.0384 |  |  | 4.9867 | 9716.5529 | 4.908 | 9625.0384 |  |  | 5.583 | 259.6755 |  |  | 4.9268 | 10015.3567 |  |  | 5.583 | 259.6755 |  |  | 4.9268 | 10015.3567
7.917 | 5856.1502 |  |  |  |  | 7.9169 | 5990.2449 |  |  |  |  | 7.917 | 5931.4234 |  |  |  |  | 7.917 | 5856.1502 |  |  |  |  | 7.9169 | 5990.2449 |  |  |  |  | 7.917 | 5931.4234 | [6 empty] | 4.9867 | 9716.5529 | 4.908 | 9625.0384 |  |  | 4.9867 | 9716.5529 | 4.908 | 9625.0384 |  |  | 5.583 | 259.6755 |  |  | 4.9268 | 10015.3567 |  |  | 5.583 | 259.6755 |  |  | 4.9268 | 10015.3567
7.9169 | 5904.1514 |  |  |  |  | 7.9167 | 6039.3452 |  |  |  |  | 7.9167 | 5980.0416 |  |  |  |  | 7.9169 | 5904.1514 |  |  |  |  | 7.9167 | 6039.3452 |  |  |  |  | 7.9167 | 5980.0416 | [6 empty] | 4.9276 | 9796.1967 | 4.9076 | 9703.9322 |  |  | 4.9276 | 9796.1967 | 4.9076 | 9703.9322 |  |  | 5.4427 | 261.804 |  |  | 4.8729 | 10097.4498 |  |  | 5.4427 | 261.804 |  |  | 4.8729 | 10097.4498
7.9169 | 5904.1514 |  |  |  |  | 7.9167 | 6039.3452 |  |  |  |  | 7.9167 | 5980.0416 |  |  |  |  | 7.9169 | 5904.1514 |  |  |  |  | 7.9167 | 6039.3452 |  |  |  |  | 7.9167 | 5980.0416 | [6 empty] | 4.9276 | 9796.1967 | 4.9076 | 9703.9322 |  |  | 4.9276 | 9796.1967 | 4.9076 | 9703.9322 |  |  | 5.4427 | 261.804 |  |  | 4.8729 | 10097.4498 |  |  | 5.4427 | 261.804 |  |  | 4.8729 | 10097.4498
7.9167 | 5952.1527 |  |  |  |  | 7.9156 | 6088.4456 |  |  |  |  | 7.9162 | 6028.6599 |  |  |  |  | 7.9167 | 5952.1527 |  |  |  |  | 7.9156 | 6088.4456 |  |  |  |  | 7.9162 | 6028.6599 | [6 empty] | 4.9276 | 9875.8406 | 4.9014 | 9782.826 |  |  | 4.9276 | 9875.8406 | 4.9014 | 9782.826 |  |  | 5.381 | 263.9325 |  |  | 4.7783 | 10179.5429 |  |  | 5.381 | 263.9325 |  |  | 4.7783 | 10179.5429
7.9167 | 5952.1527 |  |  |  |  | 7.9156 | 6088.4456 |  |  |  |  | 7.9162 | 6028.6599 |  |  |  |  | 7.9167 | 5952.1527 |  |  |  |  | 7.9156 | 6088.4456 |  |  |  |  | 7.9162 | 6028.6599 | [6 empty] | 4.9276 | 9875.8406 | 4.9014 | 9782.826 |  |  | 4.9276 | 9875.8406 | 4.9014 | 9782.826 |  |  | 5.381 | 263.9325 |  |  | 4.7783 | 10179.5429 |  |  | 5.381 | 263.9325 |  |  | 4.7783 | 10179.5429
7.9161 | 6000.1539 |  |  |  |  | 7.9133 | 6137.546 |  |  |  |  | 7.9143 | 6077.2781 |  |  |  |  | 7.9161 | 6000.1539 |  |  |  |  | 7.9133 | 6137.546 |  |  |  |  | 7.9143 | 6077.2781 | [6 empty] | 4.9115 | 9955.4845 | 4.9003 | 9861.7197 |  |  | 4.9115 | 9955.4845 | 4.9003 | 9861.7197 |  |  | 5.3058 | 266.061 |  |  | 4.7722 | 10261.636 |  |  | 5.3058 | 266.061 |  |  | 4.7722 | 10261.636
7.9161 | 6000.1539 |  |  |  |  | 7.9133 | 6137.546 |  |  |  |  | 7.9143 | 6077.2781 |  |  |  |  | 7.9161 | 6000.1539 |  |  |  |  | 7.9133 | 6137.546 |  |  |  |  | 7.9143 | 6077.2781 | [6 empty] | 4.9115 | 9955.4845 | 4.9003 | 9861.7197 |  |  | 4.9115 | 9955.4845 | 4.9003 | 9861.7197 |  |  | 5.3058 | 266.061 |  |  | 4.7722 | 10261.636 |  |  | 5.3058 | 266.061 |  |  | 4.7722 | 10261.636
7.9153 | 6048.1551 |  |  |  |  | 7.9114 | 6186.6463 |  |  |  |  | 7.9135 | 6125.8963 |  |  |  |  | 7.9153 | 6048.1551 |  |  |  |  | 7.9114 | 6186.6463 |  |  |  |  | 7.9135 | 6125.8963 | [6 empty] | 4.8373 | 10035.1284 | 4.8831 | 9940.6135 |  |  | 4.8373 | 10035.1284 | 4.8831 | 9940.6135 |  |  | 5.1098 | 268.1895 |  |  | 4.7661 | 10343.7291 |  |  | 5.1098 | 268.1895 |  |  | 4.7661 | 10343.7291
7.9153 | 6048.1551 |  |  |  |  | 7.9114 | 6186.6463 |  |  |  |  | 7.9135 | 6125.8963 |  |  |  |  | 7.9153 | 6048.1551 |  |  |  |  | 7.9114 | 6186.6463 |  |  |  |  | 7.9135 | 6125.8963 | [6 empty] | 4.8373 | 10035.1284 | 4.8831 | 9940.6135 |  |  | 4.8373 | 10035.1284 | 4.8831 | 9940.6135 |  |  | 5.1098 | 268.1895 |  |  | 4.7661 | 10343.7291 |  |  | 5.1098 | 268.1895 |  |  | 4.7661 | 10343.7291
7.9142 | 6096.1563 |  |  |  |  | 7.908 | 6235.7467 |  |  |  |  | 7.9109 | 6174.5145 |  |  |  |  | 7.9142 | 6096.1563 |  |  |  |  | 7.908 | 6235.7467 |  |  |  |  | 7.9109 | 6174.5145 | [6 empty] | 4.7722 | 10114.7722 | 4.8829 | 10019.5072 |  |  | 4.7722 | 10114.7722 | 4.8829 | 10019.5072 |  |  | 4.9341 | 270.318 |  |  | 4.7085 | 10425.8222 |  |  | 4.9341 | 270.318 |  |  | 4.7085 | 10425.8222
7.9142 | 6096.1563 |  |  |  |  | 7.908 | 6235.7467 |  |  |  |  | 7.9109 | 6174.5145 |  |  |  |  | 7.9142 | 6096.1563 |  |  |  |  | 7.908 | 6235.7467 |  |  |  |  | 7.9109 | 6174.5145 | [6 empty] | 4.7722 | 10114.7722 | 4.8829 | 10019.5072 |  |  | 4.7722 | 10114.7722 | 4.8829 | 10019.5072 |  |  | 4.9341 | 270.318 |  |  | 4.7085 | 10425.8222 |  |  | 4.9341 | 270.318 |  |  | 4.7085 | 10425.8222
7.9129 | 6144.1576 |  |  |  |  | 7.9021 | 6284.8471 |  |  |  |  | 7.907 | 6223.1328 |  |  |  |  | 7.9129 | 6144.1576 |  |  |  |  | 7.9021 | 6284.8471 |  |  |  |  | 7.907 | 6223.1328 | [6 empty] | 4.725 | 10194.4161 | 4.8067 | 10098.401 |  |  | 4.725 | 10194.4161 | 4.8067 | 10098.401 |  |  | 4.9054 | 272.4465 |  |  | 4.6977 | 10507.9152 |  |  | 4.9054 | 272.4465 |  |  | 4.6977 | 10507.9152
7.9129 | 6144.1576 |  |  |  |  | 7.9021 | 6284.8471 |  |  |  |  | 7.907 | 6223.1328 |  |  |  |  | 7.9129 | 6144.1576 |  |  |  |  | 7.9021 | 6284.8471 |  |  |  |  | 7.907 | 6223.1328 | [6 empty] | 4.725 | 10194.4161 | 4.8067 | 10098.401 |  |  | 4.725 | 10194.4161 | 4.8067 | 10098.401 |  |  | 4.9054 | 272.4465 |  |  | 4.6977 | 10507.9152 |  |  | 4.9054 | 272.4465 |  |  | 4.6977 | 10507.9152
7.9105 | 6192.1588 |  |  |  |  | 7.8917 | 6333.9474 |  |  |  |  | 7.9014 | 6271.751 |  |  |  |  | 7.9105 | 6192.1588 |  |  |  |  | 7.8917 | 6333.9474 |  |  |  |  | 7.9014 | 6271.751 | [6 empty] | 4.7155 | 10274.06 | 4.7872 | 10177.2947 |  |  | 4.7155 | 10274.06 | 4.7872 | 10177.2947 |  |  | 4.8428 | 274.575 |  |  | 4.667 | 10590.0083 |  |  | 4.8428 | 274.575 |  |  | 4.667 | 10590.0083
7.9105 | 6192.1588 |  |  |  |  | 7.8917 | 6333.9474 |  |  |  |  | 7.9014 | 6271.751 |  |  |  |  | 7.9105 | 6192.1588 |  |  |  |  | 7.8917 | 6333.9474 |  |  |  |  | 7.9014 | 6271.751 | [6 empty] | 4.7155 | 10274.06 | 4.7872 | 10177.2947 |  |  | 4.7155 | 10274.06 | 4.7872 | 10177.2947 |  |  | 4.8428 | 274.575 |  |  | 4.667 | 10590.0083 |  |  | 4.8428 | 274.575 |  |  | 4.667 | 10590.0083
7.9055 | 6240.16 |  |  |  |  | 7.8761 | 6383.0478 |  |  |  |  | 7.8916 | 6320.3692 |  |  |  |  | 7.9055 | 6240.16 |  |  |  |  | 7.8761 | 6383.0478 |  |  |  |  | 7.8916 | 6320.3692 | [6 empty] | 4.7085 | 10353.7039 | 4.7872 | 10256.1885 |  |  | 4.7085 | 10353.7039 | 4.7872 | 10256.1885 |  |  | 4.814 | 276.7034 |  |  | 4.667 | 10672.1014 |  |  | 4.814 | 276.7034 |  |  | 4.667 | 10672.1014
7.9055 | 6240.16 |  |  |  |  | 7.8761 | 6383.0478 |  |  |  |  | 7.8916 | 6320.3692 |  |  |  |  | 7.9055 | 6240.16 |  |  |  |  | 7.8761 | 6383.0478 |  |  |  |  | 7.8916 | 6320.3692 | [6 empty] | 4.7085 | 10353.7039 | 4.7872 | 10256.1885 |  |  | 4.7085 | 10353.7039 | 4.7872 | 10256.1885 |  |  | 4.814 | 276.7034 |  |  | 4.667 | 10672.1014 |  |  | 4.814 | 276.7034 |  |  | 4.667 | 10672.1014
7.8973 | 6288.1613 |  |  |  |  | 7.8498 | 6432.1482 |  |  |  |  | 7.8763 | 6368.9874 |  |  |  |  | 7.8973 | 6288.1613 |  |  |  |  | 7.8498 | 6432.1482 |  |  |  |  | 7.8763 | 6368.9874 | [6 empty] | 4.6983 | 10433.3477 | 4.7444 | 10335.0823 |  |  | 4.6983 | 10433.3477 | 4.7444 | 10335.0823 |  |  | 4.8041 | 278.8319 |  |  | 4.6576 | 10754.1945 |  |  | 4.8041 | 278.8319 |  |  | 4.6576 | 10754.1945
7.8973 | 6288.1613 |  |  |  |  | 7.8498 | 6432.1482 |  |  |  |  | 7.8763 | 6368.9874 |  |  |  |  | 7.8973 | 6288.1613 |  |  |  |  | 7.8498 | 6432.1482 |  |  |  |  | 7.8763 | 6368.9874 | [6 empty] | 4.6983 | 10433.3477 | 4.7444 | 10335.0823 |  |  | 4.6983 | 10433.3477 | 4.7444 | 10335.0823 |  |  | 4.8041 | 278.8319 |  |  | 4.6576 | 10754.1945 |  |  | 4.8041 | 278.8319 |  |  | 4.6576 | 10754.1945
7.8871 | 6336.1625 |  |  |  |  | 7.8211 | 6481.2485 |  |  |  |  | 7.854 | 6417.6057 |  |  |  |  | 7.8871 | 6336.1625 |  |  |  |  | 7.8211 | 6481.2485 |  |  |  |  | 7.854 | 6417.6057 | [6 empty] | 4.6965 | 10512.9916 | 4.7379 | 10413.976 |  |  | 4.6965 | 10512.9916 | 4.7379 | 10413.976 |  |  | 4.7819 | 280.9604 |  |  | 4.6113 | 10836.2876 |  |  | 4.7819 | 280.9604 |  |  | 4.6113 | 10836.2876
7.8871 | 6336.1625 |  |  |  |  | 7.8211 | 6481.2485 |  |  |  |  | 7.854 | 6417.6057 |  |  |  |  | 7.8871 | 6336.1625 |  |  |  |  | 7.8211 | 6481.2485 |  |  |  |  | 7.854 | 6417.6057 | [6 empty] | 4.6965 | 10512.9916 | 4.7379 | 10413.976 |  |  | 4.6965 | 10512.9916 | 4.7379 | 10413.976 |  |  | 4.7819 | 280.9604 |  |  | 4.6113 | 10836.2876 |  |  | 4.7819 | 280.9604 |  |  | 4.6113 | 10836.2876
7.8707 | 6384.1637 |  |  |  |  | 7.7761 | 6530.3489 |  |  |  |  | 7.8285 | 6466.2239 |  |  |  |  | 7.8707 | 6384.1637 |  |  |  |  | 7.7761 | 6530.3489 |  |  |  |  | 7.8285 | 6466.2239 | [6 empty] | 4.6892 | 10592.6355 | 4.7287 | 10492.8698 |  |  | 4.6892 | 10592.6355 | 4.7287 | 10492.8698 |  |  | 4.38 | 283.0889 |  |  | 4.5348 | 10918.3807 |  |  | 4.38 | 283.0889 |  |  | 4.5348 | 10918.3807
7.8707 | 6384.1637 |  |  |  |  | 7.7761 | 6530.3489 |  |  |  |  | 7.8285 | 6466.2239 |  |  |  |  | 7.8707 | 6384.1637 |  |  |  |  | 7.7761 | 6530.3489 |  |  |  |  | 7.8285 | 6466.2239 | [6 empty] | 4.6892 | 10592.6355 | 4.7287 | 10492.8698 |  |  | 4.6892 | 10592.6355 | 4.7287 | 10492.8698 |  |  | 4.38 | 283.0889 |  |  | 4.5348 | 10918.3807 |  |  | 4.38 | 283.0889 |  |  | 4.5348 | 10918.3807
7.8484 | 6432.165 |  |  |  |  | 7.7202 | 6579.4493 |  |  |  |  | 7.7879 | 6514.8421 |  |  |  |  | 7.8484 | 6432.165 |  |  |  |  | 7.7202 | 6579.4493 |  |  |  |  | 7.7879 | 6514.8421 | [6 empty] | 4.6892 | 10672.2794 | 4.6764 | 10571.7635 |  |  | 4.6892 | 10672.2794 | 4.6764 | 10571.7635 |  |  | 4.3772 | 285.2174 |  |  | 4.52 | 11000.4738 |  |  | 4.3772 | 285.2174 |  |  | 4.52 | 11000.4738
7.8484 | 6432.165 |  |  |  |  | 7.7202 | 6579.4493 |  |  |  |  | 7.7879 | 6514.8421 |  |  |  |  | 7.8484 | 6432.165 |  |  |  |  | 7.7202 | 6579.4493 |  |  |  |  | 7.7879 | 6514.8421 | [6 empty] | 4.6892 | 10672.2794 | 4.6764 | 10571.7635 |  |  | 4.6892 | 10672.2794 | 4.6764 | 10571.7635 |  |  | 4.3772 | 285.2174 |  |  | 4.52 | 11000.4738 |  |  | 4.3772 | 285.2174 |  |  | 4.52 | 11000.4738
7.8136 | 6480.1662 |  |  |  |  | 7.6655 | 6628.5497 |  |  |  |  | 7.7361 | 6563.4603 |  |  |  |  | 7.8136 | 6480.1662 |  |  |  |  | 7.6655 | 6628.5497 |  |  |  |  | 7.7361 | 6563.4603 | [6 empty] | 4.6161 | 10751.9232 | 4.668 | 10650.6573 |  |  | 4.6161 | 10751.9232 | 4.668 | 10650.6573 |  |  | 4.3396 | 287.3459 |  |  | 4.4134 | 11082.5669 |  |  | 4.3396 | 287.3459 |  |  | 4.4134 | 11082.5669
7.8136 | 6480.1662 |  |  |  |  | 7.6655 | 6628.5497 |  |  |  |  | 7.7361 | 6563.4603 |  |  |  |  | 7.8136 | 6480.1662 |  |  |  |  | 7.6655 | 6628.5497 |  |  |  |  | 7.7361 | 6563.4603 | [6 empty] | 4.6161 | 10751.9232 | 4.668 | 10650.6573 |  |  | 4.6161 | 10751.9232 | 4.668 | 10650.6573 |  |  | 4.3396 | 287.3459 |  |  | 4.4134 | 11082.5669 |  |  | 4.3396 | 287.3459 |  |  | 4.4134 | 11082.5669
7.7758 | 6528.1674 |  |  |  |  | 7.604 | 6677.65 |  |  |  |  | 7.6859 | 6612.0786 |  |  |  |  | 7.7758 | 6528.1674 |  |  |  |  | 7.604 | 6677.65 |  |  |  |  | 7.6859 | 6612.0786 | [6 empty] | 4.5789 | 10831.5671 | 4.5759 | 10729.551 |  |  | 4.5789 | 10831.5671 | 4.5759 | 10729.551 |  |  | 4.2755 | 289.4744 |  |  | 4.3936 | 11164.6599 |  |  | 4.2755 | 289.4744 |  |  | 4.3936 | 11164.6599
7.7758 | 6528.1674 |  |  |  |  | 7.604 | 6677.65 |  |  |  |  | 7.6859 | 6612.0786 |  |  |  |  | 7.7758 | 6528.1674 |  |  |  |  | 7.604 | 6677.65 |  |  |  |  | 7.6859 | 6612.0786 | [6 empty] | 4.5789 | 10831.5671 | 4.5759 | 10729.551 |  |  | 4.5789 | 10831.5671 | 4.5759 | 10729.551 |  |  | 4.2755 | 289.4744 |  |  | 4.3936 | 11164.6599 |  |  | 4.2755 | 289.4744 |  |  | 4.3936 | 11164.6599
7.7261 | 6576.1687 |  |  |  |  | 7.5367 | 6726.7504 |  |  |  |  | 7.6261 | 6660.6968 |  |  |  |  | 7.7261 | 6576.1687 |  |  |  |  | 7.5367 | 6726.7504 |  |  |  |  | 7.6261 | 6660.6968 | [6 empty] | 4.4971 | 10911.211 | 4.5213 | 10808.4448 |  |  | 4.4971 | 10911.211 | 4.5213 | 10808.4448 |  |  | 4.2526 | 291.6029 |  |  | 4.3936 | 11246.753 |  |  | 4.2526 | 291.6029 |  |  | 4.3936 | 11246.753
7.7261 | 6576.1687 |  |  |  |  | 7.5367 | 6726.7504 |  |  |  |  | 7.6261 | 6660.6968 |  |  |  |  | 7.7261 | 6576.1687 |  |  |  |  | 7.5367 | 6726.7504 |  |  |  |  | 7.6261 | 6660.6968 | [6 empty] | 4.4971 | 10911.211 | 4.5213 | 10808.4448 |  |  | 4.4971 | 10911.211 | 4.5213 | 10808.4448 |  |  | 4.2526 | 291.6029 |  |  | 4.3936 | 11246.753 |  |  | 4.2526 | 291.6029 |  |  | 4.3936 | 11246.753
7.6684 | 6624.1699 |  |  |  |  | 7.4642 | 6775.8508 |  |  |  |  | 7.5569 | 6709.315 |  |  |  |  | 7.6684 | 6624.1699 |  |  |  |  | 7.4642 | 6775.8508 |  |  |  |  | 7.5569 | 6709.315 | [6 empty] | 4.4971 | 10990.8549 | 4.4297 | 10887.3386 |  |  | 4.4971 | 10990.8549 | 4.4297 | 10887.3386 |  |  | 4.2202 | 293.7314 |  |  | 4.3152 | 11328.8461 |  |  | 4.2202 | 293.7314 |  |  | 4.3152 | 11328.8461
7.6684 | 6624.1699 |  |  |  |  | 7.4642 | 6775.8508 |  |  |  |  | 7.5569 | 6709.315 |  |  |  |  | 7.6684 | 6624.1699 |  |  |  |  | 7.4642 | 6775.8508 |  |  |  |  | 7.5569 | 6709.315 | [6 empty] | 4.4971 | 10990.8549 | 4.4297 | 10887.3386 |  |  | 4.4971 | 10990.8549 | 4.4297 | 10887.3386 |  |  | 4.2202 | 293.7314 |  |  | 4.3152 | 11328.8461 |  |  | 4.2202 | 293.7314 |  |  | 4.3152 | 11328.8461
7.602 | 6672.1711 |  |  |  |  | 7.3785 | 6824.9511 |  |  |  |  | 7.488 | 6757.9332 |  |  |  |  | 7.602 | 6672.1711 |  |  |  |  | 7.3785 | 6824.9511 |  |  |  |  | 7.488 | 6757.9332 | [6 empty] | 4.4041 | 11070.4988 | 4.3902 | 10966.2323 |  |  | 4.4041 | 11070.4988 | 4.3902 | 10966.2323 |  |  | 4.2112 | 295.8598 |  |  | 4.3152 | 11410.9392 |  |  | 4.2112 | 295.8598 |  |  | 4.3152 | 11410.9392
7.602 | 6672.1711 |  |  |  |  | 7.3785 | 6824.9511 |  |  |  |  | 7.488 | 6757.9332 |  |  |  |  | 7.602 | 6672.1711 |  |  |  |  | 7.3785 | 6824.9511 |  |  |  |  | 7.488 | 6757.9332 | [6 empty] | 4.4041 | 11070.4988 | 4.3902 | 10966.2323 |  |  | 4.4041 | 11070.4988 | 4.3902 | 10966.2323 |  |  | 4.2112 | 295.8598 |  |  | 4.3152 | 11410.9392 |  |  | 4.2112 | 295.8598 |  |  | 4.3152 | 11410.9392
7.5373 | 6720.1724 |  |  |  |  | 7.2934 | 6874.0515 |  |  |  |  | 7.4016 | 6806.5515 |  |  |  |  | 7.5373 | 6720.1724 |  |  |  |  | 7.2934 | 6874.0515 |  |  |  |  | 7.4016 | 6806.5515 | [6 empty] | 4.3923 | 11150.1426 | 4.3783 | 11045.1261 |  |  | 4.3923 | 11150.1426 | 4.3783 | 11045.1261 |  |  | 4.1941 | 297.9883 |  |  | 4.3063 | 11493.0323 |  |  | 4.1941 | 297.9883 |  |  | 4.3063 | 11493.0323
7.5373 | 6720.1724 |  |  |  |  | 7.2934 | 6874.0515 |  |  |  |  | 7.4016 | 6806.5515 |  |  |  |  | 7.5373 | 6720.1724 |  |  |  |  | 7.2934 | 6874.0515 |  |  |  |  | 7.4016 | 6806.5515 | [6 empty] | 4.3923 | 11150.1426 | 4.3783 | 11045.1261 |  |  | 4.3923 | 11150.1426 | 4.3783 | 11045.1261 |  |  | 4.1941 | 297.9883 |  |  | 4.3063 | 11493.0323 |  |  | 4.1941 | 297.9883 |  |  | 4.3063 | 11493.0323
7.457 | 6768.1736 |  |  |  |  | 7.2059 | 6923.1519 |  |  |  |  | 7.3248 | 6855.1697 |  |  |  |  | 7.457 | 6768.1736 |  |  |  |  | 7.2059 | 6923.1519 |  |  |  |  | 7.3248 | 6855.1697 | [6 empty] | 4.3839 | 11229.7865 | 4.2905 | 11124.0198 |  |  | 4.3839 | 11229.7865 | 4.2905 | 11124.0198 |  |  | 4.1899 | 300.1168 |  |  | 4.3027 | 11575.1254 |  |  | 4.1899 | 300.1168 |  |  | 4.3027 | 11575.1254
7.457 | 6768.1736 |  |  |  |  | 7.2059 | 6923.1519 |  |  |  |  | 7.3248 | 6855.1697 |  |  |  |  | 7.457 | 6768.1736 |  |  |  |  | 7.2059 | 6923.1519 |  |  |  |  | 7.3248 | 6855.1697 | [6 empty] | 4.3839 | 11229.7865 | 4.2905 | 11124.0198 |  |  | 4.3839 | 11229.7865 | 4.2905 | 11124.0198 |  |  | 4.1899 | 300.1168 |  |  | 4.3027 | 11575.1254 |  |  | 4.1899 | 300.1168 |  |  | 4.3027 | 11575.1254
7.3739 | 6816.1748 |  |  |  |  | 7.1183 | 6972.2522 |  |  |  |  | 7.2462 | 6903.7879 |  |  |  |  | 7.3739 | 6816.1748 |  |  |  |  | 7.1183 | 6972.2522 |  |  |  |  | 7.2462 | 6903.7879 | [6 empty] | 4.2965 | 11309.4304 | 4.2905 | 11202.9136 |  |  | 4.2965 | 11309.4304 | 4.2905 | 11202.9136 |  |  | 4.1518 | 302.2453 |  |  | 4.3027 | 11657.2185 |  |  | 4.1518 | 302.2453 |  |  | 4.3027 | 11657.2185
7.3739 | 6816.1748 |  |  |  |  | 7.1183 | 6972.2522 |  |  |  |  | 7.2462 | 6903.7879 |  |  |  |  | 7.3739 | 6816.1748 |  |  |  |  | 7.1183 | 6972.2522 |  |  |  |  | 7.2462 | 6903.7879 | [6 empty] | 4.2965 | 11309.4304 | 4.2905 | 11202.9136 |  |  | 4.2965 | 11309.4304 | 4.2905 | 11202.9136 |  |  | 4.1518 | 302.2453 |  |  | 4.3027 | 11657.2185 |  |  | 4.1518 | 302.2453 |  |  | 4.3027 | 11657.2185
7.2915 | 6864.176 |  |  |  |  | 7.0391 | 7021.3526 |  |  |  |  | 7.1559 | 6952.4061 |  |  |  |  | 7.2915 | 6864.176 |  |  |  |  | 7.0391 | 7021.3526 |  |  |  |  | 7.1559 | 6952.4061 | [6 empty] | 4.2936 | 11389.0743 | 4.2803 | 11281.8074 |  |  | 4.2936 | 11389.0743 | 4.2803 | 11281.8074 |  |  | 4.128 | 304.3738 |  |  | 4.2927 | 11739.3116 |  |  | 4.128 | 304.3738 |  |  | 4.2927 | 11739.3116
7.2915 | 6864.176 |  |  |  |  | 7.0391 | 7021.3526 |  |  |  |  | 7.1559 | 6952.4061 |  |  |  |  | 7.2915 | 6864.176 |  |  |  |  | 7.0391 | 7021.3526 |  |  |  |  | 7.1559 | 6952.4061 | [6 empty] | 4.2936 | 11389.0743 | 4.2803 | 11281.8074 |  |  | 4.2936 | 11389.0743 | 4.2803 | 11281.8074 |  |  | 4.128 | 304.3738 |  |  | 4.2927 | 11739.3116 |  |  | 4.128 | 304.3738 |  |  | 4.2927 | 11739.3116
7.1958 | 6912.1773 |  |  |  |  | 6.9482 | 7070.453 |  |  |  |  | 7.0663 | 7001.0244 |  |  |  |  | 7.1958 | 6912.1773 |  |  |  |  | 6.9482 | 7070.453 |  |  |  |  | 7.0663 | 7001.0244 | [6 empty] | 4.2936 | 11468.7181 | 4.2677 | 11360.7011 |  |  | 4.2936 | 11468.7181 | 4.2677 | 11360.7011 |  |  | 4.0337 | 306.5023 |  |  | 4.2834 | 11821.4046 |  |  | 4.0337 | 306.5023 |  |  | 4.2834 | 11821.4046
7.1958 | 6912.1773 |  |  |  |  | 6.9482 | 7070.453 |  |  |  |  | 7.0663 | 7001.0244 |  |  |  |  | 7.1958 | 6912.1773 |  |  |  |  | 6.9482 | 7070.453 |  |  |  |  | 7.0663 | 7001.0244 | [6 empty] | 4.2936 | 11468.7181 | 4.2677 | 11360.7011 |  |  | 4.2936 | 11468.7181 | 4.2677 | 11360.7011 |  |  | 4.0337 | 306.5023 |  |  | 4.2834 | 11821.4046 |  |  | 4.0337 | 306.5023 |  |  | 4.2834 | 11821.4046
7.1336 | 6960.1785 |  |  |  |  | 6.857 | 7119.5533 |  |  |  |  | 6.9628 | 7049.6426 |  |  |  |  | 7.1336 | 6960.1785 |  |  |  |  | 6.857 | 7119.5533 |  |  |  |  | 6.9628 | 7049.6426 | [6 empty] | 4.2936 | 11548.362 | 4.2677 | 11439.5949 |  |  | 4.2936 | 11548.362 | 4.2677 | 11439.5949 |  |  | 3.9692 | 308.6308 |  |  | 4.2834 | 11903.4977 |  |  | 3.9692 | 308.6308 |  |  | 4.2834 | 11903.4977
7.1336 | 6960.1785 |  |  |  |  | 6.857 | 7119.5533 |  |  |  |  | 6.9628 | 7049.6426 |  |  |  |  | 7.1336 | 6960.1785 |  |  |  |  | 6.857 | 7119.5533 |  |  |  |  | 6.9628 | 7049.6426 | [6 empty] | 4.2936 | 11548.362 | 4.2677 | 11439.5949 |  |  | 4.2936 | 11548.362 | 4.2677 | 11439.5949 |  |  | 3.9692 | 308.6308 |  |  | 4.2834 | 11903.4977 |  |  | 3.9692 | 308.6308 |  |  | 4.2834 | 11903.4977
7.0479 | 7008.1797 |  |  |  |  | 6.7718 | 7168.6537 |  |  |  |  | 6.8756 | 7098.2608 |  |  |  |  | 7.0479 | 7008.1797 |  |  |  |  | 6.7718 | 7168.6537 |  |  |  |  | 6.8756 | 7098.2608 | [6 empty] | 4.2936 | 11628.0059 | 4.2578 | 11518.4886 |  |  | 4.2936 | 11628.0059 | 4.2578 | 11518.4886 |  |  | 3.9438 | 310.7593 |  |  | 4.2113 | 11985.5908 |  |  | 3.9438 | 310.7593 |  |  | 4.2113 | 11985.5908
7.0479 | 7008.1797 |  |  |  |  | 6.7718 | 7168.6537 |  |  |  |  | 6.8756 | 7098.2608 |  |  |  |  | 7.0479 | 7008.1797 |  |  |  |  | 6.7718 | 7168.6537 |  |  |  |  | 6.8756 | 7098.2608 | [6 empty] | 4.2936 | 11628.0059 | 4.2578 | 11518.4886 |  |  | 4.2936 | 11628.0059 | 4.2578 | 11518.4886 |  |  | 3.9438 | 310.7593 |  |  | 4.2113 | 11985.5908 |  |  | 3.9438 | 310.7593 |  |  | 4.2113 | 11985.5908
6.9657 | 7056.181 |  |  |  |  | 6.689 | 7217.7541 |  |  |  |  | 6.7972 | 7146.879 |  |  |  |  | 6.9657 | 7056.181 |  |  |  |  | 6.689 | 7217.7541 |  |  |  |  | 6.7972 | 7146.879 | [6 empty] | 4.2898 | 11707.6498 | 4.2259 | 11597.3824 |  |  | 4.2898 | 11707.6498 | 4.2259 | 11597.3824 |  |  | 3.9295 | 312.8877 |  |  | 4.2103 | 12067.6839 |  |  | 3.9295 | 312.8877 |  |  | 4.2103 | 12067.6839
6.9657 | 7056.181 |  |  |  |  | 6.689 | 7217.7541 |  |  |  |  | 6.7972 | 7146.879 |  |  |  |  | 6.9657 | 7056.181 |  |  |  |  | 6.689 | 7217.7541 |  |  |  |  | 6.7972 | 7146.879 | [6 empty] | 4.2898 | 11707.6498 | 4.2259 | 11597.3824 |  |  | 4.2898 | 11707.6498 | 4.2259 | 11597.3824 |  |  | 3.9295 | 312.8877 |  |  | 4.2103 | 12067.6839 |  |  | 3.9295 | 312.8877 |  |  | 4.2103 | 12067.6839
6.8661 | 7104.1822 |  |  |  |  | 6.5599 | 7266.8544 |  |  |  |  | 6.7217 | 7195.4973 |  |  |  |  | 6.8661 | 7104.1822 |  |  |  |  | 6.5599 | 7266.8544 |  |  |  |  | 6.7217 | 7195.4973 | [6 empty] | 4.2898 | 11787.2936 | 4.2259 | 11676.2761 |  |  | 4.2898 | 11787.2936 | 4.2259 | 11676.2761 |  |  | 3.9217 | 315.0162 |  |  | 4.2103 | 12149.777 |  |  | 3.9217 | 315.0162 |  |  | 4.2103 | 12149.777
6.8661 | 7104.1822 |  |  |  |  | 6.5599 | 7266.8544 |  |  |  |  | 6.7217 | 7195.4973 |  |  |  |  | 6.8661 | 7104.1822 |  |  |  |  | 6.5599 | 7266.8544 |  |  |  |  | 6.7217 | 7195.4973 | [6 empty] | 4.2898 | 11787.2936 | 4.2259 | 11676.2761 |  |  | 4.2898 | 11787.2936 | 4.2259 | 11676.2761 |  |  | 3.9217 | 315.0162 |  |  | 4.2103 | 12149.777 |  |  | 3.9217 | 315.0162 |  |  | 4.2103 | 12149.777
6.7792 | 7152.1834 |  |  |  |  | 6.4725 | 7315.9548 |  |  |  |  | 6.6457 | 7244.1155 |  |  |  |  | 6.7792 | 7152.1834 |  |  |  |  | 6.4725 | 7315.9548 |  |  |  |  | 6.6457 | 7244.1155 | [6 empty] | 4.2804 | 11866.9375 | 4.1836 | 11755.1699 |  |  | 4.2804 | 11866.9375 | 4.1836 | 11755.1699 |  |  | 3.9178 | 317.1447 |  |  | 4.1784 | 12231.8701 |  |  | 3.9178 | 317.1447 |  |  | 4.1784 | 12231.8701
6.7792 | 7152.1834 |  |  |  |  | 6.4725 | 7315.9548 |  |  |  |  | 6.6457 | 7244.1155 |  |  |  |  | 6.7792 | 7152.1834 |  |  |  |  | 6.4725 | 7315.9548 |  |  |  |  | 6.6457 | 7244.1155 | [6 empty] | 4.2804 | 11866.9375 | 4.1836 | 11755.1699 |  |  | 4.2804 | 11866.9375 | 4.1836 | 11755.1699 |  |  | 3.9178 | 317.1447 |  |  | 4.1784 | 12231.8701 |  |  | 3.9178 | 317.1447 |  |  | 4.1784 | 12231.8701
6.6992 | 7200.1847 |  |  |  |  | 6.3829 | 7365.0552 |  |  |  |  | 6.5244 | 7292.7337 |  |  |  |  | 6.6992 | 7200.1847 |  |  |  |  | 6.3829 | 7365.0552 |  |  |  |  | 6.5244 | 7292.7337 | [6 empty] | 4.2796 | 11946.5814 | 4.1496 | 11834.0637 |  |  | 4.2796 | 11946.5814 | 4.1496 | 11834.0637 |  |  | 3.8279 | 319.2732 |  |  | 4.1773 | 12313.9632 |  |  | 3.8279 | 319.2732 |  |  | 4.1773 | 12313.9632
6.6992 | 7200.1847 |  |  |  |  | 6.3829 | 7365.0552 |  |  |  |  | 6.5244 | 7292.7337 |  |  |  |  | 6.6992 | 7200.1847 |  |  |  |  | 6.3829 | 7365.0552 |  |  |  |  | 6.5244 | 7292.7337 | [6 empty] | 4.2796 | 11946.5814 | 4.1496 | 11834.0637 |  |  | 4.2796 | 11946.5814 | 4.1496 | 11834.0637 |  |  | 3.8279 | 319.2732 |  |  | 4.1773 | 12313.9632 |  |  | 3.8279 | 319.2732 |  |  | 4.1773 | 12313.9632
6.6338 | 7248.1859 |  |  |  |  | 6.3177 | 7414.1555 |  |  |  |  | 6.4739 | 7341.3519 |  |  |  |  | 6.6338 | 7248.1859 |  |  |  |  | 6.3177 | 7414.1555 |  |  |  |  | 6.4739 | 7341.3519 | [6 empty] | 4.2796 | 12026.2253 | 4.0481 | 11912.9574 |  |  | 4.2796 | 12026.2253 | 4.0481 | 11912.9574 |  |  | 3.6314 | 321.4017 |  |  | 4.1734 | 12396.0563 |  |  | 3.6314 | 321.4017 |  |  | 4.1734 | 12396.0563
6.6338 | 7248.1859 |  |  |  |  | 6.3177 | 7414.1555 |  |  |  |  | 6.4739 | 7341.3519 |  |  |  |  | 6.6338 | 7248.1859 |  |  |  |  | 6.3177 | 7414.1555 |  |  |  |  | 6.4739 | 7341.3519 | [6 empty] | 4.2796 | 12026.2253 | 4.0481 | 11912.9574 |  |  | 4.2796 | 12026.2253 | 4.0481 | 11912.9574 |  |  | 3.6314 | 321.4017 |  |  | 4.1734 | 12396.0563 |  |  | 3.6314 | 321.4017 |  |  | 4.1734 | 12396.0563
6.53 | 7296.1871 |  |  |  |  | 6.2408 | 7463.2559 |  |  |  |  | 6.3824 | 7389.9702 |  |  |  |  | 6.53 | 7296.1871 |  |  |  |  | 6.2408 | 7463.2559 |  |  |  |  | 6.3824 | 7389.9702 | [6 empty] | 4.2765 | 12105.8691 | 4.0429 | 11991.8512 |  |  | 4.2765 | 12105.8691 | 4.0429 | 11991.8512 |  |  | 3.5804 | 323.5302 |  |  | 4.1734 | 12478.1493 |  |  | 3.5804 | 323.5302 |  |  | 4.1734 | 12478.1493
6.53 | 7296.1871 |  |  |  |  | 6.2408 | 7463.2559 |  |  |  |  | 6.3824 | 7389.9702 |  |  |  |  | 6.53 | 7296.1871 |  |  |  |  | 6.2408 | 7463.2559 |  |  |  |  | 6.3824 | 7389.9702 | [6 empty] | 4.2765 | 12105.8691 | 4.0429 | 11991.8512 |  |  | 4.2765 | 12105.8691 | 4.0429 | 11991.8512 |  |  | 3.5804 | 323.5302 |  |  | 4.1734 | 12478.1493 |  |  | 3.5804 | 323.5302 |  |  | 4.1734 | 12478.1493
6.4412 | 7344.1884 |  |  |  |  | 6.1774 | 7512.3563 |  |  |  |  | 6.2872 | 7438.5884 |  |  |  |  | 6.4412 | 7344.1884 |  |  |  |  | 6.1774 | 7512.3563 |  |  |  |  | 6.2872 | 7438.5884 | [6 empty] | 4.1745 | 12185.513 | 4.0376 | 12070.7449 |  |  | 4.1745 | 12185.513 | 4.0376 | 12070.7449 |  |  | 3.5559 | 325.6587 |  |  | 4.1684 | 12560.2424 |  |  | 3.5559 | 325.6587 |  |  | 4.1684 | 12560.2424
6.4412 | 7344.1884 |  |  |  |  | 6.1774 | 7512.3563 |  |  |  |  | 6.2872 | 7438.5884 |  |  |  |  | 6.4412 | 7344.1884 |  |  |  |  | 6.1774 | 7512.3563 |  |  |  |  | 6.2872 | 7438.5884 | [6 empty] | 4.1745 | 12185.513 | 4.0376 | 12070.7449 |  |  | 4.1745 | 12185.513 | 4.0376 | 12070.7449 |  |  | 3.5559 | 325.6587 |  |  | 4.1684 | 12560.2424 |  |  | 3.5559 | 325.6587 |  |  | 4.1684 | 12560.2424
6.3119 | 7392.1896 |  |  |  |  | 6.0697 | 7561.4566 |  |  |  |  | 6.1964 | 7487.2066 |  |  |  |  | 6.3119 | 7392.1896 |  |  |  |  | 6.0697 | 7561.4566 |  |  |  |  | 6.1964 | 7487.2066 | [6 empty] | 4.1695 | 12265.1569 | 4.0376 | 12149.6387 |  |  | 4.1695 | 12265.1569 | 4.0376 | 12149.6387 |  |  | 3.5227 | 327.7872 |  |  | 4.156 | 12642.3355 |  |  | 3.5227 | 327.7872 |  |  | 4.156 | 12642.3355
6.3119 | 7392.1896 |  |  |  |  | 6.0697 | 7561.4566 |  |  |  |  | 6.1964 | 7487.2066 |  |  |  |  | 6.3119 | 7392.1896 |  |  |  |  | 6.0697 | 7561.4566 |  |  |  |  | 6.1964 | 7487.2066 | [6 empty] | 4.1695 | 12265.1569 | 4.0376 | 12149.6387 |  |  | 4.1695 | 12265.1569 | 4.0376 | 12149.6387 |  |  | 3.5227 | 327.7872 |  |  | 4.156 | 12642.3355 |  |  | 3.5227 | 327.7872 |  |  | 4.156 | 12642.3355
6.2395 | 7440.1908 |  |  |  |  | 5.9557 | 7610.557 |  |  |  |  | 6.1356 | 7535.8248 |  |  |  |  | 6.2395 | 7440.1908 |  |  |  |  | 5.9557 | 7610.557 |  |  |  |  | 6.1356 | 7535.8248 | [6 empty] | 4.1684 | 12344.8008 | 4.0016 | 12228.5324 |  |  | 4.1684 | 12344.8008 | 4.0016 | 12228.5324 |  |  | 3.4921 | 329.9156 |  |  | 4.156 | 12724.4286 |  |  | 3.4921 | 329.9156 |  |  | 4.156 | 12724.4286
6.2395 | 7440.1908 |  |  |  |  | 5.9557 | 7610.557 |  |  |  |  | 6.1356 | 7535.8248 |  |  |  |  | 6.2395 | 7440.1908 |  |  |  |  | 5.9557 | 7610.557 |  |  |  |  | 6.1356 | 7535.8248 | [6 empty] | 4.1684 | 12344.8008 | 4.0016 | 12228.5324 |  |  | 4.1684 | 12344.8008 | 4.0016 | 12228.5324 |  |  | 3.4921 | 329.9156 |  |  | 4.156 | 12724.4286 |  |  | 3.4921 | 329.9156 |  |  | 4.156 | 12724.4286
6.1876 | 7488.1921 |  |  |  |  | 5.8589 | 7659.6574 |  |  |  |  | 6.0969 | 7584.4431 |  |  |  |  | 6.1876 | 7488.1921 |  |  |  |  | 5.8589 | 7659.6574 |  |  |  |  | 6.0969 | 7584.4431 | [6 empty] | 4.1684 | 12424.4446 | 3.9958 | 12307.4262 |  |  | 4.1684 | 12424.4446 | 3.9958 | 12307.4262 |  |  | 3.4648 | 332.0441 |  |  | 4.156 | 12806.5217 |  |  | 3.4648 | 332.0441 |  |  | 4.156 | 12806.5217
6.1876 | 7488.1921 |  |  |  |  | 5.8589 | 7659.6574 |  |  |  |  | 6.0969 | 7584.4431 |  |  |  |  | 6.1876 | 7488.1921 |  |  |  |  | 5.8589 | 7659.6574 |  |  |  |  | 6.0969 | 7584.4431 | [6 empty] | 4.1684 | 12424.4446 | 3.9958 | 12307.4262 |  |  | 4.1684 | 12424.4446 | 3.9958 | 12307.4262 |  |  | 3.4648 | 332.0441 |  |  | 4.156 | 12806.5217 |  |  | 3.4648 | 332.0441 |  |  | 4.156 | 12806.5217
6.1108 | 7536.1933 |  |  |  |  | 5.8019 | 7708.7577 |  |  |  |  | 6.0193 | 7633.0613 |  |  |  |  | 6.1108 | 7536.1933 |  |  |  |  | 5.8019 | 7708.7577 |  |  |  |  | 6.0193 | 7633.0613 | [6 empty] | 4.1684 | 12504.0885 | 3.9423 | 12386.32 |  |  | 4.1684 | 12504.0885 | 3.9423 | 12386.32 |  |  | 3.4648 | 334.1726 |  |  | 4.1153 | 12888.6148 |  |  | 3.4648 | 334.1726 |  |  | 4.1153 | 12888.6148
6.1108 | 7536.1933 |  |  |  |  | 5.8019 | 7708.7577 |  |  |  |  | 6.0193 | 7633.0613 |  |  |  |  | 6.1108 | 7536.1933 |  |  |  |  | 5.8019 | 7708.7577 |  |  |  |  | 6.0193 | 7633.0613 | [6 empty] | 4.1684 | 12504.0885 | 3.9423 | 12386.32 |  |  | 4.1684 | 12504.0885 | 3.9423 | 12386.32 |  |  | 3.4648 | 334.1726 |  |  | 4.1153 | 12888.6148 |  |  | 3.4648 | 334.1726 |  |  | 4.1153 | 12888.6148
6.0531 | 7584.1945 |  |  |  |  | 5.7568 | 7757.8581 |  |  |  |  | 5.9234 | 7681.6795 |  |  |  |  | 6.0531 | 7584.1945 |  |  |  |  | 5.7568 | 7757.8581 |  |  |  |  | 5.9234 | 7681.6795 | [6 empty] | 4.1684 | 12583.7324 | 3.9404 | 12465.2137 |  |  | 4.1684 | 12583.7324 | 3.9404 | 12465.2137 |  |  | 3.4232 | 336.3011 |  |  | 4.114 | 12970.7079 |  |  | 3.4232 | 336.3011 |  |  | 4.114 | 12970.7079
6.0531 | 7584.1945 |  |  |  |  | 5.7568 | 7757.8581 |  |  |  |  | 5.9234 | 7681.6795 |  |  |  |  | 6.0531 | 7584.1945 |  |  |  |  | 5.7568 | 7757.8581 |  |  |  |  | 5.9234 | 7681.6795 | [6 empty] | 4.1684 | 12583.7324 | 3.9404 | 12465.2137 |  |  | 4.1684 | 12583.7324 | 3.9404 | 12465.2137 |  |  | 3.4232 | 336.3011 |  |  | 4.114 | 12970.7079 |  |  | 3.4232 | 336.3011 |  |  | 4.114 | 12970.7079
5.9765 | 7632.1957 |  |  |  |  | 5.684 | 7806.9585 |  |  |  |  | 5.8765 | 7730.2977 |  |  |  |  | 5.9765 | 7632.1957 |  |  |  |  | 5.684 | 7806.9585 |  |  |  |  | 5.8765 | 7730.2977 | [6 empty] | 4.156 | 12663.3763 | 3.3517 | 12544.1075 |  |  | 4.156 | 12663.3763 | 3.3517 | 12544.1075 |  |  | 3.4169 | 338.4296 |  |  | 3.9903 | 13052.801 |  |  | 3.4169 | 338.4296 |  |  | 3.9903 | 13052.801
5.9765 | 7632.1957 |  |  |  |  | 5.684 | 7806.9585 |  |  |  |  | 5.8765 | 7730.2977 |  |  |  |  | 5.9765 | 7632.1957 |  |  |  |  | 5.684 | 7806.9585 |  |  |  |  | 5.8765 | 7730.2977 | [6 empty] | 4.156 | 12663.3763 | 3.3517 | 12544.1075 |  |  | 4.156 | 12663.3763 | 3.3517 | 12544.1075 |  |  | 3.4169 | 338.4296 |  |  | 3.9903 | 13052.801 |  |  | 3.4169 | 338.4296 |  |  | 3.9903 | 13052.801
5.9086 | 7680.197 |  |  |  |  | 5.6141 | 7856.0588 |  |  |  |  | 5.8512 | 7778.916 |  |  |  |  | 5.9086 | 7680.197 |  |  |  |  | 5.6141 | 7856.0588 |  |  |  |  | 5.8512 | 7778.916 | [6 empty] | 4.156 | 12743.0201 | 3.3517 | 12623.0012 |  |  | 4.156 | 12743.0201 | 3.3517 | 12623.0012 |  |  | 3.4169 | 340.5581 |  |  | 3.9903 | 13134.894 |  |  | 3.4169 | 340.5581 |  |  | 3.9903 | 13134.894
5.9086 | 7680.197 |  |  |  |  | 5.6141 | 7856.0588 |  |  |  |  | 5.8512 | 7778.916 |  |  |  |  | 5.9086 | 7680.197 |  |  |  |  | 5.6141 | 7856.0588 |  |  |  |  | 5.8512 | 7778.916 | [6 empty] | 4.156 | 12743.0201 | 3.3517 | 12623.0012 |  |  | 4.156 | 12743.0201 | 3.3517 | 12623.0012 |  |  | 3.4169 | 340.5581 |  |  | 3.9903 | 13134.894 |  |  | 3.4169 | 340.5581 |  |  | 3.9903 | 13134.894
5.8378 | 7728.1982 |  |  |  |  | 5.5577 | 7905.1592 |  |  |  |  | 5.7853 | 7827.5342 |  |  |  |  | 5.8378 | 7728.1982 |  |  |  |  | 5.5577 | 7905.1592 |  |  |  |  | 5.7853 | 7827.5342 | [6 empty] | 4.1508 | 12822.664 | 3.3517 | 12701.895 |  |  | 4.1508 | 12822.664 | 3.3517 | 12701.895 |  |  | 3.3417 | 342.6866 |  |  | 3.9827 | 13216.9871 |  |  | 3.3417 | 342.6866 |  |  | 3.9827 | 13216.9871
5.8378 | 7728.1982 |  |  |  |  | 5.5577 | 7905.1592 |  |  |  |  | 5.7853 | 7827.5342 |  |  |  |  | 5.8378 | 7728.1982 |  |  |  |  | 5.5577 | 7905.1592 |  |  |  |  | 5.7853 | 7827.5342 | [6 empty] | 4.1508 | 12822.664 | 3.3517 | 12701.895 |  |  | 4.1508 | 12822.664 | 3.3517 | 12701.895 |  |  | 3.3417 | 342.6866 |  |  | 3.9827 | 13216.9871 |  |  | 3.3417 | 342.6866 |  |  | 3.9827 | 13216.9871
5.7677 | 7776.1994 |  |  |  |  | 5.526 | 7954.2596 |  |  |  |  | 5.7242 | 7876.1524 |  |  |  |  | 5.7677 | 7776.1994 |  |  |  |  | 5.526 | 7954.2596 |  |  |  |  | 5.7242 | 7876.1524 | [6 empty] | 4.1508 | 12902.3079 | 3.297 | 12780.7887 |  |  | 4.1508 | 12902.3079 | 3.297 | 12780.7887 |  |  | 3.264 | 344.8151 |  |  | 3.9827 | 13299.0802 |  |  | 3.264 | 344.8151 |  |  | 3.9827 | 13299.0802
5.7677 | 7776.1994 |  |  |  |  | 5.526 | 7954.2596 |  |  |  |  | 5.7242 | 7876.1524 |  |  |  |  | 5.7677 | 7776.1994 |  |  |  |  | 5.526 | 7954.2596 |  |  |  |  | 5.7242 | 7876.1524 | [6 empty] | 4.1508 | 12902.3079 | 3.297 | 12780.7887 |  |  | 4.1508 | 12902.3079 | 3.297 | 12780.7887 |  |  | 3.264 | 344.8151 |  |  | 3.9827 | 13299.0802 |  |  | 3.264 | 344.8151 |  |  | 3.9827 | 13299.0802
5.6339 | 7824.2007 |  |  |  |  | 5.514 | 8003.36 |  |  |  |  | 5.663 | 7924.7706 |  |  |  |  | 5.6339 | 7824.2007 |  |  |  |  | 5.514 | 8003.36 |  |  |  |  | 5.663 | 7924.7706 | [6 empty] | 4.1508 | 12981.9518 | 3.297 | 12859.6825 |  |  | 4.1508 | 12981.9518 | 3.297 | 12859.6825 |  |  | 3.264 | 346.9436 |  |  | 3.9827 | 13381.1733 |  |  | 3.264 | 346.9436 |  |  | 3.9827 | 13381.1733
5.6339 | 7824.2007 |  |  |  |  | 5.514 | 8003.36 |  |  |  |  | 5.663 | 7924.7706 |  |  |  |  | 5.6339 | 7824.2007 |  |  |  |  | 5.514 | 8003.36 |  |  |  |  | 5.663 | 7924.7706 | [6 empty] | 4.1508 | 12981.9518 | 3.297 | 12859.6825 |  |  | 4.1508 | 12981.9518 | 3.297 | 12859.6825 |  |  | 3.264 | 346.9436 |  |  | 3.9827 | 13381.1733 |  |  | 3.264 | 346.9436 |  |  | 3.9827 | 13381.1733
5.6031 | 7872.2019 |  |  |  |  | 5.4461 | 8052.4603 |  |  |  |  | 5.5751 | 7973.3889 |  |  |  |  | 5.6031 | 7872.2019 |  |  |  |  | 5.4461 | 8052.4603 |  |  |  |  | 5.5751 | 7973.3889 | [6 empty] | 4.0953 | 13061.5956 |  |  |  |  | 4.0953 | 13061.5956 |  |  |  |  | 3.2457 | 349.072 |  |  | 3.9827 | 13463.2664 |  |  | 3.2457 | 349.072 |  |  | 3.9827 | 13463.2664
5.6031 | 7872.2019 |  |  |  |  | 5.4461 | 8052.4603 |  |  |  |  | 5.5751 | 7973.3889 |  |  |  |  | 5.6031 | 7872.2019 |  |  |  |  | 5.4461 | 8052.4603 |  |  |  |  | 5.5751 | 7973.3889 | [6 empty] | 4.0953 | 13061.5956 |  |  |  |  | 4.0953 | 13061.5956 |  |  |  |  | 3.2457 | 349.072 |  |  | 3.9827 | 13463.2664 |  |  | 3.2457 | 349.072 |  |  | 3.9827 | 13463.2664
5.5929 | 7920.2031 |  |  |  |  | 5.2881 | 8101.5607 |  |  |  |  | 5.4767 | 8022.0071 |  |  |  |  | 5.5929 | 7920.2031 |  |  |  |  | 5.2881 | 8101.5607 |  |  |  |  | 5.4767 | 8022.0071 | [6 empty] | 3.9827 | 13141.2395 |  |  |  |  | 3.9827 | 13141.2395 |  |  |  |  | 3.2266 | 351.2005 |  |  | 3.9827 | 13545.3595 |  |  | 3.2266 | 351.2005 |  |  | 3.9827 | 13545.3595
5.5929 | 7920.2031 |  |  |  |  | 5.2881 | 8101.5607 |  |  |  |  | 5.4767 | 8022.0071 |  |  |  |  | 5.5929 | 7920.2031 |  |  |  |  | 5.2881 | 8101.5607 |  |  |  |  | 5.4767 | 8022.0071 | [6 empty] | 3.9827 | 13141.2395 |  |  |  |  | 3.9827 | 13141.2395 |  |  |  |  | 3.2266 | 351.2005 |  |  | 3.9827 | 13545.3595 |  |  | 3.2266 | 351.2005 |  |  | 3.9827 | 13545.3595
5.5144 | 7968.2044 |  |  |  |  | 5.2148 | 8150.6611 |  |  |  |  | 5.3839 | 8070.6253 |  |  |  |  | 5.5144 | 7968.2044 |  |  |  |  | 5.2148 | 8150.6611 |  |  |  |  | 5.3839 | 8070.6253 | [6 empty] | 3.9827 | 13220.8834 |  |  |  |  | 3.9827 | 13220.8834 |  |  |  |  | 3.2266 | 353.329 |  |  | 3.8326 | 13627.4526 |  |  | 3.2266 | 353.329 |  |  | 3.8326 | 13627.4526
5.5144 | 7968.2044 |  |  |  |  | 5.2148 | 8150.6611 |  |  |  |  | 5.3839 | 8070.6253 |  |  |  |  | 5.5144 | 7968.2044 |  |  |  |  | 5.2148 | 8150.6611 |  |  |  |  | 5.3839 | 8070.6253 | [6 empty] | 3.9827 | 13220.8834 |  |  |  |  | 3.9827 | 13220.8834 |  |  |  |  | 3.2266 | 353.329 |  |  | 3.8326 | 13627.4526 |  |  | 3.2266 | 353.329 |  |  | 3.8326 | 13627.4526
5.3573 | 8016.2056 |  |  |  |  | 5.2057 | 8199.7614 |  |  |  |  | 5.3835 | 8119.2435 |  |  |  |  | 5.3573 | 8016.2056 |  |  |  |  | 5.2057 | 8199.7614 |  |  |  |  | 5.3835 | 8119.2435 | [6 empty] | 3.9827 | 13300.5273 |  |  |  |  | 3.9827 | 13300.5273 |  |  |  |  | 3.1801 | 355.4575 |  |  | 3.8326 | 13709.5457 |  |  | 3.1801 | 355.4575 |  |  | 3.8326 | 13709.5457
5.3573 | 8016.2056 |  |  |  |  | 5.2057 | 8199.7614 |  |  |  |  | 5.3835 | 8119.2435 |  |  |  |  | 5.3573 | 8016.2056 |  |  |  |  | 5.2057 | 8199.7614 |  |  |  |  | 5.3835 | 8119.2435 | [6 empty] | 3.9827 | 13300.5273 |  |  |  |  | 3.9827 | 13300.5273 |  |  |  |  | 3.1801 | 355.4575 |  |  | 3.8326 | 13709.5457 |  |  | 3.1801 | 355.4575 |  |  | 3.8326 | 13709.5457
5.3038 | 8064.2068 |  |  |  |  | 5.1495 | 8248.8618 |  |  |  |  | 5.2381 | 8167.8617 |  |  |  |  | 5.3038 | 8064.2068 |  |  |  |  | 5.1495 | 8248.8618 |  |  |  |  | 5.2381 | 8167.8617 | [6 empty] | 3.9827 | 13380.1712 |  |  |  |  | 3.9827 | 13380.1712 |  |  |  |  | 3.1579 | 357.586 |  |  | 3.6014 | 13791.6388 |  |  | 3.1579 | 357.586 |  |  | 3.6014 | 13791.6388
5.3038 | 8064.2068 |  |  |  |  | 5.1495 | 8248.8618 |  |  |  |  | 5.2381 | 8167.8617 |  |  |  |  | 5.3038 | 8064.2068 |  |  |  |  | 5.1495 | 8248.8618 |  |  |  |  | 5.2381 | 8167.8617 | [6 empty] | 3.9827 | 13380.1712 |  |  |  |  | 3.9827 | 13380.1712 |  |  |  |  | 3.1579 | 357.586 |  |  | 3.6014 | 13791.6388 |  |  | 3.1579 | 357.586 |  |  | 3.6014 | 13791.6388
5.2344 | 8112.2081 |  |  |  |  | 5.0081 | 8297.9622 |  |  |  |  | 5.2298 | 8216.48 |  |  |  |  | 5.2344 | 8112.2081 |  |  |  |  | 5.0081 | 8297.9622 |  |  |  |  | 5.2298 | 8216.48 | [6 empty] | 3.8326 | 13459.815 |  |  |  |  | 3.8326 | 13459.815 |  |  |  |  | 3.1579 | 359.7145 |  |  | 3.6014 | 13873.7318 |  |  | 3.1579 | 359.7145 |  |  | 3.6014 | 13873.7318
5.2344 | 8112.2081 |  |  |  |  | 5.0081 | 8297.9622 |  |  |  |  | 5.2298 | 8216.48 |  |  |  |  | 5.2344 | 8112.2081 |  |  |  |  | 5.0081 | 8297.9622 |  |  |  |  | 5.2298 | 8216.48 | [6 empty] | 3.8326 | 13459.815 |  |  |  |  | 3.8326 | 13459.815 |  |  |  |  | 3.1579 | 359.7145 |  |  | 3.6014 | 13873.7318 |  |  | 3.1579 | 359.7145 |  |  | 3.6014 | 13873.7318
4.8332 | 8160.2093 |  |  |  |  | 4.645 | 8347.0625 |  |  |  |  | 5.1109 | 8265.0982 |  |  |  |  | 4.8332 | 8160.2093 |  |  |  |  | 4.645 | 8347.0625 |  |  |  |  | 5.1109 | 8265.0982 | [6 empty] | 3.8326 | 13539.4589 |  |  |  |  | 3.8326 | 13539.4589 |  |  |  |  | 3.1579 | 361.843 |  |  | 3.4541 | 13955.8249 |  |  | 3.1579 | 361.843 |  |  | 3.4541 | 13955.8249
4.8332 | 8160.2093 |  |  |  |  | 4.645 | 8347.0625 |  |  |  |  | 5.1109 | 8265.0982 |  |  |  |  | 4.8332 | 8160.2093 |  |  |  |  | 4.645 | 8347.0625 |  |  |  |  | 5.1109 | 8265.0982 | [6 empty] | 3.8326 | 13539.4589 |  |  |  |  | 3.8326 | 13539.4589 |  |  |  |  | 3.1579 | 361.843 |  |  | 3.4541 | 13955.8249 |  |  | 3.1579 | 361.843 |  |  | 3.4541 | 13955.8249
4.8214 | 8208.2105 |  |  |  |  | 4.3836 | 8396.1629 |  |  |  |  | 4.9879 | 8313.7164 |  |  |  |  | 4.8214 | 8208.2105 |  |  |  |  | 4.3836 | 8396.1629 |  |  |  |  | 4.9879 | 8313.7164 | [6 empty] | 3.8326 | 13619.1028 |  |  |  |  | 3.8326 | 13619.1028 |  |  |  |  | 3.1344 | 363.9715 |  |  | 3.4541 | 14037.918 |  |  | 3.1344 | 363.9715 |  |  | 3.4541 | 14037.918
4.8214 | 8208.2105 |  |  |  |  | 4.3836 | 8396.1629 |  |  |  |  | 4.9879 | 8313.7164 |  |  |  |  | 4.8214 | 8208.2105 |  |  |  |  | 4.3836 | 8396.1629 |  |  |  |  | 4.9879 | 8313.7164 | [6 empty] | 3.8326 | 13619.1028 |  |  |  |  | 3.8326 | 13619.1028 |  |  |  |  | 3.1344 | 363.9715 |  |  | 3.4541 | 14037.918 |  |  | 3.1344 | 363.9715 |  |  | 3.4541 | 14037.918
4.5758 | 8256.2117 |  |  |  |  | 4.1045 | 8445.2633 |  |  |  |  | 4.4549 | 8362.3346 |  |  |  |  | 4.5758 | 8256.2117 |  |  |  |  | 4.1045 | 8445.2633 |  |  |  |  | 4.4549 | 8362.3346 | [6 empty] | 3.8326 | 13698.7467 |  |  |  |  | 3.8326 | 13698.7467 |  |  |  |  | 3.1222 | 366.0999 |  |  | 3.4541 | 14120.0111 |  |  | 3.1222 | 366.0999 |  |  | 3.4541 | 14120.0111
4.5758 | 8256.2117 |  |  |  |  | 4.1045 | 8445.2633 |  |  |  |  | 4.4549 | 8362.3346 |  |  |  |  | 4.5758 | 8256.2117 |  |  |  |  | 4.1045 | 8445.2633 |  |  |  |  | 4.4549 | 8362.3346 | [6 empty] | 3.8326 | 13698.7467 |  |  |  |  | 3.8326 | 13698.7467 |  |  |  |  | 3.1222 | 366.0999 |  |  | 3.4541 | 14120.0111 |  |  | 3.1222 | 366.0999 |  |  | 3.4541 | 14120.0111
4.4181 | 8304.213 |  |  |  |  | 4.0806 | 8494.3636 |  |  |  |  | 4.1895 | 8410.9529 |  |  |  |  | 4.4181 | 8304.213 |  |  |  |  | 4.0806 | 8494.3636 |  |  |  |  | 4.1895 | 8410.9529 | [6 empty] | 3.8326 | 13778.3905 |  |  |  |  | 3.8326 | 13778.3905 |  |  |  |  | 3.0833 | 368.2284 |  |  | 3.4541 | 14202.1042 |  |  | 3.0833 | 368.2284 |  |  | 3.4541 | 14202.1042
4.4181 | 8304.213 |  |  |  |  | 4.0806 | 8494.3636 |  |  |  |  | 4.1895 | 8410.9529 |  |  |  |  | 4.4181 | 8304.213 |  |  |  |  | 4.0806 | 8494.3636 |  |  |  |  | 4.1895 | 8410.9529 | [6 empty] | 3.8326 | 13778.3905 |  |  |  |  | 3.8326 | 13778.3905 |  |  |  |  | 3.0833 | 368.2284 |  |  | 3.4541 | 14202.1042 |  |  | 3.0833 | 368.2284 |  |  | 3.4541 | 14202.1042
4.4181 | 8352.2142 |  |  |  |  | 4.0758 | 8543.464 |  |  |  |  | 4.1847 | 8459.5711 |  |  |  |  | 4.4181 | 8352.2142 |  |  |  |  | 4.0758 | 8543.464 |  |  |  |  | 4.1847 | 8459.5711 | [6 empty] | 3.4541 | 13858.0344 |  |  |  |  | 3.4541 | 13858.0344 |  |  |  |  | 3.0833 | 370.3569 |  |  | 3.2296 | 14284.1973 |  |  | 3.0833 | 370.3569 |  |  | 3.2296 | 14284.1973
4.4181 | 8352.2142 |  |  |  |  | 4.0758 | 8543.464 |  |  |  |  | 4.1847 | 8459.5711 |  |  |  |  | 4.4181 | 8352.2142 |  |  |  |  | 4.0758 | 8543.464 |  |  |  |  | 4.1847 | 8459.5711 | [6 empty] | 3.4541 | 13858.0344 |  |  |  |  | 3.4541 | 13858.0344 |  |  |  |  | 3.0833 | 370.3569 |  |  | 3.2296 | 14284.1973 |  |  | 3.0833 | 370.3569 |  |  | 3.2296 | 14284.1973
4.3913 | 8400.2154 |  |  |  |  | 4.0758 | 8592.5644 |  |  |  |  | 4.114 | 8508.1893 |  |  |  |  | 4.3913 | 8400.2154 |  |  |  |  | 4.0758 | 8592.5644 |  |  |  |  | 4.114 | 8508.1893 | [6 empty] | 3.4541 | 13937.6783 |  |  |  |  | 3.4541 | 13937.6783 | [8 empty] | 3.0601 | 14050.4982 | [6 empty] | 3.0601 | 14050.4982
4.3913 | 8400.2154 |  |  |  |  | 4.0758 | 8592.5644 |  |  |  |  | 4.114 | 8508.1893 |  |  |  |  | 4.3913 | 8400.2154 |  |  |  |  | 4.0758 | 8592.5644 |  |  |  |  | 4.114 | 8508.1893 | [6 empty] | 3.4541 | 13937.6783 |  |  |  |  | 3.4541 | 13937.6783 | [8 empty] | 3.0601 | 14050.4982 | [6 empty] | 3.0601 | 14050.4982
4.3913 | 8448.2167 |  |  |  |  | 4.0709 | 8641.6647 |  |  |  |  | 4.1096 | 8556.8075 |  |  |  |  | 4.3913 | 8448.2167 |  |  |  |  | 4.0709 | 8641.6647 |  |  |  |  | 4.1096 | 8556.8075 | [6 empty] | 3.4541 | 14017.3222 |  |  |  |  | 3.4541 | 14017.3222 | [8 empty] | 3.0601 | 14130.7868 | [6 empty] | 3.0601 | 14130.7868
4.3913 | 8448.2167 |  |  |  |  | 4.0709 | 8641.6647 |  |  |  |  | 4.1096 | 8556.8075 |  |  |  |  | 4.3913 | 8448.2167 |  |  |  |  | 4.0709 | 8641.6647 |  |  |  |  | 4.1096 | 8556.8075 | [6 empty] | 3.4541 | 14017.3222 |  |  |  |  | 3.4541 | 14017.3222 | [8 empty] | 3.0601 | 14130.7868 | [6 empty] | 3.0601 | 14130.7868
4.3913 | 8496.2179 |  |  |  |  | 4.0659 | 8690.7651 |  |  |  |  | 4.0953 | 8605.4258 |  |  |  |  | 4.3913 | 8496.2179 |  |  |  |  | 4.0659 | 8690.7651 |  |  |  |  | 4.0953 | 8605.4258 | [6 empty] | 3.4541 | 14096.966 |  |  |  |  | 3.4541 | 14096.966 | [8 empty] | 3.0601 | 14211.0754 | [6 empty] | 3.0601 | 14211.0754
4.3913 | 8496.2179 |  |  |  |  | 4.0659 | 8690.7651 |  |  |  |  | 4.0953 | 8605.4258 |  |  |  |  | 4.3913 | 8496.2179 |  |  |  |  | 4.0659 | 8690.7651 |  |  |  |  | 4.0953 | 8605.4258 | [6 empty] | 3.4541 | 14096.966 |  |  |  |  | 3.4541 | 14096.966 | [8 empty] | 3.0601 | 14211.0754 | [6 empty] | 3.0601 | 14211.0754
4.3784 | 8544.2191 |  |  |  |  | 4.3645 | 8591.395 |  |  |  |  | 4.0859 | 8654.044 |  |  |  |  | 4.3784 | 8544.2191 |  |  |  |  | 4.3645 | 8591.395 |  |  |  |  | 4.0859 | 8654.044 | [6 empty] | 3.4541 | 14176.6099 |  |  |  |  | 3.4541 | 14176.6099 | [8 empty] | 3.0601 | 14291.3639 | [6 empty] | 3.0601 | 14291.3639
4.3784 | 8544.2191 |  |  |  |  | 4.3645 | 8591.395 |  |  |  |  | 4.0859 | 8654.044 |  |  |  |  | 4.3784 | 8544.2191 |  |  |  |  | 4.3645 | 8591.395 |  |  |  |  | 4.0859 | 8654.044 | [6 empty] | 3.4541 | 14176.6099 |  |  |  |  | 3.4541 | 14176.6099 | [8 empty] | 3.0601 | 14291.3639 | [6 empty] | 3.0601 | 14291.3639
4.3708 | 8592.2204 |  |  |  |  | 4.0673 | 8639.6613 |  |  |  |  | 4.0846 | 8702.6622 |  |  |  |  | 4.3708 | 8592.2204 |  |  |  |  | 4.0673 | 8639.6613 |  |  |  |  | 4.0846 | 8702.6622 | [6 empty] | 3.3611 | 13705.0313 |  |  |  |  | 3.3611 | 13705.0313 | [8 empty] | 3.0601 | 14371.6525 | [6 empty] | 3.0601 | 14371.6525
4.3708 | 8592.2204 |  |  |  |  | 4.0673 | 8639.6613 |  |  |  |  | 4.0846 | 8702.6622 |  |  |  |  | 4.3708 | 8592.2204 |  |  |  |  | 4.0673 | 8639.6613 |  |  |  |  | 4.0846 | 8702.6622 | [6 empty] | 3.3611 | 13705.0313 |  |  |  |  | 3.3611 | 13705.0313 | [8 empty] | 3.0601 | 14371.6525 | [6 empty] | 3.0601 | 14371.6525
4.3684 | 8640.2216 |  |  |  |  | 4.0595 | 8687.9276 |  |  |  |  | 4.1009 | 8648.4103 |  |  |  |  | 4.3684 | 8640.2216 |  |  |  |  | 4.0595 | 8687.9276 |  |  |  |  | 4.1009 | 8648.4103 | [6 empty] | 3.0601 | 13781.5958 |  |  |  |  | 3.0601 | 13781.5958 | [8 empty] | 3.0601 | 14451.9411 | [6 empty] | 3.0601 | 14451.9411
4.3684 | 8640.2216 |  |  |  |  | 4.0595 | 8687.9276 |  |  |  |  | 4.1009 | 8648.4103 |  |  |  |  | 4.3684 | 8640.2216 |  |  |  |  | 4.0595 | 8687.9276 |  |  |  |  | 4.1009 | 8648.4103 | [6 empty] | 3.0601 | 13781.5958 |  |  |  |  | 3.0601 | 13781.5958 | [8 empty] | 3.0601 | 14451.9411 | [6 empty] | 3.0601 | 14451.9411
4.0737 | 8688.2228 | [10 empty] | 3.0601 | 8696.457 |  |  |  |  | 4.0737 | 8688.2228 | [10 empty] | 3.0601 | 8696.457 | [6 empty] | 3.0601 | 13858.1602 |  |  |  |  | 3.0601 | 13858.1602 | [8 empty] | 3.0601 | 14532.2296 | [6 empty] | 3.0601 | 14532.2296
4.0737 | 8688.2228 | [10 empty] | 3.0601 | 8696.457 |  |  |  |  | 4.0737 | 8688.2228 | [10 empty] | 3.0601 | 8696.457 | [6 empty] | 3.0601 | 13858.1602 |  |  |  |  | 3.0601 | 13858.1602 | [8 empty] | 3.0601 | 14532.2296 | [6 empty] | 3.0601 | 14532.2296
[12 empty] | 3.0601 | 8744.5038 | [16 empty] | 3.0601 | 8744.5038 | [6 empty] | 3.0601 | 13934.7246 |  |  |  |  | 3.0601 | 13934.7246
[12 empty] | 3.0601 | 8744.5038 | [16 empty] | 3.0601 | 8744.5038 | [6 empty] | 3.0601 | 13934.7246 |  |  |  |  | 3.0601 | 13934.7246
[12 empty] | 3.0601 | 8792.5505 | [16 empty] | 3.0601 | 8792.5505 | [6 empty] | 3.0601 | 14011.289 |  |  |  |  | 3.0601 | 14011.289
[12 empty] | 3.0601 | 8792.5505 | [16 empty] | 3.0601 | 8792.5505 | [6 empty] | 3.0601 | 14011.289 |  |  |  |  | 3.0601 | 14011.289
[38 empty] | 3.0601 | 14087.8534 |  |  |  |  | 3.0601 | 14087.8534
[38 empty] | 3.0601 | 14087.8534 |  |  |  |  | 3.0601 | 14087.8534
[38 empty] | 3.0601 | 14164.4179 |  |  |  |  | 3.0601 | 14164.4179
[38 empty] | 3.0601 | 14164.4179 |  |  |  |  | 3.0601 | 14164.4179
[38 empty] | 3.0601 | 14240.9823 |  |  |  |  | 3.0601 | 14240.9823
[38 empty] | 3.0601 | 14240.9823 |  |  |  |  | 3.0601 | 14240.9823
[38 empty] | 3.0601 | 14317.5467 |  |  |  |  | 3.0601 | 14317.5467
[38 empty] | 3.0601 | 14317.5467 |  |  |  |  | 3.0601 | 14317.5467

## Frequencies
Campbell Diagram
Rotor speed [rpm] | Eigen Value 1 [Hz] | Eigen Value 2 [Hz] | Eigen Value 3 [Hz] | Eigen Value 4 [Hz] | Eigen Value 5 [Hz] | Eigen Value 6 [Hz] | Eigen Value 7 [Hz] | Eigen Value 8 [Hz] | Eigen Value 9 [Hz] | Eigen Value 10 [Hz] | Eigen Value 11 [Hz] | Eigen Value 12 [Hz] | Eigen Value 13 [Hz] | Eigen Value 14 [Hz]
0 | 0.33049 | 0.33686 | 0.60332 | 0.62537 | 0.66361 | 0.80815 | 0.81434 | 1.5569 | 1.632 | 1.6747 | 1.7888 | 2.1639 | 2.1987 | 2.365
7.5 | 0.33088 | 0.33675 | 0.61985 | 0.64329 | 0.68304 | 0.81404 | 0.82075 | 1.575 | 1.6545 | 1.696 | 1.813 | 2.1658 | 2.2049 | 2.3788
15 | 0.33177 | 0.33642 | 0.66583 | 0.69341 | 0.73782 | 0.83101 | 0.83927 | 1.6272 | 1.7203 | 1.7571 | 1.8839 | 2.1706 | 2.2236 | 2.4195
Single Blade Frequencies
Rotor speed [rpm] | Eigen Value 1 [Hz] | Eigen Value 2 [Hz] | Eigen Value 3 [Hz] | Eigen Value 4 [Hz] | Eigen Value 5 [Hz] | Eigen Value 6 [Hz] | Eigen Value 7 [Hz] | Eigen Value 8 [Hz] | Eigen Value 9 [Hz] | Eigen Value 10 [Hz] | Eigen Value 11 [Hz] | Eigen Value 12 [Hz] | Eigen Value 13 [Hz] | Eigen Value 14 [Hz]
0 | 0.634 | 0.80152 | 1.7574 | 2.3414 | 3.3567 | 5.1985 | 5.238 | 7.8474 | 8.4433 | 10.5977 | 11.423 | 12.8559 | 13.9453 | 17.6196
7.5 | 0.6534 | 0.80749 | 1.7822 | 2.356 | 3.3864 | 5.2154 | 5.2694 | 7.8807 | 8.4616 | 10.629 | 11.4236 | 12.874 | 13.9764 | 17.6444
15 | 0.70744 | 0.82486 | 1.8544 | 2.3992 | 3.4733 | 5.263 | 5.3649 | 7.9796 | 8.5155 | 10.7203 | 11.4268 | 12.9276 | 14.0693 | 17.7151

## DLC-MaxTip
MAXIMUM TIP DISPLACEMENT | blade Number | 1 | DLC Number | 46 | DLC Name | DLC13_Seed1_9ms
Displacements at the tip | FlapWise [m] | 9.9993 | EdgeWise [m] | -1.4611 | @ time [sec] | 608.12 | Safety Factor not included!
[5 empty] | Blade station: |  |  | 0 |  |  | Blade station: |  |  | 0.5 |  |  | Blade station: |  |  | 0.8
Time [sec] | RotorSpeed [rpm] | Collective Pitch [deg] |  | Fx [N] | Fy [N] | Fz [N] | Mx [Nm] | My [Nm] | Mz [Nm] | Fx [N] | Fy [N] | Fz [N] | Mx [Nm] | My [Nm] | Mz [Nm] | Fx [N] | Fy [N] | Fz [N] | Mx [Nm] | My [Nm] | Mz [Nm]
0 | 11.3032 | 1.1728 |  | 94429.6292 | -185526.318 | 329247.034 | 7039674.35 | 3450643.37 | -34483.5023 | 134848.279 | -16601.4903 | 203851.316 | 300790.708 | 2136431.62 | -26468.0338 | 56026.2942 | -4974.1814 | 50727.647 | 39937.498 | 320645.602 | -7660.3289
0.2 | 11.3424 | 3.6135 |  | 97563.8931 | -232667.214 | 341694.272 | 7873324.59 | 3861302.38 | -32363.8049 | 143476.381 | -14301.3241 | 209934.038 | 177841.007 | 2122516.71 | -17849.4573 | 52542.716 | -117.5578 | 52157.9565 | 10808.3239 | 304985.38 | -2403.8037
0.4 | 11.3992 | 5.7966 |  | 75477.6922 | -236647.746 | 366060.014 | 7879501.91 | 3584239.34 | -41917.6922 | 144470.814 | -14943.9238 | 221921.222 | 207379.602 | 2196015.74 | -26781.9799 | 55014.9626 | -1154.877 | 55590.755 | 17186.3213 | 309759.328 | -6298.3747
0.6 | 11.5171 | 7.267 |  | 26176.332 | -222889.213 | 398646.911 | 7396325.3 | 2338431.09 | -39647.5616 | 133639.027 | -26369.6218 | 232039.415 | 387424.305 | 2150929.79 | -28263.1555 | 55682.6393 | -5330.9444 | 57611.6981 | 39505.873 | 316957.065 | -9196.5106
0.8 | 11.634 | 8.6451 |  | 840.7104 | -245993.386 | 441366.325 | 7587935.06 | 1437153.86 | -40025.7869 | 122096.525 | -39270.7959 | 244697.866 | 545816.286 | 1916493.53 | -20567.5474 | 50190.4883 | -8609.5033 | 59840.8299 | 54300.8373 | 293716.251 | -4710.8852
1 | 11.7485 | 10.0391 |  | -12611.0393 | -257196.308 | 475384.142 | 7789178.94 | 1160295.57 | -38322.2369 | 121767.152 | -42900.3042 | 252689.777 | 577403.532 | 1907171.03 | -18742.3547 | 50633.4292 | -9041.7236 | 61132.6078 | 54827.4431 | 289231.491 | -3043.5321
1.2 | 11.8274 | 11.4391 |  | 1047.1189 | -279777.45 | 519108.195 | 8111760.21 | 1587349.51 | -67017.719 | 127765.359 | -36995.4578 | 261481.342 | 471354.035 | 1899305.89 | -40322.4486 | 46469.5984 | -5197.3068 | 61556.3197 | 36722.6157 | 251756.551 | -13779.5002
1.4 | 11.8975 | 12.8393 |  | 22500.6768 | -301029.28 | 567880.951 | 8006233.74 | 1947837.09 | -78790.1061 | 119589.159 | -28187.8036 | 276339.534 | 336043.933 | 1467670.28 | -41082.0905 | 29389.1125 | -2554.6964 | 64267.5094 | 24864.4053 | 155202.753 | -11923.6525
1.6 | 11.9428 | 14.2183 |  | -16426.0882 | -242267.778 | 613153.256 | 6133937.24 | 671406.922 | -58289.825 | 81434.3939 | -28112.5423 | 291055.317 | 325847.628 | 1143926.3 | -30106.4627 | 28148.4419 | -2203.6612 | 68431.5451 | 21262.4859 | 158231.146 | -10161.1567
1.8 | 11.9153 | 14.8101 |  | -50955.8647 | -177055.556 | 649319.952 | 4339125.88 | -762288.766 | -40073.3208 | 44922.6513 | -35522.3294 | 300015.772 | 474741.991 | 763206.907 | -23741.3064 | 22317.8638 | -6376.1417 | 69919.4266 | 42284.0725 | 124281.981 | -8579.9026
2 | 11.8685 | 14.6752 |  | -49528.5548 | -149301.889 | 672247.743 | 3497500.27 | -1162534.42 | -32501.077 | 28626.7905 | -36293.5604 | 299776.547 | 517171.001 | 414493.825 | -21079.1892 | 10453.4311 | -8246.8496 | 67961.4979 | 53409.8768 | 59635.7907 | -6785.0174
2.2 | 11.7702 | 14.3621 |  | -31692.2423 | -123745.983 | 680869.557 | 2827975.69 | -789430.927 | -44034.8258 | 20871.2627 | -25972.7109 | 297020.343 | 357001.476 | 261198.257 | -28243.3952 | 7083.9373 | -4472.754 | 67227.3777 | 33960.104 | 46981.7993 | -9780.476
2.4 | 11.6607 | 13.7367 |  | 10622.9983 | -96851.7441 | 684187.321 | 2282333.9 | 270720.484 | -53581.0088 | 24601.6392 | -8903.5407 | 294783.09 | 157293.245 | 160226.709 | -31501.8223 | 1144.3387 | -1434.6191 | 66003.8857 | 22651.2243 | 8134.9696 | -10448.8154
2.6 | 11.5761 | 13.0208 |  | 47156.1195 | -68937.4157 | 688470.07 | 1799262.84 | 1174838.27 | -59545.1868 | 27006.1547 | 4785.1198 | 297476.394 | -7295.7849 | 228311.535 | -31959.7631 | 2526.5442 | 1806.3427 | 67919.0935 | 6854.2446 | 6641.3612 | -9004.3397
2.8 | 11.5083 | 12.4204 |  | 69391.5344 | -38962.8194 | 680932.324 | 1467473.14 | 1794612.75 | -57461.679 | 32050.1496 | 13716.7135 | 296986.359 | -103726.961 | 453345.556 | -33300.1856 | 10802.877 | 3711.7104 | 67641.5297 | -1194.6349 | 56736.2424 | -12670.4952
3 | 11.4753 | 11.9072 |  | 119241.381 | -44725.3591 | 664786.205 | 2033632.01 | 2900822.52 | -59785.5639 | 49663.1795 | 18921.2346 | 293951.038 | -143583.451 | 569835.653 | -32440.1233 | 10740.2407 | 3808.9297 | 67783.8872 | -1266.3365 | 59084.2394 | -8634.3458
3.2 | 11.4546 | 11.5839 |  | 142516.232 | -27734.294 | 635498.404 | 2092956.12 | 3571811.45 | -56790.0213 | 63790.994 | 24524.0041 | 284625.829 | -207779.802 | 860605.364 | -36626.6671 | 18169.4873 | 5318.9953 | 65457.65 | -8297.4562 | 84692.4526 | -12717.7089
3.4 | 11.4141 | 11.2988 |  | 168767.55 | -32325.3358 | 604141.061 | 2189736.32 | 4146292.83 | -59847.3548 | 65727.5644 | 30243.3745 | 277033.123 | -279063.029 | 935685.445 | -32969.3134 | 22217.5014 | 6659.7334 | 64561.0591 | -15163.1073 | 119113.6 | -10631.3997
3.6 | 11.3956 | 10.9042 |  | 185694.528 | -19403.941 | 562204.478 | 2028427.86 | 4511201.7 | -57078.6108 | 69538.2158 | 34108.3995 | 265546.307 | -304092.674 | 999786.511 | -33146.0326 | 23325.5197 | 6558.5734 | 61790.2332 | -13547.9858 | 126573.227 | -11655.4953
3.8 | 11.3568 | 10.5914 |  | 193381.869 | -27454.6812 | 525867.281 | 2082055.85 | 4610979.09 | -55282.5937 | 68182.8734 | 34757.3728 | 258035.864 | -335427.726 | 982849.161 | -26355.3725 | 23861.666 | 7515.6462 | 60966.9285 | -20206.3537 | 125998.745 | -7755.2117
4 | 11.2915 | 10.1287 |  | 194038.602 | -36873.9661 | 484733.247 | 2288555.06 | 4588545.44 | -65824.3808 | 68139.9195 | 32819.7295 | 247523.598 | -297247.269 | 997022.37 | -34540.824 | 25356.3716 | 6397.5778 | 58985.7478 | -14504.4116 | 138083.226 | -11649.3517
4.38 | 11.0161 | 9.1094 |  | 195536.053 | -66765.6459 | 416241.672 | 3278031.58 | 4688661.74 | -54837.3501 | 87087.8476 | 18451.1526 | 230148.954 | -233778.909 | 1089702.76 | -30259.4602 | 22046.8804 | 8609.1403 | 54349.1956 | -26587.1165 | 121840.455 | -8939.8208
4.78 | 11.0707 | 8.3722 |  | 153868.19 | -114718.802 | 367254.239 | 4387022.51 | 4789155.72 | -63052.8903 | 106423.602 | 24742.2414 | 217479.886 | -220241.429 | 1418767.74 | -41520.0124 | 30569.9598 | 5865.8232 | 53182.7182 | -12238.596 | 167061.209 | -15702.809
5.18 | 11.469 | 8.1734 |  | 98172.4523 | -188316.426 | 371079.226 | 5899277.67 | 3801182.34 | -69340.3572 | 114355.596 | 3083.5757 | 227462.709 | 46228.4809 | 1449364.15 | -41137.8743 | 29348.2035 | 1775.385 | 56105.901 | 605.6324 | 152910.165 | -12007.8014
5.58 | 11.2662 | 9.8254 |  | -909.6088 | -174037.63 | 399974.833 | 5094881.71 | 1398282.17 | -31070.8738 | 82547.4183 | -16773.9392 | 236156.276 | 247351.481 | 1343314.03 | -16371.2746 | 36206.8834 | -1413.4307 | 57721.4213 | 13813.83 | 211948.478 | -7120.3513
5.98 | 11.5767 | 10.6115 |  | -46989.6924 | -208846.026 | 460432.113 | 5449793.59 | 462324.057 | -37837.8951 | 81587.3914 | -22884.0632 | 250148.182 | 341934.734 | 1194999.47 | -15142.4154 | 28964.5669 | -5359.9425 | 60262.7601 | 42714.8924 | 168112.622 | -2518.2096
6.38 | 11.557 | 10.7596 |  | -21213.0795 | -247249.84 | 527560.717 | 7139695.91 | 680224.297 | -65410.7068 | 105236.021 | -46751.6961 | 267751.314 | 553832.957 | 1512663.63 | -40313.9098 | 35692.8009 | -5207.2316 | 61761.2947 | 36704.4797 | 189923.303 | -16611.6512
6.78 | 11.519 | 10.5847 |  | -40220.5535 | -278083.651 | 605322.568 | 7011672.23 | 395420.54 | -68888.0377 | 91526.9613 | -36464.3087 | 286845.907 | 473972.545 | 1174210.27 | -35567.5303 | 26114.2302 | -5759.4986 | 68346.6854 | 37820.8912 | 138282.859 | -11647.3053
7.18 | 11.5116 | 10.6927 |  | 10138.2843 | -197792.85 | 652332.333 | 5516766.42 | 754743.19 | -48888.7236 | 76493.8387 | -35947.1922 | 288767.943 | 450742.144 | 1081542.16 | -24929.2711 | 25799.7894 | -3929.7206 | 63467.44 | 34148.0964 | 141046.067 | -7480.2451
7.58 | 11.3814 | 10.4966 |  | 49057.1639 | -180310.356 | 691330.73 | 4886079.58 | 2263912.99 | -69676.3702 | 82222.2576 | -840.7687 | 300712.172 | 95831.1607 | 1079082.4 | -36731.533 | 25423.6224 | 161.3297 | 68820.7625 | 15949.497 | 143435.511 | -13253.0315
7.98 | 11.4463 | 10.0794 |  | 102889.694 | -96531.813 | 684799.446 | 3681162.62 | 2705837.27 | -37319.9565 | 72736.1291 | -2032.0471 | 298628.843 | 42813.9795 | 1135618.07 | -20649.7109 | 30102.2131 | 3661.3117 | 67115.3431 | -2089.1238 | 170141.275 | -10104.9826
8.38 | 11.426 | 9.6194 |  | 179172.587 | -79766.6293 | 651117.527 | 3651225.95 | 5141559.48 | -55775.1162 | 101267.773 | 33634.7477 | 287494.565 | -244947.444 | 1420361.81 | -34326.3437 | 32053.7419 | 5148.8531 | 66050.9784 | -4644.3067 | 163767.314 | -9759.4588
8.78 | 11.5249 | 10.8955 |  | 216562.167 | -48903.5379 | 604460.79 | 3001696.06 | 5774057.23 | -57486.2227 | 95967.4647 | 41854.1165 | 292295.322 | -367667.449 | 1408384.49 | -35035.156 | 33794.2352 | 8150.5114 | 71264.784 | -24724.6961 | 185497.636 | -12503.24
9.18 | 11.5915 | 10.1899 |  | 187830.368 | -35271.8006 | 517665.31 | 2626915.77 | 4355649.47 | -49598.3975 | 72525.5293 | 20631.7753 | 262988.48 | -189265.658 | 1126008.37 | -28313.9645 | 30642.4236 | 6462.6104 | 60399.846 | -12721.661 | 175355.702 | -10089.1841
9.58 | 11.5057 | 10.1883 |  | 177992.692 | -67598.2522 | 444040.895 | 3061615.03 | 4757240.54 | -58764.9359 | 85324.3629 | 31270.6681 | 243386.089 | -256859.961 | 1104748.22 | -30013.087 | 23577.7796 | 5151.5006 | 58939.1435 | -7091.4212 | 137327.642 | -6146.9277
9.98 | 11.5142 | 10.7615 |  | 144181.314 | -80543.2327 | 409705.784 | 3366876.29 | 4159094.39 | -49141.1073 | 86160.2728 | 18939.8136 | 247377.593 | -309776.678 | 1140950.51 | -29785.7405 | 23817.0417 | 11978.3512 | 60689.7799 | -46828.5403 | 128093.427 | -10127.7246
10.38 | 11.4585 | 10.086 |  | 52191.6982 | -158675.559 | 409941.924 | 4442077.5 | 2085751.24 | -78367.4715 | 70490.4678 | -3962.4722 | 242550.525 | 184523.289 | 915811.231 | -42398.4256 | 20407.585 | -3125.2207 | 59975.8836 | 27837.1 | 117711.169 | -11712.9072
10.78 | 11.5867 | 10.3122 |  | -8679.4101 | -162403.514 | 419297.245 | 4568529.54 | 678834.771 | -28169.0371 | 67088.4218 | -24531.5023 | 243149.107 | 343039.926 | 976409.535 | -15065.0279 | 22794.0032 | -3625.48 | 60181.4876 | 23501.5344 | 133297.367 | -6911.2067
11.18 | 11.3322 | 10.0925 |  | -45435.903 | -228884.631 | 485404.266 | 5874128.65 | 594625.105 | -62698.4348 | 86269.3167 | -25902.6061 | 260261.645 | 388334.698 | 1125815.67 | -34817.5992 | 23251.5669 | -5116.2101 | 63337.6591 | 34491.3234 | 119630.107 | -9623.1912
11.58 | 11.5531 | 9.9549 |  | -26882.2852 | -284676.614 | 548733.983 | 7521248.63 | 510598.89 | -84212.4063 | 101888.495 | -46352.7432 | 272028.562 | 586197.133 | 1174914.47 | -50566.8043 | 20306.5086 | -6832.8658 | 64335.2605 | 41207.5102 | 100320.478 | -19216.2775
11.98 | 11.3411 | 9.8821 |  | -66006.2582 | -217154.725 | 617123.503 | 5567561.14 | -142268.957 | -24101.5058 | 75958.1222 | -34614.7656 | 283597.04 | 485046.785 | 1153389.31 | -10838.4931 | 29898.0284 | -6099.9236 | 65925.1088 | 38194.9042 | 168404.196 | -9432.2107
12.38 | 11.527 | 9.8735 |  | 27055.9602 | -210846.558 | 675583.531 | 5677331.42 | 1677874.46 | -67278.4853 | 84350.8664 | -17524.9132 | 299018.41 | 254683.026 | 1180424.63 | -35351.426 | 26399.0817 | -481.6581 | 69761.1233 | 10096.0151 | 135336.403 | -9727.0289
12.78 | 11.7474 | 9.7405 |  | 61966.972 | -187005.869 | 704093.073 | 5094981.37 | 2430301.96 | -77931.3739 | 86714.0393 | -4863.3346 | 305812.809 | 179769.985 | 1050650.04 | -42008.1798 | 20944.523 | -1071.9255 | 69283.6941 | 19030.0028 | 113674.011 | -11670.3516
13.18 | 11.3627 | 10.3326 |  | 114499.869 | -103660.596 | 687738.938 | 3679619.53 | 3452044.58 | -55697.1992 | 81724.0906 | 14223.9995 | 297207.821 | 21838.4277 | 1218551.4 | -26713.2412 | 29847.0426 | -426.2951 | 67652.0343 | 20925.7376 | 163264.973 | -12078.5395
13.58 | 11.5868 | 9.6202 |  | 186559.535 | -57518.0975 | 646228.186 | 2793596.45 | 5021424.48 | -56691.5353 | 83953.441 | 37090.8479 | 293835.09 | -381104.005 | 1237676.91 | -28746.3559 | 30025.3635 | 10488.699 | 69768.302 | -38101.2965 | 161913.318 | -10091.649
13.98 | 11.8352 | 9.9247 |  | 197634.661 | -62246.7258 | 591757.688 | 2804917.23 | 5239062.83 | -66877.2797 | 84189.9457 | 39221.5765 | 285405.021 | -308218.87 | 1109273.46 | -32750.5176 | 23969.75 | 6599.8089 | 66739.3252 | -15295.957 | 129331.223 | -5809.1626
14.38 | 11.4297 | 10.6955 |  | 175529.363 | -44947.5033 | 506618.729 | 2453380.54 | 4534928.38 | -71314.0906 | 73065.857 | 32868.8159 | 260891.65 | -209136.631 | 974079.345 | -40147.3996 | 22566.8421 | 3093.7469 | 61788.2388 | 5173.2073 | 128764.01 | -15788.3567
14.78 | 11.6144 | 9.8709 |  | 155902.363 | -57752.2225 | 438708.01 | 2744727.69 | 4261475.59 | -44282.9758 | 69398.9764 | 29584.6427 | 248595.513 | -317160.377 | 1058420.06 | -20419.5835 | 28874.08 | 8794.5595 | 62092.6897 | -32864.2307 | 173230.682 | -7112.2932
15.18 | 11.3535 | 9.9135 |  | 93048.1893 | -100406.95 | 409001.492 | 2988329.85 | 2902119.33 | -91325.774 | 62826.6003 | 15173.6968 | 241793.754 | -41083.9105 | 717222.701 | -56035.2103 | 12474.3492 | 714.8464 | 59835.1062 | 11483.3199 | 66250.4615 | -17123.7622
15.58 | 11.5532 | 9.6551 |  | 10538.1283 | -96400.4512 | 397103.589 | 2523418.59 | 651963.938 | -15133.4204 | 30297.5927 | -9364.6634 | 237436.571 | 170509.911 | 515109.411 | 1325.038 | 16292.746 | -1023.2687 | 58862.3432 | 11286.4206 | 105319.808 | -234.3579
15.98 | 11.3459 | 9.5441 |  | 12155.0949 | -246473.231 | 439640.122 | 6170451.42 | 1720898.05 | -98032.3039 | 86958.6167 | -14157.1143 | 249344.34 | 208413.291 | 1018647.43 | -58810.3079 | 19124.6313 | -692.7146 | 60236.3491 | 12666.862 | 91833.4259 | -18926.5641
16.38 | 11.5075 | 9.1457 |  | -73838.065 | -207973.066 | 489179.463 | 5480411.48 | -841397.585 | -28493.5427 | 66419.4259 | -48423.541 | 262978.422 | 609023.808 | 945766.452 | -21194.9364 | 22386.9981 | -7637.5849 | 64884.3792 | 40377.4702 | 125091.494 | -12599.3314
16.78 | 11.4904 | 10.0197 |  | -30968.502 | -269176.869 | 556937.278 | 7100114.54 | 328115.098 | -48099.8988 | 92852.6802 | -46542.5332 | 273932.681 | 464733.067 | 1181362.45 | -20679.1931 | 24323.8089 | -2074.4029 | 64112.2466 | 17242.322 | 115163.543 | -4810.1565
17.18 | 11.4304 | 8.989 |  | -6417.6776 | -278426.833 | 636665.115 | 6951784.55 | 1199996.75 | -89982.8682 | 94020.3485 | -24733.0055 | 288309.217 | 362917.281 | 1108529.67 | -50599.8531 | 20823.7976 | -4089.7368 | 66331.0672 | 34319.2434 | 103530.58 | -17673.2002
17.58 | 11.4396 | 9.1573 |  | 23650.6747 | -204336.236 | 681632.611 | 5901492.08 | 1063159.57 | -40789.9896 | 82241.0825 | -34975.1014 | 304439.617 | 374685.33 | 1109752.1 | -25769.0989 | 26323.2175 | -945.3887 | 69496.1903 | 15931.8105 | 147750.997 | -11411.1677
17.98 | 11.3996 | 8.7746 |  | 81116.3068 | -162903.795 | 690949.726 | 4775120.42 | 2892543.94 | -58038.8479 | 88562.5331 | 3669.2899 | 292772.109 | 77126.8584 | 1195651.98 | -27992.0699 | 25457.1089 | 480.5927 | 65833.8352 | 15108.0296 | 133790.085 | -9013.6347
18.38 | 11.5292 | 8.9533 |  | 156362.216 | -132452.231 | 681849.824 | 3894408.19 | 4532907.61 | -84848.5549 | 87130.8763 | 33293.1266 | 297833.46 | -345991.747 | 977931.907 | -46016.2983 | 17157.4223 | 8694.8891 | 67095.889 | -18050.4464 | 90077.9469 | -14702.4542
18.78 | 11.4903 | 9.1897 |  | 164445.788 | -23545.8196 | 624611.071 | 2446261.26 | 3633380.92 | -18519.3543 | 69659.3446 | 9860.7779 | 289458.863 | -20637.6443 | 1097775.72 | -5591.7042 | 30000.9951 | 2114.1774 | 66159.7239 | 7625.7223 | 166530.047 | -5552.0228
19.18 | 11.4569 | 8.5227 |  | 220231.525 | -68591.9572 | 551678.875 | 3318662.79 | 6008125.11 | -68966.684 | 105716.972 | 45078.2002 | 265892.492 | -433088.312 | 1386349.49 | -42479.4549 | 27569.4248 | 9874.7166 | 62960.4557 | -29388.4608 | 133669.016 | -10268.3472
19.58 | 11.5064 | 8.5847 |  | 212614.573 | -16985.7475 | 484282.123 | 2335811.24 | 5349128.48 | -56277.6502 | 83203.013 | 34861.7829 | 258490.438 | -372487.952 | 1274202.46 | -35312.2849 | 34304.2239 | 10099.8007 | 60205.9097 | -28553.448 | 202361.616 | -14024.7746
19.98 | 11.4421 | 8.4928 |  | 135006.367 | -91483.0198 | 434800.052 | 3724046.78 | 3882967.46 | -55122.9455 | 82525.4807 | 16523.7824 | 247757.075 | -37417.1679 | 1358866.34 | -29041.9642 | 38914.7343 | 593.1529 | 61000.8597 | 12751.3719 | 231548.468 | -11756.8273
20.38 | 11.4711 | 9.5247 |  | 94940.7096 | -136633.238 | 394653.217 | 4480570.57 | 3202255.01 | -63727.7934 | 89231.0133 | 4459.4478 | 237654.007 | -5737.6471 | 1211874.08 | -40116.8017 | 27478.589 | 3039.7188 | 60312.516 | -6725.4584 | 151330.386 | -11019.7381
20.78 | 11.5524 | 8.1355 |  | 25710.8046 | -138782.942 | 402632.201 | 4281210.7 | 1353010.45 | -25899.5214 | 66851.8711 | -17036.9938 | 239904.222 | 172511.028 | 1012433.04 | -10413.3518 | 27234.0987 | 1051.9128 | 57114.8765 | 6746.1351 | 161503.747 | -1917.3965
21.18 | 11.4565 | 8.368 |  | 1078.3683 | -255185.985 | 445578.499 | 7311321.11 | 1432232.52 | -71761.6118 | 112473.497 | -35488.7887 | 253887.127 | 471520.462 | 1438590.1 | -46367.6825 | 28221.8279 | -5077.9512 | 63798.6528 | 29235.0886 | 141833.045 | -13962.7138
21.58 | 11.5319 | 8.0384 |  | -57656.6941 | -209155.435 | 492067.983 | 5801868.28 | -424810.779 | -42548.2792 | 75055.044 | -48164.2405 | 255175.704 | 550105.072 | 1114880.13 | -30692.9387 | 28107.2448 | -5138.5058 | 59248.2246 | 36325.9231 | 160338.16 | -14820.8189
21.98 | 11.358 | 8.63 |  | -60405.5885 | -251398.503 | 584979.761 | 5991898.6 | 24328.6601 | -32271.9925 | 75369.6869 | -32583.6767 | 278476.689 | 346257.786 | 932304.204 | -7951.5055 | 18899.3416 | -680.9987 | 63730.6663 | 8685.1838 | 103685.75 | -1845.5895
22.38 | 11.5162 | 8.0297 |  | -9341.1664 | -246701.498 | 644395.045 | 6958753.27 | 910196.382 | -71197.2763 | 102501.646 | -39149.662 | 294220.114 | 517471.394 | 1342547.15 | -44285.4995 | 27447.6125 | -5481.9943 | 69250.1927 | 34146.9713 | 137006.03 | -17358.8661
22.78 | 11.5061 | 8.4052 |  | 50468.9989 | -220907.525 | 686620.985 | 6660533.3 | 2140742.76 | -46699.9098 | 106515.554 | -25168.449 | 302514.187 | 228243.813 | 1481673.05 | -30812.1047 | 34508.8894 | 2776.4255 | 68974.2642 | -1434.3059 | 185066.047 | -16639.0899
23.18 | 11.4834 | 7.7506 |  | 96121.2147 | -143203.118 | 699073.734 | 4518796.62 | 3188573.45 | -59026.8694 | 88363.1446 | 7461.4735 | 297721.562 | 56335.3643 | 1261239.92 | -30372.3361 | 30280.2138 | 164.0286 | 67494.8715 | 17570.2633 | 162448.264 | -10058.1372
23.58 | 11.6218 | 8.2093 |  | 169954.253 | -94089.2822 | 676407.546 | 3687568.24 | 4532932.36 | -43263.3456 | 96682.7402 | 21137.9414 | 304400.533 | -195422.295 | 1214386.34 | -22485.6809 | 23559.212 | 6887.29 | 71529.2435 | -20305.399 | 130789.341 | -4017.5717
23.98 | 11.4003 | 8.038 |  | 185895.513 | -79852.0712 | 620202.582 | 3336164.27 | 4927149.31 | -65171.2403 | 87926.8818 | 31862.9263 | 286419.508 | -197236.696 | 1213263.11 | -33120.4082 | 29327.2799 | 3398.7934 | 66855.2676 | 3437.2771 | 161218.428 | -10844.0025
24.38 | 11.6108 | 7.9116 |  | 221028.929 | -55233.7591 | 536740.837 | 3151118.66 | 5698701.85 | -61185.0058 | 95307.681 | 38294.9888 | 265809.663 | -376730.823 | 1291987.95 | -39089.0407 | 28601.9735 | 9690.8204 | 63317.598 | -31883.7695 | 160527.062 | -14032.1249
24.78 | 11.5569 | 8.8185 |  | 180390.832 | -22441.3217 | 478826.7 | 2007004.59 | 4405320.07 | -38901.386 | 65540.6699 | 28074.0763 | 265498.794 | -351814.612 | 1052407.43 | -15121.8815 | 28091.4357 | 11068.1442 | 64828.86 | -41357.4911 | 168398.547 | -6055.3183
25.18 | 11.4818 | 7.8561 |  | 144790.715 | -125361.879 | 430420.318 | 4386604 | 4315325.42 | -71313.4808 | 96694.5059 | 18850.7397 | 243266.676 | -76381.4343 | 1258783.03 | -39762.3488 | 25827.9686 | 1821.3639 | 58120.8545 | 9087.029 | 142751.757 | -10105.3025
25.58 | 11.527 | 8.0296 |  | 63273.5156 | -146951.107 | 401009.477 | 4675932.69 | 2678075.23 | -41082.6885 | 88504.6457 | 1655.7572 | 242636.992 | 57869.7329 | 1308302.99 | -22594.7663 | 32674.2503 | 69.7576 | 60959.4187 | 13858.1576 | 181992.927 | -7905.0584
25.98 | 11.5516 | 7.9654 |  | 38692.3686 | -187808.961 | 414132.228 | 6143697.41 | 1951359.95 | -40610.9147 | 104460.235 | -29424.4224 | 244577.47 | 355306.723 | 1544373.89 | -23777.495 | 35429.0441 | -1906.4931 | 58813.0266 | 18600.1424 | 186430.477 | -2425.514
26.38 | 11.4255 | 7.6413 |  | -34351.4582 | -259544.229 | 468950.325 | 6971213.26 | 922456.762 | -99005.3003 | 101117.241 | -30183.3877 | 255381.983 | 439622.478 | 1407043.89 | -69165.1281 | 31962.8811 | -5178.1032 | 62269.1119 | 38096.6499 | 189496.011 | -25663.9765
26.78 | 11.4575 | 7.5806 |  | -73527.3614 | -203959.067 | 518879.678 | 5870480.05 | -899652.055 | -10805.1617 | 75344.5437 | -59278.9203 | 262288.04 | 674628.993 | 1222512.54 | -2422.2751 | 30773.4135 | -6756.357 | 60333.7845 | 41509.0442 | 181381.421 | -4398.0391
27.18 | 11.3589 | 6.9765 |  | -40264.8983 | -262644.6 | 592591.545 | 6973575.2 | 801299.973 | -63822.722 | 98548.5193 | -30334.0852 | 276607.329 | 458386.925 | 1436249.55 | -32416.0549 | 35809.5668 | -6777.5093 | 65362.8163 | 45411.213 | 193292.815 | -9868.8654
27.58 | 11.4638 | 6.7023 |  | 32541.3085 | -249362.204 | 657146.116 | 7375222.34 | 1931244.65 | -65286.8949 | 115452.56 | -33430.4853 | 297409.144 | 362763.49 | 1576468.51 | -42807.3154 | 36214.9314 | -655.3021 | 67831.2903 | 15947.6075 | 191814.301 | -13190.6994
27.98 | 11.4039 | 6.4945 |  | 35119.8357 | -180466.43 | 689923.873 | 5446621.62 | 1857040.74 | -65895.0936 | 91256.8123 | -15195.728 | 297494.931 | 356556.179 | 1416129.03 | -36787.3074 | 36192.8348 | -5945.1292 | 68469.8247 | 45424.9459 | 202676.526 | -14819.4743
28.38 | 11.4115 | 6.4656 |  | 120457.571 | -115101.707 | 676095.935 | 3854955.74 | 3029681.97 | -46240.2576 | 68119.9761 | 1918.7951 | 292085.519 | -15390.9544 | 1070133.4 | -15877.614 | 29248.7866 | 4925.1944 | 64514.6942 | -6935.4078 | 179972.055 | -6026.2708
28.78 | 11.3629 | 5.634 |  | 162731.773 | -90786.3783 | 647568.67 | 3708333.08 | 4681897 | -55989.3357 | 96086.4734 | 28620.5248 | 289793.2 | -209666.51 | 1370585.94 | -33547.5886 | 31313.1162 | 5075.4497 | 67130.7212 | -6238.9735 | 157896.117 | -11982.7987
29.18 | 11.4035 | 5.0294 |  | 225066.706 | -80584.1838 | 573451.765 | 4144312.88 | 5481478.73 | -53179.9961 | 104047.014 | 21633.8259 | 270520.264 | -203386.076 | 1391453.57 | -33488.9898 | 32113.3358 | 6785.735 | 60931.7515 | -11704.0104 | 186292.152 | -11187.0159
29.58 | 11.2755 | 5.4173 |  | 216742.277 | -106063.494 | 512424.418 | 4686351.05 | 6243539.29 | -37368.9574 | 127218.596 | 35038.1958 | 259242.142 | -355475.878 | 1778354.65 | -25185.7444 | 40112.5576 | 10245.4691 | 61321.8345 | -36375.8963 | 214320.549 | -9367.3529
29.98 | 11.5164 | 5.0126 |  | 180096.345 | -102979.998 | 440528.796 | 4706872.92 | 5160313.23 | -46716.091 | 120521.118 | 22404.1593 | 240742.605 | -147907.362 | 1658734.59 | -34412.6694 | 37432.4758 | 3110.1383 | 57470.4049 | 10595.9116 | 221485.094 | -12884.1723
30.38 | 11.392 | 5.9196 |  | 155761.449 | -148965.653 | 392113.654 | 6132648.98 | 4452237.03 | -35977.4355 | 129421.058 | -6039.6384 | 238203.051 | 82298.0113 | 1901061.21 | -29556.8145 | 46496.8661 | 2566.8288 | 59458.9445 | -1042.0007 | 255583.314 | -9622.775
30.78 | 11.3839 | 5.2387 |  | 75553.4452 | -200252.76 | 375262.258 | 6854176.2 | 3524336.68 | -42421.8234 | 133061.156 | -8416.8027 | 222946.838 | 110592.395 | 1969173.96 | -33339.8449 | 49252.7387 | 2506.3 | 53739.3156 | -2237.0498 | 276075.418 | -14329.5003
31.18 | 11.4097 | 5.9517 |  | 18402.0608 | -210037.549 | 408861.711 | 7005758.23 | 1780819.37 | -54924.7352 | 124327.155 | -36174.6721 | 246127.426 | 549029.581 | 1791439.22 | -37987.5183 | 41659.8632 | -8598.195 | 64105.2269 | 45704.6753 | 216018.222 | -11081.7976
31.58 | 11.4621 | 5.8059 |  | -63225.255 | -192221.634 | 449070.421 | 5965962.09 | -266743.342 | -19670.5817 | 85561.2637 | -48644.5269 | 245450.104 | 538586.276 | 1519604.46 | -14197.478 | 44647.3434 | -4975.7373 | 59170.9175 | 34340.4216 | 267915.943 | -4293.8109
31.98 | 11.3515 | 4.7293 |  | -59605.9222 | -222509.623 | 521734.554 | 6160627.13 | -50625.7893 | -65405.789 | 84614.6123 | -42514.6921 | 257081.511 | 587911.073 | 1256765.17 | -40778.4399 | 30802.4214 | -7890.8957 | 61604.5667 | 47534.266 | 186107.202 | -11654.1844
32.38 | 11.0807 | 4.4683 |  | -87521.9125 | -218780.341 | 597527.254 | 5765374.01 | -339462.187 | -39067.1618 | 73073.2501 | -34957.8441 | 278004.184 | 479450.187 | 1279685.77 | -22782.129 | 37035.7922 | -5495.4937 | 64887.7427 | 35608.7738 | 221653.154 | -11012.3148
32.78 | 11.3009 | 4.1326 |  | -18904.6611 | -198737.273 | 633872.26 | 5936076.25 | 567472.232 | -46595.1227 | 87640.2778 | -36403.9543 | 278554.983 | 503810.738 | 1356582.3 | -31516.3007 | 34470.2459 | -5927.0477 | 64190.894 | 38151.4743 | 193203.739 | -11091.8429
33.18 | 11.1157 | 3.6451 |  | 46793.663 | -169614.445 | 658741.091 | 5283162.42 | 2339291.83 | -59269.0288 | 94480.6241 | -6076.9149 | 282118.223 | 230398.772 | 1521480.24 | -34974.3391 | 39751.2082 | -3807.374 | 64500.432 | 36462.2482 | 218308.191 | -11940.6612
33.58 | 10.8649 | 3.1559 |  | 101977.995 | -134751.904 | 658492.425 | 4633762.78 | 3311979.18 | -47970.9883 | 94345.784 | 3963.254 | 281850.687 | 131695.265 | 1472132.21 | -25186.6612 | 39480.416 | -1989.8248 | 63851.9732 | 27208.4841 | 231256.84 | -9098.2444
33.98 | 10.9624 | 3.0671 |  | 188335.876 | -113214.004 | 600500.368 | 5106227.65 | 4808863.19 | -43619.0853 | 117030.993 | 4594.5921 | 266624.495 | -12611.7107 | 1720927.67 | -31760.0739 | 41876.5482 | 4310.3321 | 60678.0896 | -6183.1218 | 216694.24 | -9578.4113
34.38 | 10.8852 | 3.0122 |  | 206092.007 | -97833.8541 | 541517.88 | 4416037.82 | 5811607.29 | -49766.5908 | 113307.584 | 32792.2411 | 251217.446 | -292387.815 | 1762616.86 | -31452.6921 | 46647.2356 | 7813.1892 | 58089.7632 | -20376.2913 | 273001.82 | -11181.1061
34.78 | 10.7189 | 2.9539 |  | 206018.542 | -101531.035 | 479922.189 | 4569254.62 | 5675022.94 | -44330.6654 | 117936.046 | 25268.8368 | 239633.331 | -155251.859 | 1674471.34 | -27690.6552 | 39295.0563 | 4170.9036 | 56444.2592 | -2217.149 | 235772.881 | -6967.3727
35.18 | 10.9176 | 2.8922 |  | 180062.002 | -99217.7876 | 392738.625 | 4848947.48 | 4848619.01 | -27860.7898 | 115257.233 | 10088.6101 | 219389.528 | -51862.1366 | 1779791.82 | -19390.0833 | 45959.6659 | 3382.6032 | 54722.1641 | -6266.1258 | 262572.841 | -8207.0554
35.58 | 10.8538 | 2.8258 |  | 129597.448 | -149911.373 | 336708.798 | 6079427.51 | 4584868.51 | -22769.9283 | 138719.167 | 7352.106 | 200612.624 | 19204.0731 | 2136226.2 | -19497.9677 | 53538.3165 | -168.0279 | 49421.2512 | 17569.9849 | 276157.605 | -7069.798
35.98 | 10.7068 | 2.7577 |  | 87395.753 | -182101.825 | 313716.42 | 7020065.41 | 3564121.11 | -43498.983 | 139082.868 | -14833.1199 | 196033.473 | 367343.025 | 2226798.87 | -37017.2658 | 60090.1916 | -8107.6083 | 49382.1035 | 56432.5963 | 342035.052 | -13583.7737
36.38 | 10.586 | 2.6937 |  | 10517.0736 | -224779.214 | 334375.853 | 7490626.25 | 2037770.04 | -43442.2656 | 134379.422 | -34041.7905 | 205288.824 | 462707.174 | 1990703.54 | -27857.7044 | 47397.9639 | -5234.3498 | 52348.4164 | 30315.9341 | 256541.07 | -5002.4015
36.78 | 10.5222 | 2.6255 |  | -52553.0096 | -208549.614 | 365367.033 | 6496196.18 | 513771.274 | -39266.1917 | 100208.751 | -40121.2733 | 200920.32 | 609248.518 | 1744936.36 | -25477.2599 | 51179.2987 | -10191.2486 | 48128.4484 | 60234.8364 | 299791.856 | -8738.0851
37.18 | 10.621 | 2.5578 |  | -57281.4245 | -208291.729 | 420755.989 | 6410610.68 | -83056.8803 | -38847.2369 | 91436.0781 | -51146.0148 | 221207.374 | 572595.261 | 1480436.03 | -25885.7884 | 41201.0339 | -5762.8572 | 52415.3836 | 38093.4916 | 242378.178 | -7118.1655
37.58 | 10.5832 | 2.4939 |  | -71520.1741 | -204448.124 | 488064.509 | 6268698.27 | -416442.9 | -27827.7688 | 86604.1175 | -53419.4109 | 234969.304 | 615480.35 | 1502431.94 | -20476.0002 | 42350.7058 | -6588.9052 | 54617.3261 | 40693.0061 | 237870.831 | -7031.1824
37.98 | 10.6094 | 2.4286 |  | -39522.8609 | -208761.187 | 550406.184 | 6044619.48 | 329854.549 | -44210.2274 | 84420.8936 | -37238.6249 | 246027.869 | 531960.997 | 1357576.84 | -27889.152 | 35563.3885 | -7555.3045 | 57771.7963 | 48218.9348 | 223611.056 | -9848.4983
38.38 | 10.5728 | 2.3746 |  | 707.4661 | -178475.8 | 600039.889 | 5434013.29 | 1432660.21 | -39981.69 | 94951.9502 | -19078.1717 | 259048.643 | 237304.341 | 1423928.89 | -25729.4109 | 34778.125 | 71.9089 | 58628.4427 | 7046.0745 | 190679.118 | -8019.2698
38.78 | 10.5542 | 2.3128 |  | 66003.0121 | -137038.627 | 610905.792 | 4639860.54 | 2415860.82 | -45457.8308 | 87757.5745 | -6221.3495 | 259341.111 | 242055.36 | 1392292.45 | -25365.0013 | 36528.6819 | -4447.9888 | 59164.2408 | 38394.5696 | 209407.948 | -9955.7882
39.18 | 10.4066 | 2.2421 |  | 125630.917 | -139975.988 | 605715.817 | 4766465.81 | 3935870.01 | -51815.9154 | 102094.788 | 10564.8468 | 263834.332 | -84304.4679 | 1412150.18 | -27760.6256 | 30116.8469 | 5791.404 | 61652.4599 | -19319.8179 | 158055.798 | -6194.3565
39.58 | 10.4568 | 2.1705 |  | 173381.876 | -80405.1214 | 557054.104 | 3724668.2 | 4808618.15 | -42687.6117 | 100326.275 | 22351.7775 | 242412.332 | -118646.023 | 1526297.5 | -23964.4163 | 38174.5044 | 3690.3073 | 55032.5672 | -2868.4539 | 211886.85 | -8345.9586
39.98 | 10.8027 | 2.1015 |  | 202574.959 | -65817.7771 | 497620.613 | 3552698.4 | 5672729 | -39711.7254 | 106931.277 | 33359.5184 | 237254.054 | -262717.478 | 1585946.21 | -23314.2446 | 38460.9321 | 6573.6379 | 56118.3812 | -16892.1503 | 223657.481 | -7537.2649
40.38 | 10.7322 | 2.0344 |  | 205136.277 | -80350.9996 | 437142.76 | 3773776.77 | 5721291.81 | -52386.4877 | 103204.993 | 40459.4832 | 224533.421 | -350883.884 | 1526199.9 | -29329.4525 | 39654.9428 | 5501.5296 | 53412.9418 | -307.194 | 233632.685 | -7589.7157
40.78 | 10.6655 | 1.9698 |  | 176684.175 | -81344.4554 | 381894.903 | 3976290.12 | 5017385.51 | -37975.8404 | 107411.159 | 21608.5606 | 213391.127 | -146392.748 | 1664228.53 | -20372.8713 | 42121.3189 | 4497.4114 | 50977.0752 | -8317.1025 | 244068.689 | -6664.4699
41.18 | 10.578 | 1.9005 |  | 127641.214 | -126325.052 | 336981.204 | 5303866.07 | 4281725.06 | -32999.8192 | 123170.282 | 3877.0768 | 202717.28 | 107026.774 | 1918255.15 | -23581.1019 | 47691.2429 | -1002.9822 | 50200.1397 | 14038.8185 | 256496.12 | -8415.7397
41.58 | 10.7475 | 1.8317 |  | 93620.705 | -183129.032 | 313980.906 | 6788491.4 | 3320729.46 | -42428.527 | 126150.383 | -20638.8441 | 200295.92 | 238970.421 | 1896833.39 | -29284.9896 | 50230.5486 | -1039.7817 | 49581.3513 | 19042.744 | 288976.819 | -7742.4239
41.98 | 10.8924 | 1.7627 |  | 8184.1143 | -234437.478 | 340289.525 | 7514800.46 | 2085923.13 | -57967.2341 | 128616.071 | -25221.5037 | 202498.506 | 401552.205 | 1955558.52 | -38143.1172 | 49180.1609 | -6891.0315 | 49762.7918 | 54352.7935 | 286302.432 | -11605.6945
42.38 | 10.7942 | 1.6889 |  | -47100.8632 | -201683.086 | 389623.19 | 6650845.18 | 516882.065 | -8977.0119 | 108753.464 | -44928.1472 | 216448.234 | 684678.011 | 1772255.69 | -4505.3615 | 49936.2797 | -13735.2384 | 52958.5495 | 76101.2832 | 282466.208 | -5653.1475
42.78 | 10.7103 | 1.6152 |  | -61582.172 | -276877.726 | 474606.293 | 7961183.52 | 655049.839 | -55210.4445 | 118595.48 | -44711.2073 | 241599.977 | 529681.356 | 1766745.26 | -28893.1815 | 45388.3427 | -4978.5333 | 58738.2878 | 26727.5969 | 250865.418 | -7453.6908
43.18 | 11.2824 | 1.5505 |  | -57591.9634 | -263753.173 | 532557.775 | 8037210.85 | 749547.072 | -42415.5011 | 126241.647 | -48433.8483 | 247482.981 | 701866.968 | 1949824.71 | -26421.6622 | 49038.7363 | -10198.0908 | 57338.7851 | 57594.6826 | 274191.99 | -8550.6635
43.58 | 10.9677 | 1.4987 |  | -6927.9743 | -233679.071 | 604098.73 | 7620940.07 | 1405319.4 | -48655.7707 | 127841.671 | -41647.7077 | 274842.274 | 624354.985 | 1955055.25 | -34009.7884 | 49147.3469 | -9977.2648 | 66665.7982 | 58259.0583 | 275388.154 | -9224.9707
43.98 | 10.9442 | 1.4418 |  | 22087.2022 | -186064.888 | 646699.478 | 5989594.05 | 2310056.49 | -40990.1989 | 108637.04 | -9824.795 | 272286.652 | 250614.027 | 1858593.1 | -24537.3281 | 52637.6479 | -3237.0555 | 61236.4647 | 35232.4715 | 311833.743 | -9737.0025
44.38 | 11.3612 | 1.3833 |  | 110001.37 | -154426.27 | 652691.892 | 5417131.86 | 3716263.3 | -52764.9182 | 109128.8 | 811.8239 | 279330.212 | 170664.015 | 1716898.81 | -31415.0387 | 45191.4278 | -1898.0876 | 63479.1248 | 26611.61 | 265108.567 | -9106.6677
44.78 | 11.1294 | 1.3275 |  | 166869.538 | -95797.2771 | 630232.968 | 4146561.97 | 4510990.84 | -46385.0734 | 97828.5806 | 16662.1417 | 281048.272 | -32526.0507 | 1587933.86 | -28599.7504 | 43872.7094 | 887.9437 | 66722.3292 | 13245.2284 | 263490.585 | -8988.2701
45.18 | 11.0574 | 1.2728 |  | 196136.404 | -67575.7253 | 580882.564 | 3327960.41 | 5568004.05 | -49531.9406 | 99969.081 | 39975.834 | 264168.255 | -320078.189 | 1513751.02 | -25730.1768 | 39159.0137 | 6304.4995 | 60915.6464 | -7811.5162 | 236381.188 | -7165.0351
45.58 | 11.206 | 1.2152 |  | 228361.758 | -27420.6448 | 510899.694 | 2955687.24 | 5663229.81 | -51627.0905 | 97343.2992 | 29672.465 | 255055.558 | -288548.511 | 1629402.98 | -32119.6414 | 44417.101 | 8658.5048 | 59622.3249 | -23942.6324 | 251189.461 | -10350.0825
45.98 | 11.2863 | 1.1601 |  | 187183.467 | -41535.2722 | 450404.657 | 2701345.23 | 5121047.33 | -53017.8146 | 84224.4099 | 37705.5679 | 241498.29 | -259224.92 | 1461573.37 | -25338.5513 | 40651.5193 | 3740.377 | 58447.0258 | 4753.4551 | 247228.3 | -6528.4511
46.38 | 11.5752 | 1.1051 |  | 144515.167 | -92704.8001 | 407421.283 | 3725171.44 | 4481811.53 | -47951.5144 | 93903.4901 | 22989.7553 | 236039.533 | -122803.453 | 1428890.5 | -24104.2542 | 35872.5509 | 2992.2945 | 57695.0999 | -2507.5779 | 200034.655 | -3337.438
46.78 | 11.3004 | 1.0512 |  | 87807.1806 | -155736.798 | 393197.729 | 5576899.54 | 3606575.51 | -57985.27 | 120117.959 | 390.438 | 238248.233 | 45504.1476 | 1730712.05 | -40576.6477 | 38132.5347 | 3100.658 | 58881.5473 | -5032.1685 | 208628.557 | -11606.6036
47.18 | 11.6502 | 1.0336 |  | -6392.8079 | -161308.122 | 403122.123 | 5728738.25 | 1626645.1 | -36660.8753 | 105489.277 | -17632.1513 | 236701.326 | 351955.615 | 1855477 | -30013.4957 | 52831.1301 | -6843.4397 | 58299.1165 | 53130.056 | 307911.311 | -13725.4181
47.58 | 11.8867 | 1.0341 |  | -35968.6065 | -225037.256 | 461564.443 | 7090771.73 | 1131342.66 | -51511.6591 | 117590.406 | -37714.3167 | 253608.556 | 529562.444 | 1834360.72 | -31570.9708 | 49530.1284 | -6542.741 | 61664.2737 | 39081.8182 | 285977.282 | -10704.6788
47.98 | 11.6566 | 1.0341 |  | -65863.0178 | -232912.037 | 546222.046 | 7061753.1 | 403796.719 | -54572.3273 | 110380.697 | -41848.0221 | 276337.711 | 573140.743 | 1774299.82 | -33918.5259 | 47268.4762 | -7417.7426 | 65230.1139 | 47534.5612 | 274113.576 | -10973.8538
48.38 | 11.9078 | 1.0341 |  | -70473.322 | -227524.158 | 624225.636 | 6689546.46 | 193901.853 | -47084.3565 | 97335.5294 | -35703.7647 | 292692.318 | 574439.129 | 1674710.93 | -27525.659 | 47962.2243 | -10809.5431 | 68490.9538 | 75394.243 | 292765.931 | -9629.1833
48.78 | 11.8699 | 1.0341 |  | -2306.2189 | -173341.634 | 682801.06 | 5812843.37 | 1009343.26 | -53444.7947 | 95387.4434 | -35788.0007 | 304877.753 | 471228.817 | 1633115.32 | -37269.6531 | 46604.4375 | -4296.0421 | 68389.6176 | 39441.7627 | 279758.842 | -12071.6683
49.18 | 11.8126 | 1.0341 |  | 38982.5224 | -162125.738 | 732622.439 | 5181902.44 | 2219160.71 | -54204.7963 | 96242.9839 | -7538.0445 | 320931.607 | 221572.37 | 1506352.41 | -30027.1025 | 39182.2108 | -2575.4396 | 74625.6563 | 30614.5782 | 233038.556 | -8786.4771
49.58 | 11.8863 | 1.2318 |  | 115455.826 | -85835.9511 | 719600.972 | 3849152.77 | 3193645.44 | -47041.3433 | 85539.4557 | -134.5202 | 313620.769 | 52741.0151 | 1525055.21 | -28228.5702 | 42789.3659 | 3533.9706 | 70266.9347 | 2193.5385 | 252038.159 | -9327.0425
49.98 | 11.7986 | 1.4103 |  | 170291.469 | -57409.3504 | 692143.016 | 2935644.63 | 4857520.32 | -58530.5395 | 86996.8403 | 35619.1724 | 308101.246 | -214547.814 | 1436352.64 | -31042.5633 | 39765.6223 | 3457.0425 | 71207.8045 | 7971.5877 | 244370.574 | -8439.3108
50.38 | 12.0255 | 1.3845 |  | 206999.777 | -10863.361 | 620906.347 | 2180237.8 | 5080924.13 | -57837.2979 | 83273.4563 | 33920.8826 | 299665.689 | -272341.523 | 1444611.77 | -31954.5935 | 38822.8414 | 6753.8965 | 71969.3496 | -15071.3044 | 236252.818 | -11543.3071
50.78 | 11.8615 | 1.3688 |  | 193086.193 | -20827.6587 | 544667.544 | 2242055.15 | 4941038.3 | -59001.0206 | 80962.2717 | 33537.8309 | 280702.811 | -227580.642 | 1334784.28 | -30155.1548 | 34800.4794 | 5030.2701 | 68617.7691 | -8954.3 | 207807.82 | -8836.2499
51.18 | 11.8903 | 1.3614 |  | 194571.307 | -72423.5344 | 469472.545 | 3931081.44 | 5157292.47 | -42841.8333 | 105095.275 | 20307.0141 | 261636.304 | -201146.208 | 1581889.54 | -23177.4012 | 37961.5488 | 7224.0741 | 61415.7247 | -15305.4485 | 220045.357 | -7171.9505
51.58 | 11.8349 | 1.3522 |  | 113222.164 | -123993.032 | 438522.291 | 4782259.92 | 3884240.13 | -56381.8341 | 105443.073 | 10531.0117 | 258705.514 | 35713.9918 | 1648785.28 | -39757.6004 | 41850.1919 | -332.7874 | 64610.6329 | 18147.9523 | 241514 | -14579.2753
51.98 | 11.85 | 1.3388 |  | 45609.3291 | -165787.197 | 433959.139 | 5818830.63 | 2253239.49 | -42849.3653 | 109042.179 | -21168.7084 | 259803.802 | 376103.687 | 1627855.61 | -28366.8103 | 38993.0172 | -5366.8891 | 66432.763 | 34185.597 | 226958.342 | -9027.3442
52.38 | 11.8864 | 1.3314 |  | -7392.0985 | -193681.332 | 449338.8 | 6577540.61 | 1244451.85 | -44795.6641 | 115273.834 | -38437.1982 | 253777.067 | 434914.188 | 1783255.22 | -31310.4955 | 44106.77 | -2547.3805 | 59536.5853 | 26238.9357 | 257435.599 | -9265.4974
52.78 | 11.8485 | 1.3201 |  | -42006.3156 | -264864.697 | 521098.775 | 7855028.43 | 774468.032 | -65962.7396 | 117723.489 | -43138.2503 | 275127.628 | 603054.679 | 1700269.66 | -38292.8714 | 42048.7552 | -9389.1699 | 66929.876 | 58778.599 | 244688.743 | -10256.694
53.18 | 11.8218 | 1.3081 |  | -69473.4307 | -223605.277 | 578387.365 | 7120575.11 | -290225.742 | -42259.7276 | 99626.8875 | -57974.6469 | 280390.585 | 743711.385 | 1838162.39 | -30226.6453 | 54536.1978 | -10049.66 | 64543.7288 | 63824.6201 | 319312.805 | -13090.9709
53.58 | 11.7355 | 1.299 |  | -25981.678 | -225847.357 | 653066.731 | 6840646.54 | 896192.693 | -53836.2997 | 105182.854 | -37376.2072 | 296171.233 | 534769.62 | 1665105.03 | -34470.5032 | 44879.7927 | -6938.2606 | 69848.5925 | 47259.1157 | 280250.288 | -8622.0938
53.98 | 11.4642 | 1.2933 |  | -6719.8385 | -169355.705 | 702438.968 | 5361877.91 | 1461203.82 | -53683.6811 | 93244.9157 | -16234.7711 | 304924.696 | 346577.39 | 1613717.51 | -36297.2036 | 47148.7459 | -4808.3363 | 69252.7155 | 43183.2965 | 289297.169 | -11771.0071
54.38 | 11.6486 | 1.2874 |  | 68910.4257 | -103838.443 | 700103.34 | 4124064.19 | 2260935.32 | -49514.7855 | 81526.3152 | -9629.0957 | 302380.61 | 252330.206 | 1467326.28 | -34327.791 | 42816.973 | -2227.131 | 70098.0585 | 25255.3087 | 257836.155 | -13392.6149
54.78 | 11.4785 | 1.2817 |  | 128322.947 | -72590.2953 | 680766.034 | 2906679.66 | 3792680.64 | -53925.7945 | 73755.1941 | 24927.668 | 295685.886 | -160010.933 | 1220859.57 | -24452.9728 | 32823.4936 | 4430.9859 | 66523.8982 | -1069.1422 | 208453.689 | -6916.85
55.18 | 11.5134 | 1.2759 |  | 206118.117 | -34301.6734 | 622057.906 | 2756049.66 | 4978257.42 | -56367.3925 | 85244.3807 | 24577.6548 | 288700.564 | -247795.178 | 1383923.91 | -34075.4958 | 37242.1231 | 8669.4335 | 66361.0638 | -23672.9859 | 215998.852 | -10544.9055
55.58 | 11.4589 | 1.2734 |  | 188706.135 | -36164.4091 | 547212.43 | 2617929.59 | 5024289.59 | -53967.8792 | 88859.3509 | 35876.3693 | 269393.173 | -238908.09 | 1371283.46 | -30145.5385 | 34973.957 | 3826.5884 | 64203.529 | 2569.8904 | 205001.334 | -9815.7178
55.98 | 11.4574 | 1.2688 |  | 210407.346 | -53820.9358 | 462089.446 | 3532088.72 | 5248743.04 | -48822.3383 | 102769.879 | 20761.7994 | 246684.484 | -177649.964 | 1592418.43 | -29252.4798 | 39247.5932 | 6325.906 | 57103.1838 | -11666.7054 | 215698.493 | -9192.7938
56.38 | 11.397 | 1.2638 |  | 152019.48 | -97842.5902 | 410048.414 | 4295332.81 | 4582122.58 | -40415.8247 | 107673.167 | 16181.6241 | 240568.351 | -118497.929 | 1608095.68 | -26878.4616 | 41624.5127 | 4440.2033 | 60903.5718 | -8677.6833 | 257298.504 | -11445.1775
56.78 | 11.2449 | 1.2636 |  | 71040.6528 | -148096.483 | 383786.784 | 5237552.83 | 3005840.83 | -53373.5431 | 103490.496 | -2992.4169 | 227865.108 | 183343.023 | 1645377.55 | -38606.5334 | 43328.2092 | -2422.0029 | 55397.8977 | 26772.3158 | 250192.464 | -13981.3213
57.18 | 11.4283 | 1.2592 |  | 17534.8653 | -193027.544 | 387059.079 | 6184277.2 | 2038619.24 | -35550.9679 | 110652.316 | -17739.0236 | 227433.14 | 299043.897 | 1688151.88 | -19265.0868 | 38506.1045 | -3558.6838 | 55287.4995 | 33419.1961 | 217895.836 | -7698.8638
57.58 | 11.1592 | 1.2559 |  | -23706.4336 | -256123.578 | 433123.529 | 7936670.71 | 1410931.42 | -52753.8519 | 129700.899 | -40663.1742 | 241458.423 | 586660.479 | 1976359.23 | -32736.9354 | 51452.0619 | -8617.1129 | 58918.8773 | 53447.8066 | 309569.489 | -10696.168
57.98 | 11.3903 | 1.2526 |  | -48766.7651 | -291058.622 | 488365.084 | 8930979.94 | 575786.043 | -48571.6035 | 133275.904 | -60094.0202 | 255387.999 | 741344.777 | 1986042.37 | -32245.5883 | 49663.1375 | -9316.2842 | 63206.2754 | 49482.9679 | 278817.435 | -9808.4224
58.38 | 11.2128 | 1.2515 |  | -56793.7439 | -285887.438 | 551546.433 | 8839343.51 | 786814.714 | -51561.6716 | 141312.977 | -51852.0812 | 259865.091 | 779966.241 | 2207745.2 | -32888.2384 | 55544.3739 | -13645.7056 | 61726.4856 | 80265.5923 | 306164.001 | -10224.4649
58.78 | 11.3008 | 1.246 |  | 8231.5566 | -266496.368 | 612869.143 | 8488845.37 | 1680845.59 | -60534.5236 | 133503.39 | -46004.9944 | 276658.611 | 537214.755 | 2079181.43 | -38998.7248 | 56078.4877 | -4750.3692 | 63078.0115 | 38238.6061 | 323282.71 | -11663.0757
59.18 | 11.265 | 1.2441 |  | 29722.8153 | -196667.726 | 656313.057 | 6721966.19 | 1932492.26 | -45900.8417 | 112844.741 | -29687.9535 | 284509.498 | 522885.188 | 1957519.69 | -30359.4764 | 57798.8766 | -8983.9806 | 66621.8892 | 62852.6129 | 355674.909 | -11172.5179
59.58 | 11.1368 | 1.2408 |  | 90221.4154 | -162092.316 | 660913.459 | 5652630.11 | 3378684.27 | -58197.2772 | 108374.781 | -156.225 | 279194.833 | 169945.247 | 1804870.08 | -35455.2949 | 51402.8391 | -2557.9776 | 62695.1267 | 34161.9808 | 301228.011 | -8750.6139
59.98 | 11.3071 | 1.2295 |  | 147040.595 | -100233.361 | 649353.166 | 3998171.65 | 4542093.63 | -55033.5539 | 100810.657 | 28071.0522 | 285290.706 | -172176.001 | 1613974.47 | -31873.8502 | 41447.4955 | 2750.5538 | 65833.0038 | 14368.8476 | 255788.798 | -7943.5685
60.38 | 11.0807 | 1.2219 |  | 161834.094 | -30514.1108 | 597369.86 | 2474120.05 | 4408132.91 | -41069.4126 | 78723.7183 | 27070.3438 | 274400.77 | -160972.517 | 1483856.15 | -20003.3468 | 44154.8308 | 4284.0544 | 64247.7684 | -4727.883 | 265945.656 | -6551.7967
60.78 | 11.282 | 1.2232 |  | 207032.66 | -30443.142 | 511952.033 | 2698312.63 | 5209630.62 | -55219.9717 | 87546.1682 | 31781.3608 | 250055.592 | -234091.43 | 1483539.48 | -32809.6444 | 42497.2528 | 5420.1403 | 59434.7992 | -8886.026 | 252389.935 | -8869.6385
61.18 | 11.1417 | 1.2209 |  | 177205.907 | -18059.1025 | 443071.054 | 2158715.83 | 4936330.3 | -46140.6116 | 82035.4029 | 39503.568 | 238499.493 | -260025.764 | 1447858 | -23697.3132 | 41703.3682 | 2827.5681 | 58051.0114 | 7489.6204 | 242872.75 | -6635.9449
61.58 | 11.2011 | 1.2166 |  | 149953.866 | -64970.1903 | 385704.484 | 3664190.62 | 4093976.76 | -38511.265 | 92310.4127 | 10647.4069 | 227112.291 | -63204.1785 | 1617052.08 | -23491.7602 | 45985.2348 | 3300.8333 | 54671.2433 | 296.2983 | 253776.371 | -4040.237
61.98 | 11.0905 | 1.2113 |  | 105903.312 | -141398.834 | 353229.369 | 5476196.86 | 3313549.32 | -54404.2057 | 107456.112 | -11812.4528 | 217705.234 | 171317.58 | 1716307.97 | -40033.6424 | 44971.2411 | 695.0983 | 53125.9143 | 12558.8928 | 265400.289 | -13604.72
62.38 | 11.1167 | 1.2112 |  | 23902.266 | -217073.411 | 357126.378 | 6969626.58 | 2200647.03 | -42263.2613 | 118121.18 | -22366.2814 | 217103.521 | 330802.779 | 1731155.62 | -26950.1763 | 44291.9774 | -4567.9853 | 53830.6859 | 36898.6494 | 269015.07 | -8785.2702
62.78 | 10.9409 | 1.208 |  | -19455.6049 | -276808.876 | 391996.846 | 8714535.06 | 1522319.39 | -41636.5534 | 139535.919 | -45636.5303 | 222076.805 | 612875.354 | 2004497.97 | -21835.5643 | 47980.7572 | -8646.6766 | 53552.1102 | 51445.602 | 271268.614 | -8409.0087
63.18 | 11.0804 | 1.1981 |  | -20600.2038 | -329268.507 | 455872.354 | 10132567.5 | 1255134.72 | -65037.5085 | 153435.957 | -62820.1285 | 246082.245 | 686209.174 | 2061151.2 | -37991.044 | 45706.2569 | -6843.5592 | 60292.806 | 40988.433 | 236234.2 | -11513.8796
63.58 | 11.1054 | 1.1953 |  | -59565.5911 | -309652.944 | 525670.116 | 9551858.21 | 666816.815 | -50889.6565 | 146323.518 | -60710.3398 | 249732.302 | 802358.262 | 2295401 | -27011.8979 | 58521.3493 | -11456.2499 | 58096.3916 | 64267.6889 | 325763.073 | -7640.754
63.98 | 10.905 | 1.1966 |  | -6296.1981 | -288448.558 | 586163.784 | 9324691.89 | 1842437.36 | -60576.3718 | 151289.906 | -48194.4582 | 258364.263 | 784257.598 | 2442783.87 | -34139.9692 | 65489.8047 | -14234.3657 | 59411.1491 | 85349.3831 | 372082.691 | -10647.3273
64.38 | 11.1263 | 1.1922 |  | 40597.5304 | -237856.601 | 631616.425 | 8246920.08 | 2485032.14 | -50036.688 | 143929.06 | -36447.3285 | 277435.444 | 559246.584 | 2364925.22 | -33569.7675 | 63175.26 | -8035.3188 | 66275.6762 | 51403.9041 | 365280.036 | -10276.4436
64.78 | 11.0747 | 1.1869 |  | 82051.4521 | -192470.695 | 647816.438 | 6812449.7 | 3156673.17 | -44063.2742 | 124370.134 | -15020.5986 | 273837.259 | 341732.498 | 2034078.15 | -24872.7139 | 58319.3887 | -6387.9603 | 61145.2226 | 54445.4508 | 343430.45 | -6086.4435
65.18 | 10.9227 | 1.1855 |  | 150836.022 | -131089.071 | 630820.662 | 5323876.02 | 4736878.41 | -39672.2207 | 121429.461 | 12860.831 | 268515.656 | 49621.5681 | 1973537.01 | -27700.6519 | 53126.1381 | -954.8314 | 60677.0053 | 24842.1432 | 303835.841 | -6722.4781
65.58 | 11.1386 | 1.1803 |  | 199013.776 | -67095.9679 | 583535.779 | 3806112.69 | 5241651.56 | -40571.6036 | 103775.621 | 25159.5732 | 268528.191 | -151207.963 | 1750977.56 | -25561.9406 | 48538.8723 | 3397.0109 | 64192.5389 | 2848.5888 | 287884.146 | -5432.6397
65.98 | 11.0264 | 1.1762 |  | 205682.55 | -60096.9973 | 514327.67 | 3509889.18 | 5235944.48 | -50274.5838 | 93987.2083 | 27111.9109 | 250336.305 | -122430.648 | 1622403.18 | -26761.8574 | 48989.8278 | 1049.5779 | 60531.026 | 15226.7755 | 294376.57 | -5856.8261
66.38 | 10.8754 | 1.174 |  | 197864.86 | -73535.9446 | 439769.957 | 3680277.91 | 5620618.65 | -43808.5731 | 107014.915 | 36485.3206 | 229665.084 | -263066.761 | 1590365.6 | -24142.6703 | 39407.8778 | 4152.0581 | 55014.2678 | 1980.5422 | 231784.813 | -5567.0683
66.78 | 10.7933 | 1.1681 |  | 164094.938 | -105102.144 | 383085.044 | 4813336.51 | 5100953.59 | -29984.547 | 122230.273 | 17948.5739 | 219752.156 | -82801.4175 | 1891261.65 | -22100.8407 | 46186.0509 | 3184.7226 | 54062.5309 | -3758.1506 | 247947.589 | -6176.3596
67.18 | 10.9126 | 1.163 |  | 129369.677 | -150345.256 | 337909.554 | 6190693.64 | 3906223.39 | -36352.6442 | 123588.555 | -13640.393 | 209517.005 | 188765.541 | 1962525.15 | -25369.4656 | 52132.3687 | 171.3557 | 51171.3886 | 13201.4387 | 302899.688 | -9712.7463
67.58 | 10.8797 | 1.1565 |  | 41938.6103 | -207557.68 | 343695.909 | 6792963.93 | 2584647.55 | -37422.5057 | 121096.582 | -19677.9119 | 208904.761 | 276305.928 | 1812080.48 | -22733.3133 | 44494.0167 | -1678.4956 | 51124.8026 | 17023.0427 | 259092.605 | -7708.1119
67.98 | 10.7455 | 1.1567 |  | -5785.6533 | -250473.423 | 371905.053 | 7779600.61 | 1618243.26 | -36666.2638 | 126810.674 | -38640.224 | 213240.624 | 584356.965 | 1856589.59 | -20125.7307 | 43453.2456 | -9039.6543 | 51510.3968 | 54901.6301 | 256751.661 | -7913.724
68.38 | 10.9675 | 1.1509 |  | -28146.8848 | -303840.787 | 414412.22 | 9287750.49 | 1004943.71 | -55753.9809 | 137964.708 | -57332.1383 | 229279.1 | 695108.764 | 2007252.43 | -32768.559 | 48144.7409 | -8411.9368 | 57860.2123 | 42981.3286 | 265917.651 | -11877.0838
68.78 | 11.02 | 1.1459 |  | -69139.3688 | -308755.613 | 476011.973 | 9596243.37 | 768100.377 | -34933.0153 | 148512.277 | -52836.6393 | 232480.706 | 730558.68 | 2358650.19 | -20451.0086 | 61954.746 | -13085.9301 | 54740.3258 | 76472.5126 | 328875.868 | -8324.1804
69.18 | 10.8863 | 1.1426 |  | -4089.8315 | -332362.652 | 547766.072 | 10678567.5 | 1850586.87 | -62910.4711 | 173747.244 | -60791.3364 | 252652.292 | 898743.057 | 2474542.01 | -33408.396 | 57513.1734 | -16220.5354 | 60001.1859 | 89116.7094 | 302355.645 | -8104.496
69.58 | 10.693 | 1.1357 |  | 17934.6529 | -323798.491 | 608573.349 | 10197206.2 | 2600999.72 | -56553.4961 | 167962.018 | -42853.7218 | 266243.117 | 656765.621 | 2550336.47 | -27228.1215 | 65209.81 | -10904.413 | 62185.4065 | 64029.2928 | 359238.486 | -6224.6311
69.98 | 10.8753 | 1.1327 |  | 99955.424 | -267434.506 | 616286.803 | 9296318.83 | 3298980.2 | -66846.1733 | 156710.131 | -42555.1754 | 263378.908 | 589965.285 | 2392352.3 | -44220.1756 | 63099.9826 | -7993.1238 | 59598.8912 | 61020.1478 | 359143.933 | -13180.3149
70.38 | 10.8654 | 1.1294 |  | 128672.778 | -173817.181 | 613810.759 | 6908421.42 | 4080091.59 | -7914.4724 | 140038.945 | -12796.2731 | 264165.57 | 311691.338 | 2215774.68 | -8125.0121 | 59526.3347 | -5745.8351 | 62459.7083 | 44430.7789 | 346733.881 | -1646.7831
70.78 | 10.707 | 1.1202 |  | 178469.492 | -143471.489 | 592714.82 | 5744213.05 | 5523080.09 | -41231.0231 | 131892.968 | 20137.1083 | 261660.366 | -98107.2989 | 2117582.31 | -28896.7962 | 56509.9242 | 3160.1354 | 61232.4812 | 2581.981 | 319011.273 | -5673.9108
71.18 | 11.2084 | 1.1225 |  | 197828.355 | -84292.608 | 527910.56 | 4488113.76 | 5631299.51 | -27650.8767 | 120151.792 | 23556.5672 | 243369.594 | -21943.1539 | 2096609.94 | -16186.8692 | 57190.8479 | -550.8613 | 56256.1933 | 21262.0778 | 323539.041 | -3340.569
71.58 | 10.877 | 1.115 |  | 229367.099 | -87471.949 | 452580.333 | 4761943.27 | 6067123.69 | -51854.7766 | 127595.104 | 24314.1365 | 233986.974 | -66111.9641 | 1997275.05 | -44041.0419 | 50813.0253 | 305.0086 | 58179.5921 | 19132.148 | 300912.616 | -13162.1901
71.98 | 10.8299 | 1.1159 |  | 173289.488 | -91599.852 | 393831.648 | 4586387.66 | 5334770.93 | -26882.3358 | 123041.352 | 25166.8432 | 216448.629 | -131336.715 | 2052016.49 | -18210.0962 | 55487.8561 | 1792.1882 | 52654.3141 | 12670.5673 | 320954.375 | -5421.0895
72.38 | 10.6749 | 1.1141 |  | 136723.06 | -139929.869 | 342481.851 | 5969262.62 | 4530947.84 | -40010.0774 | 130517.931 | 1799.0948 | 203029.857 | 194650.431 | 2196096.02 | -30662.0114 | 59221.0774 | -4164.79 | 50030.7783 | 33126.8343 | 323784.767 | -9388.3961
72.78 | 10.7676 | 1.1094 |  | 97217.5917 | -186326.769 | 317136.005 | 6850327.61 | 3264350.19 | -43670.1709 | 124050.5 | -23279.3594 | 201522.356 | 289770.784 | 1916536.98 | -27568.7474 | 49860.8478 | -1536.6551 | 49889.5675 | 20711.1041 | 285829.891 | -6938.235
73.18 | 10.7814 | 1.11 |  | 20792.4889 | -208308.971 | 327627.402 | 7080079.42 | 1963646.11 | -35047.9097 | 116895.748 | -31446.2361 | 201437.801 | 496310.866 | 1915108.36 | -24899.6848 | 52779.9442 | -8588.3941 | 51888.2524 | 51947.7491 | 311138.039 | -6737.8665
73.58 | 10.6822 | 1.1095 |  | -31262.2937 | -281554.727 | 373963.558 | 8433866.15 | 1252175.41 | -48389.3645 | 128400.32 | -40560.4493 | 212210.516 | 558168.095 | 1872859.91 | -27089.2916 | 46493.6853 | -8946.1449 | 52066.5168 | 56877.9682 | 274565.562 | -8688.9942
73.98 | 10.5412 | 1.1024 |  | -65323.3617 | -303334.256 | 441355.672 | 8772533.33 | 332743.905 | -53774.3137 | 120016.339 | -55993.8309 | 228170.473 | 703827.521 | 1836422.75 | -25375.3324 | 49970.9292 | -9660.8975 | 55490.7121 | 50446.1714 | 282847.037 | -8748.6568
74.38 | 10.4491 | 1.1067 |  | -63415.19 | -319967.641 | 497264.625 | 9467147.1 | 601596.245 | -38036.5996 | 142128.569 | -60743.7625 | 234644.539 | 777865.289 | 2026524.94 | -14829.9714 | 45662.524 | -10250.6297 | 55154.987 | 58711.2075 | 263926.18 | -2470.4248
74.78 | 10.5972 | 1.1075 |  | 14762.1657 | -325160.321 | 542351.174 | 10370185.9 | 1837897.97 | -58841.7715 | 162231 | -63482.726 | 244018.106 | 749132.619 | 2376800.24 | -31348.6151 | 58952.0294 | -8914.766 | 56348.817 | 54715.1421 | 327359.943 | -9301.758
75.18 | 10.696 | 1.1061 |  | 30941.0274 | -305432.886 | 585516.114 | 9857094.36 | 2759134.12 | -49905.2664 | 166441.66 | -35263.5902 | 250696.903 | 540416.413 | 2546389.75 | -31287.4096 | 64601.1652 | -9368.3132 | 57698.8625 | 67275.9433 | 361717.198 | -10105.2787
75.58 | 10.5718 | 1.1064 |  | 97594.4779 | -207768.136 | 592936.307 | 7646379.98 | 3178228.28 | -39351.4266 | 137588.446 | -29541.8443 | 251402.562 | 591279.671 | 2185244.03 | -28623.4895 | 58923.3639 | -12574.9001 | 58971.1915 | 80320.1108 | 337093.318 | -10639.974
75.98 | 10.5059 | 1.1029 |  | 132471.793 | -175005.606 | 583320.345 | 6299755.51 | 4390635.12 | -31182.251 | 127514.334 | 5351.5034 | 247883.181 | 4839.1935 | 2000514.08 | -18293.2781 | 52117.8009 | 2625.5505 | 55581.8251 | 3148.541 | 297695.315 | -3928.9557
76.38 | 10.4818 | 1.112 |  | 190908.97 | -92590.078 | 538561.578 | 4495691.96 | 5164732.65 | -32569.5703 | 107373.394 | 22493.4081 | 238142.003 | 43775.6996 | 1877355.66 | -21274.2884 | 54796.8658 | -5655.5655 | 55184.7674 | 57160.5164 | 316091.585 | -6635.0187
76.78 | 10.3736 | 1.1033 |  | 198225.37 | -85642.1706 | 482798.503 | 4254319.44 | 5475092.79 | -30818.7638 | 111573.493 | 26382.583 | 233315.598 | -195928.256 | 1772464.71 | -16935.9284 | 46869.2255 | 4776.5185 | 56278.088 | -6481.304 | 272629.554 | -2745.623
77.18 | 10.4374 | 1.1116 |  | 209349.918 | -76267.9965 | 405349.881 | 4131690.61 | 5699011.6 | -39433.2661 | 113924.631 | 28008.8553 | 204313.984 | -148345.546 | 1806548.64 | -25911.287 | 48506.1392 | 1994.8435 | 47500.2828 | 10626.5205 | 278210.253 | -7160.7069
77.58 | 10.2965 | 1.1094 |  | 167468.364 | -85232.0015 | 350265.185 | 4089993.11 | 4774265.48 | -43478.1061 | 102523.816 | 19376.9966 | 202565.166 | -80369.3243 | 1655496.2 | -24212.9559 | 44546.2903 | 1383.834 | 50209.5591 | 9456.3579 | 265634.749 | -6526.5161
77.98 | 10.2682 | 1.1055 |  | 97000.5743 | -105731.696 | 305828.768 | 4457889.36 | 3389388.45 | -27425.7749 | 97371.5446 | 2229.853 | 188286.189 | 46066.9573 | 1688092.73 | -17680.7856 | 47082.9336 | 1676.0029 | 47514.0464 | -1694.4461 | 265628.273 | -6307.7302
78.38 | 10.3245 | 1.113 |  | 74364.7806 | -182120.045 | 282245.717 | 6260562.16 | 3089951.21 | -42656.2821 | 118602.774 | -12445.3617 | 177392.35 | 236002.293 | 1673805.2 | -27030.1346 | 39172.996 | -2940.6561 | 42847.1924 | 26602.9888 | 221237.754 | -5853.9448
78.78 | 10.2895 | 1.1105 |  | 1948.5463 | -189491.901 | 297774.412 | 6240164.6 | 1555681.65 | -32534.1655 | 102731.179 | -25663.9305 | 186945.556 | 467654.521 | 1749740.84 | -18948.6303 | 50893.57 | -10507.5185 | 47324.2148 | 66348.4554 | 301965.612 | -6973.8102
79.18 | 10.2982 | 1.1092 |  | -33981.987 | -255758.62 | 333498.317 | 7990222.16 | 851773.337 | -48239.0592 | 119215.315 | -48545.6875 | 191800.061 | 655566.893 | 1903182.19 | -33329.8563 | 50362.6143 | -9801.113 | 48154.5324 | 54033.4813 | 287607.345 | -10435.0092
79.58 | 10.2571 | 1.1096 |  | -61587.3718 | -252139.738 | 384524.334 | 7932659.52 | 203037.609 | -24556.7481 | 116686.422 | -57130.7875 | 200994.293 | 792927.433 | 1918950.68 | -12809.2114 | 52171.177 | -13721.4513 | 49430.1976 | 73269.1143 | 299062.264 | -7368.3676
79.98 | 10.1445 | 1.1086 |  | -37451.1238 | -306161.802 | 446564.045 | 9643010.5 | 671665.499 | -39748.9992 | 145030.065 | -70720.488 | 218599.346 | 789228.852 | 2032765.51 | -17602.0685 | 45705.5612 | -8959.5264 | 51531.9424 | 50424.2381 | 241455.851 | -4648.0278
80.38 | 9.9622 | 1.1103 |  | -27873.3146 | -313280.516 | 506982.994 | 10069495.8 | 1415542.45 | -43911.5082 | 162248.838 | -60963.9193 | 223006.79 | 872374.667 | 2508759.82 | -22023.4441 | 65235.1413 | -15185.5233 | 52714.5639 | 78420.0918 | 347793.675 | -6499.5892
80.78 | 9.9846 | 1.1109 |  | 26295.1339 | -291627.028 | 537653.17 | 9634901.38 | 2380767.16 | -55131.6605 | 159590.186 | -46167.2962 | 228779.63 | 714047.489 | 2481448.39 | -36067.4824 | 65130.6879 | -12560.4313 | 53155.1073 | 77405.685 | 365885.658 | -11403.5183
81.18 | 10.0306 | 1.1125 |  | 63355.7248 | -224070.393 | 556763.563 | 7715751.58 | 2644135.85 | -21500.6723 | 135627.35 | -31599.7031 | 232168.443 | 553331.871 | 2116770.24 | -8496.2387 | 55261.6503 | -11237.1052 | 52815.6405 | 70904.4329 | 308758.211 | 1292.4394
81.58 | 10.0459 | 1.1121 |  | 148716.215 | -194634.132 | 541311.684 | 7274657.67 | 4560850.43 | -39029.9628 | 145551.177 | -7986.2693 | 228914.926 | 241352.604 | 2208148.88 | -27928.4037 | 55822.141 | -3873.7679 | 54237.2995 | 34656.3932 | 313324.1 | -7231.9051
81.98 | 10.0032 | 1.1127 |  | 174369.772 | -91614.0341 | 512924.046 | 4586574.04 | 4713245.83 | -38439.7331 | 111715.684 | 10926.6713 | 225048.743 | -49807.5488 | 1899018.53 | -30834.9292 | 53750.3336 | 2556.7358 | 51721.5327 | 8331.086 | 301832.766 | -10913.0059
82.38 | 9.9146 | 1.1154 |  | 179845.682 | -67580.6022 | 458043.349 | 3705734.96 | 4812981.2 | -22006.4532 | 98730.6056 | 21170.4258 | 209085.924 | -69958.9259 | 1635653.59 | -6488.9496 | 44456.6035 | 273.2017 | 48258.5062 | 16641.757 | 254076.23 | 1654.334
82.78 | 9.9262 | 1.1181 |  | 205829.909 | -55613.8218 | 389567.733 | 3577543.04 | 5585688.6 | -43616.0565 | 106407.221 | 33401.2884 | 194196.077 | -170742.975 | 1781367.9 | -30786.4346 | 49823.3987 | 91.0858 | 46709.8676 | 21841.861 | 279650.376 | -7846.3537
83.18 | 9.8883 | 1.1171 |  | 189286.527 | -38023.1449 | 329934.377 | 3036650.31 | 4803751.78 | -32486.4998 | 89134.7604 | 21007.3861 | 184845.431 | -174341.865 | 1581677.88 | -15398.2472 | 46176.9753 | 4177.2397 | 44233.8811 | 2505.529 | 278064.294 | -2727.1056
83.58 | 9.7507 | 1.1207 |  | 127754.88 | -92147.5907 | 276535.455 | 4286355.26 | 3950978.84 | -30438.4106 | 103752.401 | 7576.8258 | 168810.791 | 37527.4064 | 1644419.38 | -19377.6982 | 42722.5474 | -169.7493 | 42209.4005 | 11715.7856 | 239717.751 | -5356.3386
83.98 | 9.8109 | 1.1269 |  | 97917.8954 | -129112.669 | 235339.515 | 5249586.2 | 3414938.22 | -34854.5761 | 109730.019 | -3087.6138 | 155202.07 | 222673.248 | 1726707.28 | -26730.6326 | 46794.654 | -6616.5862 | 39212.828 | 49532.3929 | 268433.262 | -7801.2173
84.38 | 9.5337 | 1.1253 |  | 14605.9496 | -145841.513 | 246587.631 | 4913546.93 | 2013111.39 | -32388.6144 | 90808.0273 | -10202.0497 | 161313.845 | 206330.539 | 1558646.55 | -23445.3727 | 45590.0564 | -2477.2958 | 40623.2957 | 23469.3168 | 273862.817 | -6609.9706
84.78 | 9.7242 | 1.1314 |  | -20707.8124 | -202220.958 | 257696.182 | 6356467.73 | 842961.623 | -31011.0181 | 96505.482 | -37758.5008 | 160186.167 | 515260.677 | 1507685.87 | -18406.5692 | 40002.2398 | -7851.318 | 39163.7871 | 44148.4696 | 228857.752 | -5298.0197
85.18 | 9.66 | 1.1316 |  | -42058.7075 | -205690.278 | 293845.127 | 6746396.71 | 309820.567 | -20766.7753 | 105795.422 | -53277.8607 | 171618.926 | 592614.741 | 1596826.61 | -17659.5276 | 40494.376 | -6663.3426 | 41855.2541 | 38314.058 | 221721.718 | -6612.476
85.58 | 9.6395 | 1.1356 |  | -75330.2106 | -260412.823 | 362984.049 | 7627292.44 | 226499.228 | -41683.0946 | 114624.856 | -48168.1402 | 186295.919 | 578868.448 | 1678116.31 | -24160.8612 | 39703.5485 | -6873.4431 | 44746.1334 | 38703.0841 | 221354.88 | -7067.4138
85.98 | 9.6831 | 1.1395 |  | -55487.4272 | -251786.039 | 417244.557 | 7921654.46 | 15648.9571 | -22096.9683 | 115428.71 | -63733.368 | 198683.229 | 904115.177 | 1774690.55 | -9312.7573 | 44400.3088 | -16600.4238 | 48722.5322 | 87467.9605 | 253160.856 | -3268.1162
86.38 | 9.5043 | 1.1387 |  | -23331.645 | -288027.005 | 476944.387 | 8776728.77 | 1494628.83 | -50995.4352 | 139271.689 | -43508.9462 | 209188.117 | 584131.682 | 2097112.42 | -28324.73 | 52773.2901 | -8209.9495 | 49089.377 | 48835.7257 | 295111.274 | -7900.0126
86.78 | 9.6756 | 1.1449 |  | 27277.6594 | -253480.312 | 510173.162 | 8147567.49 | 1974021.26 | -38987.2689 | 130155.087 | -37527.7591 | 214723.692 | 633789.459 | 2029574.11 | -20434.1407 | 53574.8868 | -13333.0291 | 49362.2273 | 83807.9223 | 308615.526 | -7901.7423
87.18 | 9.4061 | 1.1401 |  | 42242.9779 | -198379.723 | 530021.967 | 7008101.03 | 2388939.64 | -21211.7437 | 125620.473 | -28483.0645 | 220429.554 | 505433.669 | 2112429.16 | -13347.9865 | 59594.0649 | -9539.0271 | 51428.9149 | 57507.3703 | 332566.058 | -4808.9266
87.58 | 9.6186 | 1.1464 |  | 132025.598 | -156770.346 | 512064.087 | 6311087.72 | 4315923.34 | -26981.4551 | 137248.688 | -2431.066 | 207545.428 | 203556.52 | 2117881.5 | -22179.7384 | 53680.7328 | -4499.1339 | 45947.0408 | 41374.4691 | 292143.973 | -4152.1799
87.98 | 9.7823 | 1.1416 |  | 168273.215 | -109367.244 | 492569.085 | 5029889.19 | 4856716.11 | -32271.2792 | 119991.112 | 13337.0403 | 213907.553 | -9135.1568 | 1975336.32 | -23795.4238 | 54070.3009 | -159.3653 | 49735.5872 | 17383.9813 | 303306.249 | -7946.8946
88.38 | 9.7854 | 1.1432 |  | 187770.207 | -68194.9949 | 433656.394 | 4016600.31 | 4728687.14 | -16190.4917 | 103935.755 | 15158.3901 | 198722.977 | 6035.6976 | 1710281.64 | -6268.4462 | 47538.2075 | -2626.1725 | 46439.7279 | 34449.1535 | 277539.431 | 1002.5339
88.78 | 9.7121 | 1.1433 |  | 212361.611 | -73418.7207 | 369333.136 | 4272093.14 | 5621587.25 | -28881.3397 | 118942.462 | 24066.2576 | 182083.701 | -131971.411 | 1903166.12 | -19179.5898 | 49335.6476 | 1693.4551 | 43527.0116 | 9874.5711 | 273973.18 | -4742.1803
89.18 | 9.6307 | 1.1441 |  | 197984.308 | -76201.0878 | 311245.745 | 4298530.27 | 5556500.81 | -31286.3501 | 119215.752 | 25144.1 | 171851.883 | -145059.762 | 1920429.54 | -25185.8726 | 50599.8688 | 1913.1501 | 42382.2568 | 7561.8702 | 282624.925 | -6680.2741
89.58 | 9.4564 | 1.1439 |  | 134192.896 | -70335.3367 | 264310.1 | 4164884.17 | 4192646.52 | -19991.2685 | 112699.925 | 7820.1505 | 160075.05 | 109007.742 | 1921832.72 | -15242.6215 | 51079.3595 | -3166.4589 | 40288.6125 | 27623.6446 | 280748.087 | -3493.2651
89.98 | 9.5834 | 1.1471 |  | 90495.754 | -99097.644 | 222217.833 | 4434591.27 | 3228219.27 | -42937.585 | 100337.806 | 2052.1979 | 146500.093 | 145143.76 | 1691217.94 | -33069.9542 | 47945.0762 | -4492.3327 | 36978.1442 | 41551.1215 | 280596.789 | -11593.4156
90.38 | 9.5703 | 1.145 |  | 21156.5274 | -88172.1158 | 213193.371 | 3624958.73 | 1560454.49 | -76529.8385 | 72654.8196 | -9604.0724 | 146794.625 | 198230.442 | 1405139.63 | -15275.0348 | 41772.4513 | -3010.3093 | 36964.3395 | 26180.9999 | 253849.636 | -5439.9186
90.78 | 9.4643 | 1.1466 |  | -30945.5051 | -128854.779 | 232310.658 | 4241623.03 | 528458.225 | -30513.48 | 69112.5114 | -23917.4277 | 151039.192 | 340640.966 | 1234245.67 | -22347.7892 | 35070.8659 | -4429.4194 | 37514.5157 | 27281.7337 | 204829.088 | -6781.7851
91.18 | 9.2928 | 1.1461 |  | -70678.3853 | -161458.207 | 277157.501 | 4631978.14 | -140512.198 | -27116.0219 | 67200.6103 | -31843.3053 | 160943.924 | 446490.153 | 1094386.03 | -17653.8885 | 30248.007 | -6335.5917 | 39161.7996 | 38463.1602 | 190902.635 | -6032.9469
91.58 | 9.4647 | 1.1485 |  | -86639.1258 | -190041.274 | 325779.184 | 5551020.98 | -633386.189 | -18826.8498 | 75011.8272 | -44838.7171 | 172799.489 | 584486.779 | 1180428.48 | -14449.4076 | 33252.8312 | -9463.5674 | 40889.2092 | 53276.9685 | 203432.428 | -5420.0864
91.98 | 9.2918 | 1.1461 |  | -96573.1888 | -203402.771 | 387462.119 | 5934483.2 | -712613.293 | -23822.8725 | 85554.0401 | -49630.4311 | 186850.582 | 653663.534 | 1354315.43 | -17578.4297 | 33957.5495 | -9570.7172 | 44561.5536 | 51535.8724 | 196446.415 | -5985.832
92.38 | 9.4152 | 1.1495 |  | -67009.3956 | -187935.313 | 434066.714 | 5912360.15 | -196062.252 | -21133.9677 | 88434.8075 | -45576.3013 | 195329.695 | 626859.241 | 1529470.91 | -15083.0572 | 43123.0942 | -10195.9583 | 46710.0838 | 55717.0085 | 249956.536 | -6096.8449
92.78 | 9.302 | 1.1512 |  | -21923.6075 | -203707.215 | 479922.974 | 6621192.19 | 994983.901 | -30494.6711 | 112577.756 | -37552.0968 | 203412.322 | 533132.93 | 1723533.8 | -20407.5668 | 43018.58 | -8212.956 | 46510.5894 | 52187.5328 | 249507.247 | -6713.2842
93.18 | 9.2164 | 1.1515 |  | 32460.9731 | -194465.277 | 506984.797 | 6657808.87 | 2307745.29 | -28807.0936 | 123489.999 | -24411.25 | 209108.607 | 405090.102 | 1911036.78 | -19172.6383 | 49897.6747 | -6445.8449 | 47823.6454 | 43501.6434 | 276684.358 | -6033.5089
93.58 | 9.2616 | 1.1515 |  | 98921.8258 | -154197.395 | 499217.494 | 6202452.53 | 2920480.12 | -30580.1561 | 119703.963 | -26365.9286 | 207147.03 | 405233.712 | 1891489.82 | -22966.6311 | 49318.9537 | -5706.5436 | 46833.3939 | 45139.0616 | 275020.626 | -7756.3275
93.98 | 9.2473 | 1.1531 |  | 123929.75 | -117284.461 | 475785.402 | 4760210.86 | 3689313.32 | -14004.3806 | 103383.141 | 3300.2915 | 198612.583 | 68646.8003 | 1610170.02 | -5167.498 | 43351.1775 | -1385.105 | 45219.069 | 25821.762 | 252989.33 | 945.9125
94.38 | 9.2649 | 1.1527 |  | 185185.957 | -105463.236 | 437864.567 | 4722224.71 | 4955984.32 | -29644.244 | 113103.329 | 16124.4402 | 191628.747 | -85540.6009 | 1654043.89 | -16305.0674 | 40917.2579 | 1651.1884 | 44046.5603 | 9213.9181 | 228657.669 | -1656.3795
94.78 | 9.21 | 1.1539 |  | 198417.147 | -73133.1733 | 375506.623 | 4506837.49 | 5298334.16 | -22697.4527 | 121539.364 | 16640.2283 | 177101.885 | -9630.4694 | 1976392.02 | -18329.8647 | 53064.6225 | -1754.1939 | 42641.4475 | 25922.4356 | 292254.66 | -6303.3011
95.18 | 9.1753 | 1.1535 |  | 198080.874 | -75075.5202 | 312248.896 | 4488057.25 | 5271565.82 | -24126.4053 | 119476.886 | 16315.5045 | 159089.412 | -6398.8511 | 1926791.29 | -20019.9085 | 50885.532 | -1762.0776 | 38380.4245 | 26891.3386 | 284676.881 | -5698.8688
95.58 | 9.1141 | 1.1511 |  | 168117.419 | -47040.3762 | 255102.008 | 3270670.6 | 4688843 | -27922.1097 | 93920.7441 | 23168.2108 | 145132.687 | -102715.43 | 1703044.97 | -18789.3615 | 49208.4665 | 373.026 | 35465.8503 | 14608.4107 | 282250.25 | -6762.3669
95.98 | 9.0127 | 1.1486 |  | 118017.133 | -56082.6247 | 216029.583 | 3095008.26 | 3579717.41 | -29766.8441 | 85072.4311 | 12602.7855 | 139359.121 | -46654.4511 | 1361260.15 | -17297.1796 | 36184.7607 | 1176.7565 | 34779.7952 | 10095.2213 | 226604.728 | -4252.8269
96.38 | 8.895 | 1.1472 |  | 55172.7577 | -73690.462 | 183722.809 | 3296259.81 | 2223990.73 | -27834.6482 | 73922.5042 | -2665.4586 | 130040.067 | 137563.583 | 1270341.87 | -14572.8295 | 36823.1185 | -2419.0085 | 32998.2829 | 21583.5876 | 212590.893 | -5419.8995
96.78 | 8.9931 | 1.148 |  | 15968.2737 | -104773.164 | 165243.98 | 3940698.65 | 1305959.57 | -27343.6406 | 71244.0869 | -15822.0464 | 121380.203 | 238189.57 | 1260061.74 | -21206.4131 | 37429.162 | -3308.2697 | 30521.7791 | 23777.792 | 218596.736 | -6801.9495
97.18 | 8.9118 | 1.1472 |  | -28041.9882 | -118458.334 | 180747.166 | 3945091.1 | 338109.268 | -24525.9727 | 59890.5 | -24510.7721 | 125607.677 | 367546.485 | 1141435.65 | -20818.3759 | 34826.3584 | -6424.1808 | 31633.8054 | 41468.024 | 217268.91 | -8739.4704
97.58 | 8.8535 | 1.1449 |  | -80230.9142 | -137585.957 | 215535.148 | 4145678.47 | -842100.531 | -4956.0808 | 52037.5124 | -37430.42 | 135350.115 | 467170.041 | 926099.003 | -6740.516 | 28016.3135 | -7282.7809 | 33670.0951 | 40410.7192 | 171443.273 | -3838.5558
97.98 | 8.8136 | 1.1432 |  | -91617.1552 | -180779.445 | 261671.088 | 5166498.27 | -1055007.86 | -15544.9273 | 62603.3039 | -47224.0724 | 143103.007 | 582292.6 | 1003616.94 | -14416.5309 | 28197.007 | -9136.17 | 34614.5536 | 48939.404 | 166739.282 | -4947.6611
98.38 | 8.7258 | 1.1411 |  | -105105.992 | -169595.651 | 309676.501 | 4937684.87 | -1393041.87 | -9335.2233 | 60912.8152 | -49512.6426 | 153735.097 | 598799.981 | 1043732.49 | -13113.7653 | 28622.7701 | -9009.3561 | 36678.4453 | 50354.9365 | 171539.157 | -6001.2798
98.78 | 8.6164 | 1.1415 |  | -88158.0165 | -181586.268 | 351893.867 | 5212785.48 | -1096827.59 | -243221.432 | 68021.018 | -49346.8013 | 159324.947 | 576709.482 | 1003678.62 | -9887.1019 | 24936.9048 | -8090.0579 | 36803.7087 | 43924.1929 | 145792.851 | -4050.9806
99.18 | 8.5016 | 1.1415 |  | -52637.6788 | -163907.231 | 392386.214 | 5207560.3 | -258454.909 | -12182.7284 | 79023.8467 | -41975.4101 | 165983.553 | 530602.457 | 1204791.52 | -9891.5488 | 28865.7342 | -7725.3354 | 37857.8234 | 42373.8624 | 158116.225 | -4786.0398
99.58 | 8.4112 | 1.1408 |  | -6989.0308 | -160491.643 | 419144.2 | 5414056.04 | 913499.508 | -25970.9074 | 89594.7564 | -29399.0998 | 170592.987 | 389080.102 | 1459169.45 | -17818.3111 | 39942.3102 | -5596.3503 | 38584.2026 | 36666.1118 | 227288.426 | -7182.8871
99.98 | 8.3075 | 1.1403 |  | 28942.8201 | -123442.301 | 426455.508 | 4525808.98 | 1301970.35 | -23065.3781 | 78194.3976 | -20852.6323 | 169299.813 | 387168.08 | 1284637.42 | -17750.0726 | 36235.676 | -8633.4618 | 37955.2318 | 58132.2872 | 213636.783 | -5701.6098
100.38 | 8.187 | 1.1391 |  | 67248.4708 | -68845.586 | 415181.439 | 2889197.18 | 2033774.21 | -22768.4716 | 61169.9333 | 1112.2206 | 164477.988 | 55220.3291 | 1061970.39 | -11922.5257 | 30769.2357 | -578.8022 | 36602.3261 | 16111.4364 | 185558.77 | -3911.1624
100.78 | 8.0628 | 1.1409 |  | 101781.928 | -24266.4276 | 383615.84 | 1855008.54 | 2540084.04 | -20149.8753 | 54411.9816 | 12142.4035 | 156467.547 | -17739.3943 | 985933.37 | -8732.4992 | 28809.73 | -1219.7253 | 35505.0027 | 19779.9964 | 164677.709 | -1597.4009
101.18 | 7.8915 | 1.1421 |  | 141560.335 | -26248.5655 | 341100.531 | 2025166.09 | 3312849.68 | -36908.2853 | 60971.238 | 17137.0122 | 145995.295 | -99070.4224 | 1002692.87 | -14490.654 | 27081.444 | 1182.4591 | 34119.7633 | 7671.9438 | 160818.609 | -3447.9936
101.58 | 7.7667 | 1.1441 |  | 167106.635 | -7994.7512 | 287015.013 | 1956036.02 | 4003404.57 | -30645.8543 | 67750.8617 | 24015.7155 | 129157.669 | -181116.344 | 1236235.26 | -13650.7853 | 35716.2126 | 2516.3881 | 30080.818 | 937.8014 | 198346.162 | -4007.8148
101.98 | 7.6487 | 1.1449 |  | 173810.665 | -18486.4391 | 229115.921 | 2371841.28 | 4252159.59 | -32130.9922 | 76090.143 | 22966.5944 | 114669.291 | -171519.483 | 1256556.74 | -17048.0287 | 34239.9427 | 2466.4144 | 27241.2561 | 574.2863 | 194331.736 | -4962.4323
102.38 | 7.5545 | 1.1466 |  | 158977.04 | -7017.6886 | 172301.949 | 1992316.1 | 3903447.36 | -24328.5745 | 69904.3231 | 21944.265 | 98081.5672 | -160839.525 | 1169686.4 | -12429.9068 | 32717.9828 | 1835.5952 | 23762.6718 | 3634.9526 | 190013.083 | -3463.2996
102.78 | 7.4403 | 1.1582 |  | 135671.204 | 5527.0675 | 126037.172 | 1429204.49 | 3412664.25 | -21479.1882 | 60146.8558 | 21874.4855 | 86602.6733 | -168254.741 | 976503.833 | -10862.8044 | 25918.1242 | 2064.6855 | 21697.2723 | 157.0587 | 143379.444 | -2387.7167
103.18 | 7.3261 | 1.1703 |  | 103079.039 | -20980.9589 | 85612.7973 | 1560684.28 | 2543907.75 | -29980.0351 | 47482.206 | 13216.4706 | 76911.1967 | -105502.319 | 722973.735 | -12956.2619 | 18190.227 | 1766.3428 | 20013.3332 | -1196.7843 | 104416.234 | -3166.2301
103.58 | 7.1982 | 1.1729 |  | 52233.246 | -20746.5255 | 55170.6494 | 1277574.05 | 1413688.02 | -17467.7724 | 34117.0763 | 3907.5847 | 66319.1313 | 12437.103 | 634246.657 | -9573.2818 | 18708.5264 | -713.8212 | 17682.9072 | 10685.8293 | 112956.41 | -2535.381
103.98 | 7.0526 | 1.1728 |  | 12088.6565 | -41881.4047 | 40924.0511 | 1637129.72 | 640523.378 | -14913.3517 | 32904.633 | -6135.7557 | 61809.3438 | 112551.961 | 594830.121 | -11401.6853 | 16863.6282 | -2030.9461 | 16874.4189 | 15460.1014 | 109620.333 | -2875.9812
104.38 | 6.9416 | 1.1728 |  | -36527.4285 | -57050.2223 | 39183.8742 | 2147562.69 | -238418.851 | 215.9397 | 35399.6096 | -18642.1984 | 60078.1008 | 252899.152 | 685073.129 | -8709.6472 | 20689.5694 | -4506.1977 | 16523.34 | 26714.9384 | 123629.092 | -3206.9883
104.78 | 6.8256 | 1.1728 |  | -56801.1643 | -117675.373 | 48639.5081 | 3371193.69 | -661497.085 | -35004.5756 | 45448.6952 | -31993.9072 | 60465.3205 | 394518.436 | 710190.367 | -9059.1591 | 18692.0701 | -6573.3279 | 16214.3581 | 33205.2515 | 104643.724 | -3306.5578
105.18 | 6.6937 | 1.1728 |  | -96983.6698 | -110385.252 | 72563.666 | 3209201.01 | -1500356.21 | 5456.9893 | 33830.6343 | -38921.0124 | 64096.9176 | 477201.996 | 647763.002 | -5027.7316 | 19839.3013 | -8067.6046 | 16617.4325 | 41152.0293 | 120713.382 | -4073.4421
105.58 | 6.588 | 1.1728 |  | -112891.708 | -129621.614 | 103613.344 | 3442851.23 | -1883164.87 | 8549.1105 | 30179.0504 | -43522.3742 | 69573.6229 | 529545.953 | 574689.505 | -2354.6327 | 18303.597 | -9089.6633 | 17236.4898 | 46510.8793 | 114024.462 | -2565.8706
105.98 | 6.4636 | 1.1728 |  | -109748.846 | -159436.114 | 139879.021 | 4157450.35 | -1785187.5 | 3799.7597 | 39299.6457 | -47185.4127 | 77327.3022 | 572126.472 | 621678.939 | -3648.3776 | 17251.088 | -9936.3614 | 18850.6849 | 50203.1478 | 100660.656 | -1986.2668
106.38 | 6.3557 | 1.1728 |  | -110641.826 | -151983.897 | 176344.578 | 4129182.09 | -1730934.69 | 3197.0036 | 43131.7021 | -46997.4487 | 83708.8193 | 579804.46 | 748660.894 | -6632.3789 | 21801.4071 | -10087.7471 | 19697.6922 | 51441.8989 | 124851.339 | -3912.4489
106.78 | 6.2557 | 1.1728 |  | -105142.583 | -139028.478 | 213233.928 | 3761233.36 | -1677740.66 | 4425.126 | 39912.8923 | -43902.2554 | 91118.7997 | 539956.07 | 706839.016 | -3241.0851 | 19387.3289 | -8969.6257 | 20885.2903 | 46149.287 | 112285.602 | -2386.3185
107.18 | 6.1633 | 1.1728 |  | -92504.7984 | -126251.057 | 244728.501 | 3528237.05 | -1400286.4 | 4083.8726 | 40691.9786 | -39230.0032 | 97409.3009 | 475287.465 | 693074.995 | -4842.772 | 18247.347 | -7401.7807 | 21843.2065 | 38829.396 | 104625.772 | -3584.2036
107.58 | 6.0846 | 1.1728 |  | -71857.6264 | -104029.274 | 270265.755 | 3008198.56 | -1028057.55 | 7895.4783 | 35900.0872 | -31168.3503 | 102179.09 | 395418.071 | 619624.541 | -1752.647 | 16648.77 | -6494.8796 | 22439.2739 | 33270.1632 | 87197.8112 | -1312.5159
107.98 | 6.0338 | 1.1728 |  | -40828.8968 | -84199.1308 | 289571.495 | 2623836.96 | -308196.578 | -1117.7565 | 37927.1982 | -19295.0939 | 104497.632 | 282958.378 | 693104.776 | -6893.9692 | 20063.6601 | -5536.9649 | 22332.0756 | 35298.2386 | 110429.661 | -3006.5963
108.38 | 5.9318 | 1.1728 |  | -5284.5561 | -65221.0132 | 296829.535 | 2131768.28 | 153843.341 | -10860.479 | 30973.3982 | -13912.7726 | 106446.705 | 232198.273 | 598126.419 | -6518.7007 | 18832.7305 | -4641.1071 | 22984.9648 | 30275.8652 | 113439.775 | -3287.9264
108.78 | 5.8271 | 1.1728 |  | 24926.6599 | -44291.0471 | 290313.935 | 1588286.16 | 663449.651 | -13510.1527 | 28793.9447 | -5202.779 | 103080.794 | 111240.446 | 466128.427 | -6596.6779 | 12908.2612 | -2025.764 | 22134.3832 | 16729.0477 | 76446.3977 | -1783.8897
109.18 | 5.7491 | 1.1728 |  | 64918.4998 | -28280.9923 | 277118.698 | 1127350.74 | 1550930.86 | -27769.5397 | 29816.1043 | 9735.758 | 98585.5991 | -69476.0882 | 445304.286 | -9704.3003 | 11180.309 | 929.8869 | 21221.0744 | 4084.2587 | 61003.8805 | -2176.2063
109.58 | 5.6514 | 1.1728 |  | 98463.3564 | -15025.3802 | 262028.744 | 1078209.16 | 2248048.86 | -25909.6121 | 36940.9034 | 14487.9153 | 95655.7609 | -119308.085 | 525623.555 | -9603.2569 | 12865.3495 | 2020.9651 | 20900.9282 | -1659.3319 | 72981.3907 | -2131.8378
109.98 | 5.579 | 1.1728 |  | 118497.421 | 3477.1093 | 233412.26 | 919612.999 | 2678646.39 | -28801.4019 | 38842.7214 | 19308.8787 | 87420.2113 | -131729.33 | 716339.335 | -9918.3822 | 20954.5335 | 1058.5147 | 19312.0236 | 5032.2468 | 117105.751 | -3068.5042
110.32 | 5.5367 | 1.1728 |  | 139856.486 | 17899.0177 | 208245.903 | 706422.212 | 3134574.22 | -32317.3742 | 40037.2417 | 24849.6425 | 80849.297 | -184372.107 | 728313.122 | -8910.8782 | 20385.7909 | 1544.2961 | 18086.2171 | 2055.2425 | 105591.722 | -1564.2274
110.52 | 5.5138 | 1.1728 |  | 144672.446 | 22288.3662 | 190900.548 | 577955.803 | 3290295.6 | -33846.9174 | 40102.0203 | 28188.689 | 76235.0373 | -252169.258 | 718718.268 | -11419.867 | 20286.4754 | 3609.0191 | 17037.3649 | -6850.7042 | 114767.676 | -2518.1508
110.72 | 5.4758 | 1.1728 |  | 152335.313 | 29842.1759 | 173940.639 | 360782.408 | 3419504.81 | -37390.9503 | 39017.0821 | 30976.9845 | 72312.8555 | -299992.153 | 642834.345 | -12959.0757 | 16537.7702 | 4907.4829 | 16453.0895 | -14058.2981 | 94464.7427 | -2747.2755
110.92 | 5.4355 | 1.1728 |  | 153932.696 | 38551.5874 | 155191.49 | 18649.7926 | 3378028.49 | -39125.1085 | 32276.1725 | 33195.5858 | 67639.7275 | -323750.192 | 532184.299 | -10974.6116 | 13589.7873 | 5139.2389 | 15523.6664 | -15662.2828 | 78179.2472 | -1708.391
111.12 | 5.4038 | 1.1728 |  | 148555.583 | 49345.8251 | 136259.232 | -358012.951 | 3164808.13 | -36594.704 | 24381.2613 | 33333.6938 | 62958.6557 | -332922.864 | 454365.211 | -9682.7087 | 13380.2411 | 5386.3916 | 14693.5226 | -16285.7505 | 81101.4853 | -1759.2531
111.32 | 5.3628 | 1.1728 |  | 146982.209 | 55616.1683 | 117686.648 | -540259.689 | 3081053.46 | -34807.044 | 22284.9922 | 33287.1321 | 57992.6209 | -328260.316 | 418601.752 | -9225.871 | 12000.7157 | 5180.159 | 13667.6169 | -16190.7739 | 71159.5376 | -1638.1575
111.52 | 5.3358 | 1.1728 |  | 150984.424 | 43104.2025 | 97905.1952 | -312508.047 | 3220884.05 | -41949.9662 | 25128.376 | 33131.7703 | 52609.1398 | -347330.338 | 372562.332 | -12228.1985 | 8478.9717 | 6121.4654 | 12531.3605 | -22476.2475 | 51311.3073 | -2074.2296
111.72 | 5.2662 | 1.1728 |  | 136754.297 | 36279.4411 | 81373.4179 | -339049.072 | 3133190.61 | -42924.8513 | 24753.7442 | 34241.2274 | 48429.6297 | -346322.995 | 387700.944 | -12011.8405 | 9242.0019 | 6244.7271 | 11882.2695 | -25004.8227 | 54071.4779 | -2341.5682
111.92 | 5.2292 | 1.1728 |  | 140119.362 | 49862.9613 | 55628.4743 | -444770.178 | 2995238.33 | -35262.4834 | 22771.8826 | 31634.2523 | 41877.0165 | -323209.926 | 412756.106 | -10027.7531 | 11103.8201 | 5501.1788 | 10855.9411 | -20131.3729 | 64618.7541 | -2135.2043
112.12 | 5.1878 | 1.1728 |  | 135004.309 | 38476.4389 | 42491.3274 | -282662.33 | 2887322.17 | -37718.7458 | 20890.9758 | 30767.5381 | 37844.3607 | -306880.536 | 397049.114 | -10156.9296 | 12046.5363 | 4684.9762 | 9757.6034 | -15397.9074 | 63761.4162 | -2579.6393
112.32 | 5.1321 | 1.1728 |  | 125365.635 | 33272.5835 | 24110.3406 | -99094.1844 | 2779765.02 | -41975.2274 | 25722.1732 | 28521.2844 | 33043.4217 | -304380.389 | 377131.61 | -15080.7688 | 10295.2461 | 4912.9532 | 8879.3493 | -16570.0799 | 54004.7918 | -1847.282
112.52 | 5.0758 | 1.1728 |  | 117913.886 | 31516.137 | 6034.9546 | -57537.3549 | 2562176.99 | -29346.1744 | 23721.3052 | 24834.6621 | 28283.7712 | -247132.791 | 417685.888 | -10094.4595 | 11503.5472 | 3855.6919 | 7999.0583 | -13197.0332 | 65466.8175 | -2398.9222
112.72 | 5.0439 | 1.1728 |  | 110334.564 | 26878.7753 | -8464.5378 | 121493.181 | 2440823.96 | -27348.703 | 26173.8454 | 21571.8605 | 24151.6956 | -207727.423 | 428169.882 | -7644.1543 | 10176.6741 | 3416.5241 | 7075.4167 | -12037.623 | 55851.2514 | -1837.4264
112.92 | 5.0072 | 1.1728 |  | 102561.192 | -2719.0259 | -23522.7839 | 549178.518 | 2384809.49 | -51351.8204 | 30787.7241 | 19413.4419 | 20037.8535 | -202921.039 | 449328.178 | -8370.4073 | 9570.9142 | 3787.5646 | 6232.9154 | -15259.4622 | 47280.7129 | -1683.1345
113.12 | 4.9635 | 1.1728 |  | 92258.0623 | 5588.5057 | -35306.9204 | 639074.69 | 2187604.03 | -20818.4392 | 30830.6564 | 15350.046 | 17161.3006 | -155097.776 | 470233.525 | -7787.7457 | 10839.78 | 2956.0048 | 5925.1895 | -11731.9491 | 66787.0289 | -1724.1028
113.32 | 4.9326 | 1.1728 |  | 75780.309 | 12080.0082 | -44447.9676 | 516359.127 | 1791324.76 | -16646.5881 | 26474.541 | 11421.7397 | 14545.9218 | -81371.9648 | 518691.755 | -5490.4247 | 15268.3177 | 773.7823 | 5315.5072 | -180.0177 | 88291.1939 | -2066.7901
113.52 | 4.9105 | 1.1728 |  | 59571.1011 | 1687.9246 | -52353.2836 | 657200.698 | 1518252.09 | -6027.4489 | 27289.1725 | 8895.3107 | 11906.6504 | -64851.5234 | 493193.868 | -5879.1249 | 13301.2144 | 730.8774 | 4678.1437 | -643.982 | 75356.3086 | -1596.2305
113.72 | 4.8734 | 1.1728 |  | 51434.3513 | -14710.4524 | -58623.7775 | 928467.048 | 1344880.04 | -19231.8168 | 26270.1975 | 5926.5662 | 10316.7845 | -44697.5376 | 415406.067 | -5808.2568 | 10761.539 | 525.3392 | 4477.5167 | -697.2086 | 61997.7501 | -1200.2243
113.92 | 4.8406 | 1.1728 |  | 35468.328 | -16675.4176 | -64843.6711 | 950250.052 | 998270.555 | -9598.9084 | 22620.8963 | 2111.031 | 8547.7792 | -1456.2376 | 383063.821 | -4474.7557 | 11688.4561 | -479.5824 | 4124.3586 | 5039.1788 | 66638.8692 | -1153.2686
114.12 | 4.8155 | 1.1728 |  | 21790.4641 | -15742.2413 | -68893.7429 | 926272.85 | 694526.669 | -4882.9427 | 20992.4036 | -1253.8271 | 7355.904 | 61358.2761 | 425734.11 | -2531.4451 | 13813.7976 | -2254.3644 | 3905.8055 | 14274.164 | 80655.6804 | -1085.7458
114.32 | 4.7908 | 1.1728 |  | 8668.6931 | -36368.8477 | -71044.5088 | 1360079.49 | 537299.619 | -6350.4269 | 26130.1066 | -3857.6254 | 6217.9739 | 52631.8442 | 433807.565 | -3756.4202 | 11451.5894 | -1195.1577 | 3294.2969 | 10482.3095 | 67401.7201 | -1301.7395
114.52 | 4.7315 | 1.1728 |  | -2850.6079 | -52336.4508 | -70374.8866 | 1782984.63 | 260407.196 | -5066.4327 | 29416.1393 | -11398.3958 | 7018.9191 | 135975.237 | 444564.803 | -4474.4652 | 9723.4402 | -2086.2663 | 3900.5169 | 11067.2498 | 49519.1639 | -1719.54
114.72 | 4.7222 | 1.1728 |  | -16950.7504 | -51209.7528 | -68742.9838 | 1720151.68 | -62839.9274 | 5029.1146 | 25970.5697 | -15087.0069 | 6164.4531 | 230732.097 | 454443.502 | -301.015 | 12302.1746 | -5104.0111 | 3412.0829 | 26299.943 | 68835.4254 | -1313.0333
114.92 | 4.6726 | 1.1728 |  | -31924.4165 | -65680.3987 | -69402.4755 | 2033542.03 | -397273.697 | 3163.9801 | 25524.9206 | -20022.1001 | 6035.7635 | 232640.617 | 470109.802 | -532.942 | 13413.2751 | -3762.637 | 3601.8206 | 17762.8792 | 77511.6349 | -840.8621
115.12 | 4.6156 | 1.1728 |  | -40509.2475 | -71848.9085 | -64948.3119 | 2348395.63 | -519682.501 | 8108.1398 | 31103.8258 | -24787.2303 | 6760.0353 | 308246.371 | 538645.627 | -862.1218 | 14460.8032 | -5640.0217 | 3342.3286 | 28717.7025 | 82222.0264 | -1340.338
115.32 | 4.6024 | 1.1728 |  | -50833.362 | -92804.3187 | -53316.2969 | 2674141.61 | -634633.075 | 4013.7835 | 31575.1137 | -27375.8571 | 8854.5559 | 362519.27 | 562434.965 | -1631.5027 | 15747.4903 | -7161.9116 | 3865.5534 | 35910.9888 | 87909.4162 | -1907.4128
115.52 | 4.5561 | 1.1728 |  | -64274.4249 | -94215.9873 | -49347.627 | 2645844.21 | -908037.746 | 5850.103 | 30578.6253 | -28606.194 | 9133.7551 | 343140.122 | 518115.743 | -2053.4591 | 13610.5736 | -6073.2701 | 3791.1829 | 30370.46 | 74600.1175 | -1867.9753
115.72 | 4.4933 | 1.1728 |  | -78670.0212 | -94918.8031 | -40281.2368 | 2535315.05 | -1318179.28 | 11664.3788 | 23739.659 | -32844.9401 | 12049.8505 | 384780.028 | 411342.086 | 1765.0652 | 11434.2059 | -6521.8286 | 4678.9597 | 30316.9877 | 64404.166 | -577.1888
115.92 | 4.474 | 1.1728 |  | -89561.6656 | -90632.951 | -32650.6939 | 2420675.03 | -1625704.67 | 21570.196 | 20775.5219 | -36298.9511 | 13060.9518 | 459497.821 | 368291.366 | 4727.6439 | 10218.5979 | -8726.4888 | 4560.2028 | 42319.0024 | 59706.0699 | -405.4142
116.12 | 4.437 | 1.1728 |  | -102277.169 | -105943.54 | -21913.0834 | 2675403.94 | -1832267.17 | 17192.6424 | 21927.8012 | -38769.7674 | 15138.0252 | 439675.817 | 348761.468 | 1923.3066 | 9054.449 | -7113.4315 | 4866.7607 | 32292.4068 | 52903.7139 | -747.5827
116.32 | 4.3793 | 1.1728 |  | -105197.33 | -108229.139 | -10694.3578 | 2812965.26 | -1859844.75 | 22083.4804 | 23071.7283 | -40158.7447 | 17867.2082 | 478545.584 | 401245.755 | 3792.5218 | 11673.0771 | -8550.814 | 5496.0699 | 39872.681 | 64546.704 | -988.1788
116.52 | 4.3588 | 1.1728 |  | -105831.742 | -119949.913 | -1066.4453 | 3137558.15 | -1814901.21 | 17473.5235 | 28572.5833 | -42132.501 | 19366.7384 | 492731.147 | 446286.114 | 1094.4805 | 11402.3489 | -8341.4009 | 5542.9493 | 38710.0137 | 62420.0412 | -1724.1284
116.72 | 4.3293 | 1.1728 |  | -108397.716 | -121819.617 | 8997.5945 | 3168539.72 | -1793123.65 | 16191.0128 | 30401.9964 | -41304.9002 | 21547.7973 | 482111.941 | 463801.294 | 922.6098 | 11375.8986 | -8165.9942 | 5887.6621 | 37931.6773 | 60567.4859 | -1425.2538
116.92 | 4.2898 | 1.1728 |  | -113150.265 | -128063.339 | 21560.5368 | 3242545 | -1926039.16 | 16088.9652 | 28111.6453 | -42719.1014 | 24954.5939 | 490091.679 | 444046.4 | 3105.524 | 11561.3638 | -8114.0311 | 6703.252 | 37304.0615 | 62797.5093 | -737.2307
117.12 | 4.2787 | 1.1728 |  | -114112.261 | -129462.772 | 34179.1492 | 3324011.55 | -2009966.08 | 19604.826 | 28260.9144 | -45456.4583 | 27884.0241 | 553295.424 | 445334.745 | 4707.2796 | 12044.814 | -10043.3198 | 7256.6904 | 48116.8197 | 68917.0408 | -595.2453
117.32 | 4.2631 | 1.1728 |  | -119708.999 | -136260.6 | 47452.1446 | 3490463.77 | -2115567.88 | 15307.4674 | 28802.8125 | -47198.9522 | 30680.6874 | 559876.575 | 484695.37 | 3294.0326 | 13795.5151 | -9816.7177 | 7672.8417 | 46131.5855 | 76043.1929 | -964.5149
117.52 | 4.2318 | 1.1728 |  | -115842.623 | -137726.096 | 61825.9482 | 3564647.43 | -2015227.94 | 15362.1836 | 31293.1253 | -46996.2677 | 33771.0128 | 571488.345 | 529934.347 | 1685.8833 | 14913.8257 | -10287.2402 | 8241.2496 | 48936.0059 | 82715.7318 | -1353.8128
117.72 | 4.2166 | 1.1728 |  | -112387.331 | -140167.823 | 73800.2344 | 3658337.12 | -1876446.26 | 15362.383 | 34399.855 | -45643.6306 | 36119.0973 | 544805.023 | 549155.602 | 971.8632 | 14840.9683 | -9568.4121 | 8452.4351 | 46138.342 | 83490.6341 | -1572.4182
117.92 | 4.2107 | 1.1728 |  | -107238.775 | -144518.884 | 89643.9788 | 3695964.79 | -1735330.79 | 9769.7315 | 35958.3557 | -43552.3172 | 40131.5874 | 508317.835 | 543525.913 | 670.4168 | 13487.6413 | -8534.191 | 9264.8186 | 40459.9701 | 70406.1388 | -1078.8861
118.12 | 4.1944 | 1.1728 |  | -110686.58 | -135057.844 | 100349.702 | 3542114.98 | -1779108.87 | 15020.3334 | 35151.5091 | -42941.6038 | 42834.2125 | 506323.33 | 555781.223 | 882.7726 | 14485.7977 | -8607.278 | 9802.9828 | 40998.4204 | 81131.3443 | -1470.4617
118.32 | 4.1923 | 1.1728 |  | -109789.989 | -134252.451 | 116050.798 | 3462174.35 | -1872324.43 | 12256.041 | 30890.6904 | -43767.2915 | 46792.5908 | 526353.063 | 515563.405 | 1941.0492 | 13938.9228 | -9169.2723 | 10683.939 | 43856.0699 | 77309.6724 | -1370.9734
118.52 | 4.2035 | 1.1728 |  | -105474.759 | -126422.441 | 131467.806 | 3230256.97 | -1872675.69 | 16719.1633 | 27318.1264 | -42461.209 | 49965.9777 | 524546.059 | 442880.28 | 3777.9523 | 12028.5306 | -9573.4054 | 11038.9352 | 47530.7609 | 64971.8779 | -590.5338
118.72 | 4.1976 | 1.1728 |  | -105966.311 | -121814.902 | 140375.465 | 3073466.3 | -1836174.98 | 14963.9013 | 25759.1715 | -39944.742 | 51882.8753 | 470522.548 | 422583.116 | 3417.2189 | 11108.1603 | -7698.665 | 11400.8462 | 36387.2944 | 61532.3845 | -826.9601
118.92 | 4.1891 | 1.1728 |  | -94929.166 | -116537.268 | 155855.542 | 2875467.33 | -1637087.43 | 12716.6869 | 22910.9324 | -36340.263 | 55591.805 | 430734.438 | 398903.224 | 2416.9191 | 11611.269 | -7097.5807 | 12110.2093 | 34990.8623 | 70077.3371 | -1493.4986
119.12 | 4.1903 | 1.1728 |  | -86395.4661 | -105060.792 | 167592.251 | 2660955.38 | -1439984.1 | 12237.7469 | 24521.5487 | -32940.0528 | 58292.7649 | 387562.874 | 409357.488 | 387.8574 | 11186.5897 | -6230.4167 | 12476.4158 | 31088.9386 | 63003.4936 | -1670.0191
119.32 | 4.1849 | 1.1728 |  | -77416.4146 | -103611.779 | 178962.012 | 2588163.64 | -1257149.75 | 7893.1304 | 23837.8194 | -29889.8145 | 61261.0977 | 341291.613 | 378642.37 | -597.9815 | 10750.5231 | -5274.6707 | 13092.2018 | 26471.4493 | 63087.968 | -1521.1891
119.52 | 4.1737 | 1.1728 |  | -73756.0678 | -93101.3404 | 187611.076 | 2406813.16 | -1227252.21 | 10597.3807 | 22223.1396 | -28563.3486 | 63728.4444 | 349553.229 | 398638.602 | 1317.992 | 11976.636 | -6098.755 | 13635.4005 | 30980.5953 | 65621.4998 | -1074.0774
119.72 | 4.176 | 1.1728 |  | -66269.2717 | -93357.9082 | 195677.96 | 2473902.95 | -1118433.09 | 10059.5808 | 24557.8241 | -28969.3778 | 65489.5875 | 364070.664 | 419105.579 | 1105.177 | 12157.323 | -6519.6687 | 13941.1372 | 32641.4823 | 65161.1952 | -1089.7276
119.92 | 4.1724 | 1.1728 |  | -53632.4415 | -93389.0327 | 203700.86 | 2565723.43 | -854015.447 | 7079.2707 | 27489.6297 | -26954.5643 | 66959.9958 | 353756.268 | 453600.348 | 677.6368 | 12779.6035 | -6727.5545 | 14124.5786 | 35015.2289 | 68496.5463 | -1018.765
120.12 | 4.1771 | 1.1728 |  | -42613.2166 | -85745.0311 | 209466.507 | 2399820.43 | -591142.539 | 3749.4889 | 28626.236 | -22957.9592 | 67776.3816 | 308443.331 | 498990.486 | -1267.8191 | 14337.8908 | -5820.8023 | 14180.5248 | 31913.9284 | 76541.0932 | -1984.4722
120.32 | 4.1844 | 1.1728 |  | -27411.3676 | -76945.9494 | 215225.852 | 2114407.55 | -268161.149 | 713.488 | 27666.8187 | -17200.5742 | 69067.2728 | 214998.647 | 435133.356 | -2315.8257 | 11304.0917 | -3377.722 | 14378.3628 | 19152.4916 | 61960.1785 | -1284.0838
120.52 | 4.1861 | 1.1728 |  | -17214.4671 | -59768.8047 | 220198.964 | 1607395.2 | -96738.3244 | 518.5069 | 21693.1243 | -10984.7593 | 70714.9956 | 149992.22 | 348940.186 | -1631.5205 | 9611.8966 | -2520.0509 | 14739.0868 | 16003.933 | 56230.204 | -813.6622
120.72 | 4.2028 | 1.1728 |  | -11101.7565 | -47576.3097 | 225295.336 | 1260622.13 | -48291.7878 | -7604.4912 | 16372.2762 | -7969.0597 | 72369.0953 | 114607.521 | 310429.901 | -2707.9814 | 9074.5106 | -1743.7759 | 15152.7537 | 11678.2561 | 50796.4814 | -1043.4217
120.92 | 4.2053 | 1.1728 |  | 1082.0703 | -48543.571 | 227751.749 | 1276061.36 | 164932.11 | -11604.2101 | 16976.8658 | -5947.944 | 72884.8129 | 83491.9331 | 264653.555 | -4969.3609 | 7289.3504 | -1017.1587 | 15196.0724 | 8680.1774 | 43661.984 | -1182.9981
121.12 | 4.2012 | 1.1729 |  | 12029.1136 | -38288.6086 | 228951.428 | 1142151.41 | 318859.48 | -11630.1219 | 16869.9096 | -4680.8619 | 73212.6114 | 80200.7587 | 285587.512 | -5228.7442 | 8064.9741 | -1127.3614 | 15291.8381 | 8953.9456 | 48976.5273 | -1961.3401
121.32 | 4.2248 | 1.1733 |  | 29594.6057 | -35249.9657 | 228887.586 | 1089666.15 | 724853.771 | -16019.2592 | 19430.6278 | 414.3079 | 72542.1223 | 31259.195 | 289298.512 | -5563.9887 | 7261.6362 | -618.8195 | 14980.2597 | 7587.7637 | 41650.6547 | -1764.3742
121.52 | 4.2403 | 1.1738 |  | 43513.703 | -27291.2166 | 227794.673 | 901585.198 | 1114457.34 | -18376.618 | 21529.57 | 6952.9294 | 72326.8415 | -74657.7571 | 293627.413 | -7428.7162 | 6811.1087 | 1949.1314 | 14919.233 | -4825.7807 | 38940.922 | -1839.3167
121.72 | 4.2553 | 1.1744 |  | 59283.0488 | -18673.9033 | 227096.616 | 696702.56 | 1460794.23 | -25970.7493 | 20923.7939 | 12984.4218 | 72930.2101 | -138443.82 | 284851.273 | -7089.2195 | 6868.7548 | 2776.8461 | 15199.5948 | -7863.4609 | 39166.7186 | -1638.5539
121.92 | 4.2905 | 1.1753 |  | 71451.5004 | -12544.6317 | 224543.869 | 602036.489 | 1675777.24 | -29393.5446 | 22807.4021 | 14594.0536 | 72927.1413 | -162731.706 | 270978.74 | -8614.6398 | 5218.5116 | 3477.424 | 15235.2732 | -11906.1046 | 26297.8225 | -1475.1188
122.12 | 4.3266 | 1.1761 |  | 79350.084 | -5287.2316 | 220752.489 | 401019.54 | 1761023.4 | -31469.1343 | 19208.8924 | 16649.2783 | 72403.3059 | -163965.342 | 255012.056 | -7668.8168 | 6085.1972 | 2827.8842 | 15247.9246 | -7635.9648 | 33461.6891 | -1701.6667
122.32 | 4.3613 | 1.1768 |  | 85423.9851 | 6059.6424 | 213717.223 | 165398.387 | 1836188.69 | -31886.3281 | 17440.2169 | 18345.4676 | 70884.0455 | -193023.079 | 255610.478 | -6828.5764 | 6403.5248 | 3767.2197 | 14930.5793 | -13038.7094 | 34944.8863 | -1292.4571
122.52 | 4.3933 | 1.1778 |  | 103102.018 | 9436.5178 | 208863.909 | 142483.713 | 2234124.39 | -33431.8877 | 20865.4413 | 22511.4757 | 69909.5475 | -233548.851 | 258986.971 | -7910.0373 | 5353.0417 | 4201.6413 | 14766.9397 | -14436.025 | 27788.2644 | -959.0343
122.72 | 4.4356 | 1.1789 |  | 115345.886 | 12238.4465 | 200843.329 | 139358.885 | 2542983.39 | -36510.7719 | 23594.5353 | 25942.0181 | 68473.6037 | -282033.078 | 330741.92 | -7981.2035 | 7710.4107 | 5377.5116 | 14585.2812 | -19877.3758 | 38737.6104 | -1258.834
122.92 | 4.4741 | 1.1801 |  | 128616.553 | 14969.7828 | 194031.601 | 200389.245 | 2882795.99 | -37303.5271 | 27760.0434 | 28946.264 | 67607.6601 | -301653.371 | 438099.323 | -8787.1362 | 11328.9669 | 5349.7712 | 14591.601 | -18414.6811 | 64469.9442 | -1779.4293
123.12 | 4.5055 | 1.1814 |  | 139588.676 | 11914.5419 | 184157.33 | 473768.957 | 3177748.46 | -34851.0862 | 35617.1401 | 29604.327 | 65873.9851 | -309222.242 | 531187.322 | -9924.0534 | 13680.7879 | 5177.235 | 14308.2133 | -16584.0682 | 72896.8918 | -1608.9717
123.32 | 4.5506 | 1.1828 |  | 148080.218 | 11389.1376 | 174556.366 | 623844.631 | 3360578.59 | -34862.8803 | 38959.9251 | 29688.7086 | 63871.4114 | -283879.163 | 607958.412 | -10046.1728 | 16029.2994 | 4190.8285 | 14043.7806 | -11632.4567 | 85362.9832 | -2050.3815
123.52 | 4.6106 | 1.1843 |  | 155531.3 | 14044.5427 | 164047.285 | 608664.108 | 3529640.38 | -35267.0763 | 41041.9311 | 31019.0016 | 61216.7427 | -296430.356 | 626987.667 | -10015.2313 | 16338.4311 | 4270.8695 | 13517.528 | -11836.0407 | 87344.2484 | -2170.9627
123.72 | 4.6491 | 1.1857 |  | 158738.524 | 24180.8242 | 148421.032 | 357767.222 | 3601003.68 | -37603.852 | 38735.8353 | 33728.6515 | 57827.2591 | -337948.375 | 588129.144 | -10272.3285 | 14641.8422 | 5459.3795 | 12935.3201 | -19371.0816 | 75402.4149 | -1930.5027
123.92 | 4.7061 | 1.1872 |  | 160774.826 | 40787.1997 | 136909.328 | -210566.413 | 3554751.1 | -42258.7654 | 29039.1118 | 37821.8532 | 55567.4165 | -370265.274 | 492726.157 | -8488.1576 | 13631.7675 | 5471.6847 | 12586.8177 | -17197.7608 | 77302.7102 | -1140.4639
124.12 | 4.7519 | 1.1888 |  | 158740.15 | 56295.1016 | 123133.283 | -687787.106 | 3457102.99 | -37423.4571 | 22470.3515 | 40603.9419 | 52893.387 | -418466.236 | 415126.335 | -8262.7897 | 12034.2004 | 6598.8687 | 12134.6003 | -22365.0593 | 68064.6784 | -701.9617
124.32 | 4.7902 | 1.1905 |  | 160035.857 | 55157.8191 | 109591.451 | -759522.517 | 3450400.4 | -46590.2109 | 19104.7463 | 41616.6718 | 50291.8658 | -439107.218 | 348042.098 | -9644.9549 | 10092.3396 | 7196.9133 | 11741.8329 | -25980.0659 | 59650.8496 | -976.3068
124.52 | 4.8338 | 1.1924 |  | 164980.436 | 49518.3548 | 95082.1311 | -626807.857 | 3559605.07 | -48081.6091 | 21728.7079 | 41209.4483 | 47291.7233 | -427196.654 | 348818.202 | -10336.4094 | 9285.3999 | 6802.2808 | 11229.027 | -24833.9655 | 53048.4763 | -988.1254
124.72 | 4.8885 | 1.1942 |  | 165259.226 | 47363.9704 | 80927.6273 | -475141.373 | 3633917.56 | -49830.6465 | 24253.6929 | 40979.1853 | 44036.1201 | -439490.396 | 398453.09 | -12517.839 | 11345.454 | 7480.2427 | 10586.1613 | -29465.5041 | 62027.2043 | -2030.3291
124.92 | 4.9069 | 1.1959 |  | 158998.823 | 52375.4546 | 63601.7143 | -513317.726 | 3573094.95 | -45594.9791 | 26147.0204 | 40371.5663 | 40484.7187 | -439514.198 | 448881.544 | -13242.3164 | 12277.3335 | 7785.3617 | 10043.429 | -31125.9986 | 70137.4792 | -2353.3233
125.12 | 4.9345 | 1.1984 |  | 156701.498 | 47695.207 | 50862.3833 | -475367.348 | 3439497.64 | -42083.3489 | 22996.3477 | 38606.4562 | 37847.3632 | -415417.15 | 367142.747 | -11236.9979 | 10586.8069 | 6948.3244 | 9645.6961 | -25691.3347 | 66297.2699 | -1854.2581
125.32 | 4.9935 | 1.2012 |  | 151826.002 | 44081.4043 | 35520.7687 | -454762.563 | 3331713.82 | -44867.0641 | 23092.6947 | 37483.5048 | 34085.7883 | -399132.372 | 304748.693 | -10951.37 | 7281.8232 | 6376.9458 | 8846.7422 | -22942.2046 | 44187.5272 | -1362.4044
125.52 | 5.0328 | 1.2035 |  | 139416.018 | 46846.4866 | 22255.8787 | -548323.521 | 3139576.41 | -37429.9333 | 21422.2031 | 37107.6255 | 31352.2723 | -418850.085 | 321994.003 | -10407.9486 | 8021.0459 | 7389.7436 | 8400.7427 | -28714.9373 | 46919.9511 | -1891.5366
125.72 | 5.0627 | 1.2063 |  | 136643.241 | 39520.3036 | 11701.7047 | -331076.762 | 3117086.17 | -36556.1156 | 24882.893 | 34574.7284 | 29985.7109 | -383338.26 | 378261.068 | -8451.9069 | 8843.0696 | 6946.8758 | 8420.2978 | -28439.5418 | 46086.784 | -1023.5334
125.92 | 5.1263 | 1.2095 |  | 135766.94 | 20120.4938 | 1351.8997 | 262078.033 | 3183088.82 | -36734.3081 | 32230.805 | 30605.5377 | 28094.7112 | -319996.229 | 493013.828 | -8521.0294 | 12157.4449 | 5452.8764 | 8060.3354 | -21214.7116 | 65069.5145 | -1776.3478
126.12 | 5.1772 | 1.2128 |  | 129317.348 | -70.5236 | -8849.7627 | 948317.982 | 3204588.5 | -34839.5588 | 42474.1177 | 25964.1098 | 26368.5396 | -273506.411 | 663241.478 | -10079.1395 | 16946.0016 | 4768.4049 | 7976.0095 | -18721.4269 | 88215.5299 | -1870.8693
126.32 | 5.2226 | 1.2165 |  | 118226.559 | -5755.1659 | -19169.7007 | 1288668.41 | 3044566.96 | -27853.4817 | 48307.4128 | 20822.9248 | 24287.2501 | -177776.287 | 832674.035 | -10346.7985 | 23036.4896 | 2081.8601 | 7715.7623 | -3655.9647 | 126317.142 | -3162.8209
126.52 | 5.2928 | 1.2203 |  | 109742.837 | -13402.7562 | -25376.8752 | 1514598.91 | 2811769.02 | -20300.8199 | 50725.356 | 15060.5657 | 22639.0261 | -115917.985 | 826799.252 | -11862.3441 | 21814.2868 | 1160.0498 | 7259.0459 | 157.0625 | 116064.402 | -4267.9768
126.72 | 5.3532 | 1.2238 |  | 95028.428 | -29153.7572 | -31176.9808 | 1550572.65 | 2468869.98 | -28555.3387 | 44573.4836 | 13428.2465 | 21792.5316 | -118926.283 | 646104.974 | -11686.5626 | 15526.0892 | 1506.2411 | 7052.2315 | -2192.365 | 83032.7513 | -2509.9241
126.92 | 5.3924 | 1.2271 |  | 67176.5156 | -16603.1126 | -35591.0241 | 1016015.43 | 1760168.61 | -21168.9786 | 29848.9161 | 10514.4946 | 21808.0367 | -73290.6031 | 534967.303 | -7053.3741 | 16156.2935 | 107.5786 | 7316.4017 | 5896.6628 | 94436.155 | -2056.4527
127.12 | 5.4547 | 1.231 |  | 53144.4702 | -23415.0065 | -37952.8539 | 1102789.67 | 1431496.16 | -12488.4113 | 28045.3437 | 6096.4131 | 21628.959 | -17808.8222 | 475614.911 | -2862.5039 | 14126.1858 | -947.5943 | 7266.7335 | 9933.8492 | 83212.0944 | -539.5092
127.32 | 5.5114 | 1.2343 |  | 43204.542 | -46214.5572 | -35608.7622 | 1693357.97 | 1319994.77 | -13919.8686 | 33744.6915 | 866.6038 | 23196.5472 | 22739.7476 | 557068.238 | -1951.593 | 16560.6427 | -1113.8271 | 7643.0068 | 8216.1829 | 95804.3187 | 401.3783
127.52 | 5.5586 | 1.2373 |  | 28048.7219 | -66591.4216 | -36975.0033 | 2558275.21 | 1279048.92 | -8281.5676 | 49010.1052 | -5585.9745 | 23452.5544 | 83504.0204 | 802144.378 | -5814.1422 | 22450.4944 | -1565.7978 | 7791.0889 | 7843.3654 | 117406.505 | -2315.9157
127.72 | 5.608 | 1.2404 |  | 24286.4711 | -93311.5852 | -32314.9915 | 3380637.21 | 1332759.48 | -11269.1571 | 61916.3892 | -11681.9367 | 25142.5883 | 183806.078 | 989149.263 | -8053.319 | 26275.8571 | -3949.6158 | 8357.1232 | 21115.7726 | 137810.858 | -3288.8255
127.92 | 5.6796 | 1.2438 |  | 10859.1567 | -111027.663 | -27058.154 | 3857411.83 | 1116396.33 | -12547.5403 | 65626.2639 | -16827.4865 | 26441.3437 | 238707.596 | 1030524.76 | -9410.6529 | 27053.9841 | -4887.0274 | 8338.9238 | 26727.1299 | 145605.705 | -4335.9094
128.12 | 5.751 | 1.2462 |  | -9136.9366 | -118472.97 | -16929.5629 | 3823065.99 | 639896.222 | -10934.8438 | 61781.3441 | -20895.975 | 30011.0841 | 266328.276 | 904555.453 | -6883.5752 | 21580.6288 | -4854.603 | 9148.8617 | 25654.9426 | 109989.795 | -2794.3073
128.32 | 5.7957 | 1.248 |  | -36540.8785 | -104589.807 | -3897.54 | 3195750.43 | -168147.858 | 144.9491 | 44558.9575 | -25541.7297 | 34264.5624 | 337405.233 | 745575.995 | -66.8787 | 20523.3825 | -6590.7403 | 10170.5904 | 34241.1989 | 112458.894 | -160.3846
128.52 | 5.863 | 1.25 |  | -60898.6776 | -94674.9354 | 4253.3543 | 2860006.86 | -765878.874 | 7491.2216 | 35968.2584 | -29802.4727 | 35911.7182 | 381191.685 | 663021.555 | 1198.9635 | 19398.7948 | -6988.6871 | 10259.9501 | 37422.9027 | 116994.128 | -1717.8046
128.72 | 5.9138 | 1.2514 |  | -60057.5377 | -114106.119 | 23833.097 | 3101278.68 | -676020.558 | 3816.0476 | 35704.2995 | -27520.7535 | 40910.0477 | 341074.363 | 566126.951 | -81.5581 | 16487.6398 | -6523.9386 | 11143.2144 | 36245.7267 | 96048.7291 | -464.4089
128.92 | 5.9421 | 1.2532 |  | -71236.0021 | -121058.142 | 37816.2592 | 3318304.86 | -746562.943 | 1901.9828 | 39961.3368 | -28644.3829 | 45242.3912 | 323441.297 | 645993.787 | -3229.2697 | 17686.6567 | -4975.4486 | 11972.9078 | 25097.3273 | 99624.2329 | -2030.6401
129.12 | 5.9922 | 1.256 |  | -71388.3249 | -136126.536 | 58163.7836 | 3738512.35 | -750630.927 | 3852.7543 | 44284.1929 | -32403.365 | 52051.6312 | 375663.302 | 689520.927 | -981.9842 | 19165.0367 | -6231.827 | 13761.3906 | 31658.7798 | 110679.16 | -1248.498
129.32 | 6.0695 | 1.2588 |  | -70664.8875 | -165968.436 | 78067.894 | 4635278.26 | -618553.586 | -161.5721 | 58272.5109 | -37761.6968 | 57664.7365 | 440481.027 | 812504.597 | -2589.9771 | 19284.1792 | -7121.8321 | 14566.8536 | 34559.528 | 97841.4715 | -1795.6504
129.52 | 6.1257 | 1.2606 |  | -80691.1899 | -178141.993 | 98765.9645 | 5203252.36 | -739195.984 | -784.2566 | 69976.8099 | -45202.4509 | 63834.6992 | 515330.523 | 1010932.35 | -7136.6595 | 23478.6209 | -7580.7502 | 16169.7741 | 34762.3676 | 118300.266 | -3702.479
129.72 | 6.1896 | 1.2623 |  | -78232.3851 | -187541.699 | 121249.844 | 5415977.1 | -744862.869 | -11143.8331 | 69654.4622 | -47255.414 | 68841.9954 | 596029.163 | 1070582.19 | -6175.5844 | 27079.4208 | -10512.4535 | 17028.3141 | 50611.8369 | 141181.201 | -3547.9386
129.92 | 6.2821 | 1.2638 |  | -81807.914 | -184368.937 | 144781.098 | 5297878.26 | -796337.756 | -3374.9248 | 68377.4618 | -45936.1486 | 74699.3703 | 569140.722 | 1031066.68 | -3856.5295 | 25973.3426 | -10025.8902 | 17950.1827 | 50596.8213 | 138937.33 | -2239.1966
130.12 | 6.3605 | 1.2646 |  | -83039.913 | -170259.621 | 168800.535 | 4848367.51 | -830428.275 | -2488.5263 | 61997.9711 | -41880.7453 | 80752.4168 | 508524.194 | 977968.083 | -4100.3467 | 25453.1246 | -8399.1935 | 18960.1375 | 42999.3367 | 140715.533 | -2979.3063
130.32 | 6.4177 | 1.2655 |  | -81573.8151 | -167814.487 | 196029.703 | 4623121.86 | -806100.786 | -4736.0436 | 58605.7547 | -38916.3105 | 89131.2663 | 452880.729 | 905194.917 | -3055.7507 | 22920.0046 | -6805.1281 | 20774.9723 | 34995.698 | 126285.365 | -2256.7329
130.52 | 6.4981 | 1.2673 |  | -72959.3241 | -164261.601 | 221998.472 | 4512043.81 | -710825.853 | -4853.7967 | 56501.9369 | -37648.8776 | 96468.7594 | 453002.702 | 857319.723 | -3811.7594 | 21092.1358 | -6856.0575 | 22196.2565 | 34548.8437 | 114357.201 | -2944.0753
130.72 | 6.5843 | 1.2695 |  | -68235.6925 | -160098.108 | 246653.709 | 4400918.67 | -595056.636 | -8832.7511 | 55703.9477 | -34420.81 | 103091.613 | 420024.64 | 835250.404 | -5195.1131 | 19913.9792 | -6455.1207 | 23368.3702 | 34242.0108 | 106203.243 | -2889.1768
130.92 | 6.6435 | 1.272 |  | -67178.2054 | -140876.701 | 268470.667 | 3918597.62 | -655270.149 | -2463.9153 | 49324.988 | -32031.0959 | 109198.141 | 388472.608 | 813337.112 | -6631.3037 | 20866.5929 | -5623.7924 | 24763.2586 | 31329.8144 | 119515.451 | -3901.3758
131.12 | 6.7237 | 1.2746 |  | -53438.4415 | -121388.02 | 287251.034 | 3431944.31 | -426340.637 | -4045.9539 | 44979.2113 | -26324.3448 | 113877.066 | 358435.234 | 760469.015 | -3604.6084 | 19466.8355 | -5964.3515 | 25521.8426 | 33825.0082 | 108837.324 | -2517.7976
131.32 | 6.8233 | 1.2768 |  | -34182.6606 | -112872.761 | 307401.509 | 3177943.68 | 2550.7121 | -13446.5006 | 44157.7732 | -19095.4893 | 119298.407 | 248963.576 | 729443.693 | -7956.5145 | 18706.9068 | -3395.587 | 26411.9067 | 21182.8568 | 100795.577 | -3153.8409
131.52 | 6.8911 | 1.2787 |  | -17664.8155 | -100002.88 | 325801.534 | 2789984.51 | 364167.611 | -19732.6284 | 40138.918 | -10819.2188 | 125483.826 | 145696.278 | 715780.645 | -8761.9616 | 20106.3368 | -1455.6698 | 27825.4132 | 11786.2866 | 109232.126 | -3012.503
131.72 | 6.9506 | 1.2814 |  | 2038.0048 | -94588.9925 | 340357.158 | 2748168.57 | 670966.711 | -20309.6108 | 42124.5795 | -8762.2413 | 131322.871 | 129492.289 | 680297.049 | -9102.2993 | 18294.1352 | -1395.7209 | 29322.5396 | 13655.0688 | 105620.267 | -2969.4258
131.92 | 7.0532 | 1.2841 |  | 25899.8196 | -97516.3962 | 351377.672 | 3007384.98 | 1145500.2 | -18458.0497 | 52681.0646 | -7653.1507 | 134687.966 | 119258.262 | 681195.424 | -9354.4509 | 14067.7468 | -1285.8266 | 29673.5023 | 13445.1963 | 75214.7534 | -2280.3345
132.12 | 7.1213 | 1.2861 |  | 41486.9391 | -94363.1395 | 358026.76 | 3027876.56 | 1482637.25 | -24338.6373 | 55612.8281 | -4375.2819 | 137087.221 | 75124.8934 | 799936.321 | -11970.0945 | 18828.3159 | -102.4676 | 30496.6256 | 7267.3754 | 101691.473 | -3729.4863
132.32 | 7.1838 | 1.2885 |  | 67185.7623 | -76755.8372 | 359417.847 | 2826503.47 | 2009320.58 | -28615.2265 | 60159.944 | 897.2581 | 137431.859 | 43803.2718 | 936425.519 | -14146.6295 | 22190.1448 | 70.6981 | 30497.102 | 7696.0526 | 119154.89 | -4641.5582
132.52 | 7.2879 | 1.2912 |  | 92989.9771 | -55741.7867 | 358808.51 | 2476587.98 | 2690451.72 | -27563.4464 | 63594.8888 | 11002.2204 | 137522.861 | -38498.5313 | 1054087.01 | -12589.942 | 27273.1236 | 411.5071 | 30453.9665 | 8652.6066 | 148195.525 | -3862.4791
132.72 | 7.3876 | 1.2933 |  | 117075.823 | -48558.7339 | 357668.33 | 2426829.92 | 3333372.83 | -29837.8532 | 68068.3018 | 19241.4647 | 139425.391 | -168591.992 | 1160613.38 | -11841.4143 | 31423.0189 | 3568.277 | 31155.6056 | -4992.1552 | 179875.33 | -3458.5305
132.92 | 7.4741 | 1.2956 |  | 150478.787 | -59274.7325 | 355329.476 | 2833860.49 | 4043295.12 | -39417.0377 | 76634.0994 | 23488.9387 | 142099.143 | -193509.62 | 1217065.97 | -15896.9117 | 31771.1488 | 3232.305 | 32212.5599 | -1304.5111 | 179812.852 | -4177.3608
133.12 | 7.6091 | 1.2978 |  | 170066.613 | -62082.9289 | 347536.974 | 2960036.85 | 4389164.09 | -44846.5751 | 79245.8063 | 25211.2161 | 141464.171 | -210399.965 | 1217289.73 | -18951.5568 | 32250.0094 | 3363.6697 | 32103.3947 | -1467.6036 | 182910.13 | -5093.0633
133.32 | 7.7368 | 1.2997 |  | 177815.847 | -38798.4191 | 334213.126 | 2527176.45 | 4567433.43 | -35159.9981 | 79263.8512 | 29912.1833 | 139731.994 | -263776.936 | 1244868.72 | -13146.2427 | 32767.5607 | 4083.4947 | 31919.5384 | -4124.9808 | 183232.141 | -2734.6969
133.52 | 7.8324 | 1.3017 |  | 191042.321 | -38850.407 | 319954.932 | 2580537.6 | 4806947.84 | -36422.9997 | 81254.147 | 31409.4822 | 139023.911 | -292966.34 | 1231714.11 | -12514.4183 | 31725.9119 | 4851.6519 | 32158.8373 | -7713.0623 | 179155.438 | -2969.5627
133.72 | 7.9548 | 1.3035 |  | 208303.592 | -44965.2441 | 308560.464 | 2734099.02 | 5124972.39 | -38459.2949 | 83358.697 | 33579.3702 | 138445.598 | -292900.263 | 1222738.93 | -15756.8806 | 30634.8373 | 4178.9553 | 32271.304 | -3105.3105 | 172523.451 | -2789.3362
133.92 | 8.0757 | 1.3038 |  | 205204.226 | -23887.902 | 287259.57 | 2451544.15 | 5178548.66 | -33919.6785 | 86005.6575 | 35363.9161 | 133828.925 | -326104.198 | 1340901.03 | -13127.5978 | 34272.4209 | 5387.2221 | 31267.9679 | -11191.3638 | 190078.876 | -3440.7563
134.12 | 8.1751 | 1.3042 |  | 211079.354 | -23331.0019 | 268664.067 | 2526098.35 | 5354596.4 | -29001.9423 | 89268.372 | 36107.2324 | 132111.12 | -342702.662 | 1383372.46 | -14777.7041 | 34528.4305 | 6210.3704 | 31587.5217 | -15406.5457 | 193958.634 | -4412.5356
134.32 | 8.288 | 1.3053 |  | 215631.654 | -34396.2289 | 248425.009 | 2755883.86 | 5462888.37 | -36074.443 | 92341.808 | 35690.0798 | 129148.336 | -362845.756 | 1302665.71 | -17577.4063 | 29327.7231 | 7160.5027 | 30922.9308 | -20775.3863 | 164620.741 | -4478.4234
134.52 | 8.3848 | 1.3056 |  | 201748.106 | -22385.788 | 228897.619 | 2393918.07 | 5112841.43 | -29795.8167 | 84391.3074 | 34344.3099 | 127130.451 | -334667.226 | 1297815.8 | -12776.0172 | 33046.712 | 5946.5265 | 31148.275 | -15415.2393 | 186519.441 | -2939.863
134.72 | 8.5096 | 1.3061 |  | 193003.973 | -22641.987 | 211181.578 | 2428351.78 | 4923025.21 | -28214.734 | 81452.5584 | 32095.8434 | 123870.679 | -291118.623 | 1331669.89 | -12805.2767 | 37042.5224 | 4471.7518 | 30395.9283 | -5339.0881 | 220098.8 | -3913.0597
134.92 | 8.6172 | 1.3064 |  | 189420.278 | -50964.6071 | 195903.068 | 3096711.72 | 5013999.97 | -31888.2632 | 92639.0295 | 29164.7452 | 122456.702 | -286335.818 | 1358593.5 | -15280.1878 | 33078.9392 | 5334.9033 | 30237.6692 | -11240.4576 | 191159.625 | -3761.5014
135.12 | 8.723 | 1.3071 |  | 177525.744 | -73037.498 | 181375.708 | 3763005.9 | 4920306.18 | -33559.4623 | 103636.928 | 23270.6802 | 122102.86 | -243493.348 | 1459712.91 | -18385.3875 | 32939.16 | 5655.6125 | 30941.3006 | -16999.4083 | 173616.343 | -5074.4674
135.32 | 8.8323 | 1.308 |  | 149888.667 | -77208.3803 | 170392.152 | 3890314.95 | 4369994.19 | -29213.5875 | 99924.8364 | 16650.132 | 121517.261 | -125944.372 | 1602175.19 | -16606.3487 | 40997.8357 | 2677.7001 | 31471.1273 | -128.4273 | 230366.092 | -5368.5115
135.52 | 8.9796 | 1.3081 |  | 128424.566 | -81894.5891 | 166723.65 | 4092446.9 | 3860452.66 | -20221.4997 | 99070.162 | 7689.6542 | 121117.972 | 14595.4241 | 1687573.62 | -13476.6689 | 46976.9487 | -995.5894 | 31082.9627 | 19976.0243 | 275933.735 | -6332.7272
135.72 | 9.1296 | 1.307 |  | 120221.976 | -138414.557 | 170991.178 | 5381671.67 | 3877191.94 | -21847.535 | 110937.062 | 1393.9219 | 126284.474 | 44574.5392 | 1646690.61 | -12074.8659 | 42542.0948 | -953.7045 | 32313.7 | 16844.1011 | 235222.851 | -1646.8673
135.92 | 9.2753 | 1.305 |  | 95440.729 | -166948.369 | 179017.539 | 6160805.61 | 3473047.33 | -28336.3455 | 121486.518 | -9115.0234 | 131114.121 | 154225.891 | 1846544.23 | -17116.7648 | 45950.6243 | -1728.3599 | 33882.2944 | 16834.7096 | 247674.226 | -5736.7066
136.12 | 9.4235 | 1.3024 |  | 76543.3691 | -196330.263 | 184798.43 | 7025481.74 | 3235695.76 | -26436.7108 | 131174.422 | -17203.0476 | 135459.369 | 256700.029 | 1949919.02 | -15295.753 | 48357.086 | -4201.7168 | 35128.3418 | 29327.8356 | 261425.927 | -3964.4921
136.32 | 9.577 | 1.2998 |  | 51238.2041 | -219246.945 | 213020.162 | 7543121.87 | 2707718.25 | -33572.2371 | 132703.639 | -26841.5087 | 143995.452 | 401184.624 | 2132246.78 | -19899.9225 | 55520.2066 | -6734.8178 | 37228.1226 | 38760.6985 | 287676.085 | -6972.3125
136.52 | 9.7217 | 1.2966 |  | 24645.1423 | -239555.324 | 227666.958 | 8103228.94 | 2266184.97 | -37432.3156 | 139539.26 | -34776.5139 | 149298.966 | 457913.429 | 2126594.04 | -26916.7289 | 53191.649 | -6895.8406 | 37936.7713 | 45092.0943 | 300680.58 | -9666.6036
136.72 | 9.8507 | 1.2924 |  | 4496.2346 | -243664.631 | 268554.372 | 7708589.94 | 1658520.18 | -35368.5874 | 122417.113 | -36469.6933 | 161181.373 | 494841.111 | 1945490.21 | -17243.8684 | 53425.8752 | -8852.201 | 40131.6403 | 53876.9141 | 301252.937 | -5470.7035
136.92 | 9.9994 | 1.2881 |  | -21699.1107 | -240332.625 | 301194.263 | 7736689.23 | 1274919.08 | -19596.5797 | 122592.765 | -39466.0016 | 171021.681 | 530916.9 | 1978695.66 | -10631.5441 | 52802.912 | -9068.3032 | 41777.2477 | 53466.2918 | 294970.37 | -3485.5215
137.12 | 10.1256 | 1.2833 |  | -21547.1257 | -280554.419 | 342453.802 | 8820871.02 | 1368841.82 | -38049.5611 | 140847.289 | -47189.7785 | 187158.787 | 557809.429 | 2046387.09 | -24273.4066 | 47403.6959 | -6925.5843 | 46186.7336 | 40970.8827 | 255673.682 | -7289.5851
137.32 | 10.2505 | 1.279 |  | -10100.1107 | -301232.275 | 390475.2 | 9261088.42 | 1574001.92 | -51028.6146 | 145707.251 | -48257.526 | 199786.812 | 626466.335 | 2049350.77 | -26194.0833 | 46422.1044 | -9605.0591 | 48154.1549 | 56092.4026 | 249463.495 | -8015.3505
137.52 | 10.3925 | 1.2748 |  | -34826.1131 | -283896.513 | 428716.281 | 8786377.18 | 1057524.54 | -43038.8709 | 134737.565 | -48720.0152 | 209956.949 | 592897.193 | 2051965.04 | -23545.3615 | 52030.0141 | -8215.8192 | 50205.0075 | 49007.0787 | 290774.009 | -8051.1495
137.72 | 10.5317 | 1.2706 |  | -21796.2063 | -254143.759 | 472104.349 | 8077984.65 | 1166681.87 | -34363.5937 | 127532.179 | -44236.0007 | 221553.399 | 626565.792 | 2042991.9 | -18600.9475 | 51780.1791 | -10474.4523 | 52512.3129 | 62327.1653 | 284094.725 | -6527.5302
137.92 | 10.664 | 1.2663 |  | -10633.5584 | -268081.82 | 517680.231 | 8260991.18 | 1446914.3 | -40983.8001 | 130485.129 | -40922.5673 | 235869.258 | 509122.276 | 1939632.84 | -23534.6551 | 46187.276 | -6152.3475 | 54917.0495 | 38563.0016 | 248147.123 | -6589.3573
138.12 | 10.7936 | 1.2617 |  | 15703.7328 | -247110.706 | 552204.582 | 7664913.9 | 1912045.47 | -42806.7422 | 124871.764 | -31089.9917 | 246608.409 | 429498.425 | 1853132.82 | -24454.8553 | 45149.4798 | -5927.0382 | 57414.4617 | 42173.6625 | 252852.343 | -7826.0748
138.32 | 10.9067 | 1.2569 |  | 29546.5554 | -216583.673 | 587818.418 | 6843853.27 | 2108264.34 | -37174.1038 | 114254.714 | -22223.1648 | 256501.11 | 313029.121 | 1771517.33 | -20509.5435 | 46091.4586 | -3595.9612 | 58678.6039 | 33591.0381 | 270869.088 | -7286.4782
138.52 | 11.0078 | 1.2527 |  | 59323.4894 | -203524.468 | 618013.258 | 6521767.93 | 2581862.96 | -40085.831 | 111395.347 | -15342.1893 | 268767.681 | 252294.596 | 1722675.45 | -22230.2396 | 46651.32 | -3415.5444 | 62177.3829 | 34629.6437 | 273449.149 | -6138.9281
138.72 | 11.0846 | 1.2489 |  | 89237.3708 | -179721.241 | 629819.13 | 6094801.61 | 3085621.11 | -45538.1762 | 110689.26 | -8641.5882 | 271555.508 | 202093.502 | 1701904.49 | -30004.4959 | 46363.8056 | -2864.2223 | 61906.2501 | 33960.7811 | 277906.081 | -9131.1425
138.92 | 11.1637 | 1.2459 |  | 116170.078 | -172103.459 | 637503.044 | 5767244.74 | 3524503.68 | -44766.3651 | 105958.943 | -674.9797 | 275006.483 | 70293.6711 | 1561033.05 | -24935.6165 | 41596.705 | 164.2653 | 62776.1251 | 19571.7362 | 253284.446 | -7524.3621
139.12 | 11.2519 | 1.2427 |  | 159259.115 | -161468.889 | 633931.408 | 5645551.2 | 4468328.26 | -40052.8142 | 112833.065 | 9931.0245 | 276407.306 | -20392.4695 | 1615256.28 | -19935.7436 | 37720.4077 | 1599.6593 | 63143.1961 | 10695.5791 | 214292.475 | -4969.6883
139.32 | 11.3195 | 1.239 |  | 190345.296 | -146402.382 | 622205.77 | 5599075.89 | 5213776.89 | -41824.6758 | 123493.834 | 16532.3532 | 275847.739 | -133885.424 | 1763123.4 | -27603.6322 | 41464.8257 | 4849.7406 | 63784.2755 | -6928.9895 | 231801.023 | -8904.1917
139.52 | 11.4093 | 1.2352 |  | 220737.542 | -124547.54 | 606828.087 | 5291421.6 | 5907961.27 | -42146.473 | 127996.12 | 25224.3138 | 274485.179 | -182783.814 | 1869200.27 | -24368.348 | 46124.0068 | 3989.1169 | 63887.9704 | -872.187 | 251110.729 | -7356.8231
139.72 | 11.5051 | 1.2309 |  | 232267.068 | -105894.265 | 583460.607 | 5162452.07 | 6277055.16 | -35848.1009 | 131710.268 | 30237.0419 | 270605.753 | -230799.934 | 2052616.94 | -26423.6019 | 53126.3114 | 4625.9333 | 63630.2352 | -20.1512 | 295635.003 | -8426.3275
139.92 | 11.6054 | 1.2264 |  | 254776.663 | -115629.169 | 563004.45 | 5516522.32 | 6766570.94 | -36025.8071 | 143029.958 | 30652.9781 | 269797.105 | -255651.308 | 2035173.15 | -28668.0966 | 47047.8814 | 5986.1426 | 63789.6858 | -5601.3107 | 271926.198 | -8520.5187
140.12 | 11.6749 | 1.2227 |  | 256930.728 | -128085.407 | 534721.279 | 5730055.65 | 6725005.09 | -34957.3628 | 143238.896 | 28074.2776 | 266777.444 | -265871.529 | 1974868.78 | -28774.9879 | 44222.4007 | 7126.4741 | 63681.9086 | -14926.3007 | 247668.921 | -8009.2383
140.32 | 11.7215 | 1.2204 |  | 237574.378 | -95246.2 | 496615.556 | 4998395 | 6207759.24 | -33195.5047 | 132094.243 | 25977.2 | 258159.267 | -181956.009 | 1958279.6 | -29448.4882 | 47497.19 | 4042.4434 | 62459.0621 | 1351.5123 | 271647.108 | -9511.0474
140.52 | 11.7887 | 1.2183 |  | 217087.408 | -97241.6679 | 465312.529 | 4627693.95 | 5718785.03 | -36726.1808 | 112837.458 | 27557.5257 | 249513.253 | -183664.221 | 1836770.07 | -23242.1838 | 50719.834 | 2934.9345 | 59712.4042 | 9824.2117 | 305600.492 | -6528.1908
140.72 | 11.8208 | 1.2158 |  | 195508.427 | -93418.9596 | 438076.12 | 4526411.73 | 5399352.65 | -40360.6549 | 113148.095 | 25115.0068 | 244759.45 | -166308.841 | 1867570.23 | -26770.4844 | 50231.4965 | 3428.2084 | 59746.1715 | 2606.0165 | 289476.608 | -8049.3083
140.92 | 11.8557 | 1.2137 |  | 177802.207 | -122941.282 | 421563.455 | 5122264.12 | 5092121.31 | -41793.0215 | 118431.202 | 18088.1919 | 244183.04 | -138860.302 | 1821356.92 | -27477.9221 | 47533.3604 | 4017.5812 | 59802.1095 | -1418.8391 | 279025.337 | -8020.6295
141.12 | 11.8858 | 1.2117 |  | 152400.227 | -157874.047 | 411267.335 | 6056104.6 | 4644607.06 | -38574.9597 | 127935.634 | 6303.0574 | 245741.27 | -16984.6499 | 1860555.7 | -25918.6977 | 44770.5109 | 2519.4368 | 60835.3494 | 3120.9638 | 250473.034 | -9056.7153
141.32 | 11.9461 | 1.209 |  | 126123.932 | -213127.332 | 406558.53 | 7507712.96 | 4177841.95 | -38540.0426 | 144105.507 | -10430.4032 | 247691.047 | 160285.879 | 1981355.23 | -24835.3083 | 42499.6673 | 23.8386 | 61840.1513 | 15407.6972 | 242991.442 | -6995.775
141.52 | 12.0114 | 1.2056 |  | 95788.8404 | -257260.765 | 408643.558 | 8649362.4 | 3660407.91 | -52764.9072 | 153705.181 | -23177.8331 | 247274.686 | 330117.984 | 2148727.04 | -36868.1651 | 48317.0987 | -3369.0623 | 61540.5478 | 30130.38 | 265074.826 | -12672.7233
141.72 | 12.0532 | 1.2019 |  | 61883.3749 | -278506.701 | 415240.261 | 9300243.32 | 3085378.99 | -52219.2262 | 157891.524 | -33758.9796 | 248471.446 | 458871.186 | 2294961.12 | -34427.6498 | 54810.3127 | -5704.5008 | 62231.588 | 38920.8435 | 294515.137 | -10233.8469
141.92 | 12.0755 | 1.1994 |  | 29029.2949 | -290689.818 | 435855.524 | 9524503.53 | 2432940.64 | -53996.907 | 156292.74 | -42040.6856 | 251349.474 | 565438.223 | 2376803.52 | -32526.6168 | 60293.3434 | -8042.3004 | 61950.977 | 53429.018 | 343957.737 | -10870.5026
142.12 | 12.1099 | 1.1982 |  | 8353.8104 | -312341.121 | 466954.448 | 10030342.8 | 2036760.95 | -55177.8429 | 162897.092 | -51226.6431 | 259184.615 | 660516.99 | 2433171.24 | -32420.7593 | 59738.8486 | -9183.3349 | 63418.4406 | 60456.6782 | 350285.777 | -10797.9761
142.32 | 12.1335 | 1.197 |  | -363.6332 | -344240.174 | 506535.428 | 10719599.2 | 1933678.37 | -68775.9699 | 167485.43 | -54543.9044 | 269860.558 | 694267.304 | 2421492.25 | -39892.5474 | 61277.5628 | -10366.2219 | 65147.7624 | 67643.3376 | 361759.96 | -10916.4193
142.52 | 12.1386 | 1.1961 |  | -20550.0994 | -333626.506 | 537705.468 | 10607492.4 | 1512132.06 | -65406.8925 | 169985.413 | -60417.9116 | 276479.413 | 767139.736 | 2514192.4 | -39693.9189 | 60233.3409 | -10492.7063 | 66595.9252 | 65703.3583 | 345360.482 | -12340.7286
142.72 | 12.1601 | 1.1956 |  | -23167.774 | -324860.179 | 582005.033 | 10226360.2 | 1310480.28 | -67355.9379 | 158460.616 | -59607.2828 | 285306.357 | 831985.567 | 2494025.43 | -35326.4517 | 64271.3339 | -13872.5408 | 68271.6336 | 83183.1221 | 366054.204 | -10358.6288
142.92 | 12.2011 | 1.1942 |  | -27557.1216 | -290863.726 | 620961.338 | 9396536.67 | 1124119.46 | -59433.2909 | 146541.696 | -55209.8106 | 291114.673 | 781881.744 | 2434924.57 | -35106.1591 | 65568.5499 | -12946.2685 | 68524.5418 | 79875.4152 | 370993.56 | -10817.139
143.12 | 12.2372 | 1.1921 |  | -2223.5826 | -289810.613 | 657483.653 | 9101945.82 | 1622368.3 | -53229.2907 | 136854.724 | -43832.1271 | 300733.585 | 634857.529 | 2234614.1 | -27355.7071 | 62045.5614 | -10887.0496 | 69742.7385 | 71310.782 | 358081.338 | -6617.353
143.32 | 12.2866 | 1.1899 |  | 39034.7971 | -311207.367 | 699785.735 | 9411984.32 | 2484013.97 | -62732.3438 | 139348.549 | -33399.6404 | 314248.74 | 444671.169 | 2092798.69 | -33108.5299 | 55382.8381 | -5311.0411 | 72025.0518 | 45923.045 | 336342.348 | -9407.9022
143.52 | 12.3186 | 1.1872 |  | 64785.6773 | -266791.105 | 720776.004 | 8554901.87 | 3029824.43 | -54070.91 | 143096.316 | -24146.6424 | 322178.483 | 375670.424 | 2132089.38 | -31490.6812 | 52548.5272 | -4481.5476 | 74950.5171 | 40003.8651 | 295711.321 | -9234.2064
143.72 | 12.3485 | 1.1773 |  | 78764.9517 | -219060.575 | 742473.597 | 7501538.9 | 3090385.87 | -42702.7715 | 134181.26 | -19669.7318 | 327175.213 | 338746.333 | 2149577.73 | -29593.2884 | 56900.5616 | -4170.4069 | 75568.6683 | 39262.9897 | 329292.013 | -8922.8967
143.92 | 12.3659 | 1.1729 |  | 117004.211 | -199070.266 | 741558.886 | 7051973.16 | 3758120.73 | -49401.1182 | 132461.57 | -10156.0229 | 326179.742 | 269872.127 | 2072797.44 | -32955.1253 | 54933.2948 | -4385.094 | 75189.2507 | 45954.2626 | 324010.245 | -9594.0947
144.12 | 12.381 | 1.1727 |  | 154012.054 | -181094.139 | 734836.526 | 6769519.12 | 4445784.5 | -38127.7526 | 135670.482 | -3455.5343 | 324069.829 | 155981.566 | 2069232.85 | -23586.3901 | 54074.3615 | -1453.1681 | 74306.9394 | 27108.4784 | 311489.224 | -7258.7026
144.32 | 12.3942 | 1.1728 |  | 206553.148 | -193971.148 | 718722.645 | 7076619.9 | 5656035.74 | -51464.5862 | 146171.648 | 10099.0522 | 322501.497 | -10234.664 | 2037379.43 | -33263.6728 | 46065.0044 | 1970.829 | 74714.6267 | 14865.7419 | 270938.197 | -8021.5026
144.52 | 12.4132 | 1.1728 |  | 223749.786 | -174926.993 | 696767.981 | 6824511.48 | 6129699.95 | -43012.9967 | 152310.748 | 16702.4899 | 318620.835 | -134092.406 | 2129229.43 | -30242.8934 | 48382.3606 | 5394.0639 | 73855.6285 | -4164.3629 | 275142.568 | -9929.7347
144.72 | 12.454 | 1.1728 |  | 252674.977 | -166700.2 | 663432.138 | 6814264.38 | 6731508.2 | -45218.6497 | 156670.245 | 21848.1624 | 314860.716 | -160576.884 | 2157715.21 | -34405.4219 | 50565.8031 | 4483.8862 | 74581.3272 | 1447.5413 | 286800.765 | -10364.1701
144.92 | 12.4764 | 1.1728 |  | 251920.553 | -138000.514 | 630883.229 | 6317403.14 | 6629224.52 | -28870.4626 | 153341.444 | 21067.1262 | 306744.935 | -143497.056 | 2226062.89 | -26456.2481 | 54013.9225 | 4324.2147 | 72748.8533 | -1486.8 | 293823.463 | -8407.5984
145.12 | 12.5005 | 1.1728 |  | 250707.574 | -136980.819 | 590399.565 | 6285833.25 | 6613744.82 | -34511.4746 | 147722.932 | 21969.7244 | 297254.804 | -98951.2096 | 2300529.73 | -29637.1895 | 61389.0756 | 1653.4793 | 71489.2219 | 14057.4657 | 349837.577 | -8710.4005
145.32 | 12.5355 | 1.1993 |  | 244252.418 | -130633.256 | 549017.721 | 6259543.13 | 6588747.02 | -28616.0786 | 151276.58 | 21482.1994 | 285518.998 | -70069.4766 | 2408306.21 | -28716.8153 | 64559.3116 | 436.8676 | 68268.6318 | 23600.8415 | 373828.255 | -8206.7484
145.52 | 12.5407 | 1.5044 |  | 232081.695 | -155005.302 | 512714.534 | 6904047.89 | 6561390.89 | -33219.2032 | 160731.118 | 18127.0998 | 279597.218 | -89696.8854 | 2474306.2 | -31696.9921 | 63805.4307 | 2420.0478 | 68307.599 | 7011.9167 | 350253.552 | -8138.2292
145.72 | 12.5535 | 1.9615 |  | 212580.669 | -173853.874 | 486428.435 | 7177750.22 | 6191266.97 | -36569.7893 | 159137.633 | 12998.0274 | 274932.242 | -2603.977 | 2488488.12 | -33322.9599 | 65973.4814 | 4.0286 | 67578.9881 | 21861.2931 | 382562.52 | -9173.6682
145.92 | 12.5652 | 2.4119 |  | 170043.622 | -178773.183 | 468392.944 | 7424937.51 | 5305812.19 | -25924.902 | 160226.349 | -20.9111 | 272298.733 | 133548.995 | 2559661 | -28163.5285 | 67656.8706 | -1913.896 | 67675.1499 | 29283.7479 | 384614.276 | -7742.8453
146.12 | 12.6116 | 2.8033 |  | 151774.492 | -232691.905 | 462459.46 | 8702223.49 | 4948174.65 | -33630.2363 | 171071.964 | -13906.6186 | 272360.583 | 312965.023 | 2626177.58 | -26215.6165 | 67197.0417 | -5779.5813 | 67614.6913 | 45110.2001 | 373594.419 | -5668.7278
146.32 | 12.6369 | 3.1797 |  | 123374.181 | -294530.123 | 455186.626 | 10093159.6 | 4524393.46 | -59380.8119 | 176314.453 | -23504.3366 | 270223.718 | 371433.011 | 2688102.49 | -40595.843 | 71595.9989 | -5591.4132 | 67309.5356 | 45794.2566 | 412637.963 | -11083.582
146.52 | 12.6314 | 3.5455 |  | 74255.4934 | -303739.768 | 460418.58 | 10289743.5 | 3551390.78 | -54923.022 | 178763.717 | -36307.711 | 270509.351 | 488741.181 | 2684964.04 | -40412.6543 | 68951.4149 | -6538.2422 | 66818.8676 | 49793.8211 | 391542.495 | -14896.2116
146.72 | 12.6732 | 3.9019 |  | 59633.8247 | -358438.022 | 484267.647 | 11183808.1 | 2997434.36 | -62407.0342 | 175956.893 | -48673.816 | 281534.348 | 587226.725 | 2358344.96 | -29899.9259 | 54467.4873 | -7476.4627 | 69220.4115 | 54410.7088 | 337166.749 | -7007.7088
146.92 | 12.6871 | 4.3697 |  | 18488.7603 | -347644.871 | 514365.109 | 10846083.5 | 2215161.22 | -55955.4185 | 166704.222 | -52208.3749 | 284507.939 | 689081.425 | 2511410.05 | -28227.6393 | 65236.6255 | -10867.7734 | 69568.3931 | 64236.7996 | 357148.427 | -7779.5489
147.12 | 12.6569 | 4.8395 |  | 558.5699 | -367351.97 | 545654.557 | 11283990.3 | 1981818.99 | -78560.4138 | 172302.232 | -56632.7992 | 291529.391 | 704858.394 | 2552344.92 | -44935.8563 | 63534.8678 | -8984.6252 | 71031.3053 | 55236.4121 | 351950.738 | -15011.7425
147.32 | 12.6552 | 5.2331 |  | 14852.3473 | -392129.364 | 594519.419 | 11367676.1 | 2023282.03 | -90387.108 | 161133.046 | -55121.0126 | 304727.269 | 724125.589 | 2240039.44 | -45192.8045 | 56405.2812 | -11151.1941 | 73108.993 | 69714.6276 | 317451.845 | -11623.2897
147.52 | 12.6374 | 5.5929 |  | -31066.3748 | -324390.887 | 629580.849 | 9702020.61 | 1000029.19 | -60876.4356 | 141105.788 | -54561.6127 | 308265.444 | 692886.14 | 2180517.85 | -34689.0336 | 57244.6992 | -9562.2558 | 72808.8557 | 61309.6098 | 325225.232 | -11871.4944
147.72 | 12.632 | 5.8546 |  | -27179.4226 | -282551.085 | 668707.424 | 8378242.1 | 756286.636 | -60001.9458 | 119410.87 | -48889.1626 | 317218.64 | 666201.457 | 1882548.23 | -35290.0463 | 51098.2796 | -10081.252 | 74507.5883 | 67020.7036 | 308655.078 | -11694.3842
147.92 | 12.6064 | 6.0423 |  | -24326.8419 | -240764.383 | 708315.487 | 7052415.4 | 613919.149 | -50577.9598 | 96257.6337 | -39188.6671 | 323282.607 | 535882.148 | 1569870.85 | -29508.7902 | 44561.6011 | -7331.6337 | 73947.9357 | 52732.6871 | 272772.094 | -10923.5135
148.12 | 12.5643 | 6.1287 |  | -2371.7621 | -206688.558 | 736337.936 | 5955175.68 | 878266.332 | -49235.3111 | 82211.9682 | -28115.581 | 331926.399 | 386024.9 | 1252928.04 | -26210.6801 | 35069.7842 | -4613.3781 | 76875.7708 | 39069.9129 | 210423.714 | -6624.2456
148.32 | 12.5326 | 6.1233 |  | 14029.2973 | -142119.591 | 754704.466 | 4606981.78 | 1162714.96 | -39257.6059 | 78725.0539 | -18051.9262 | 334287.586 | 299504.587 | 1283138.83 | -27388.037 | 35138.214 | -3342.3066 | 76370.2935 | 34006.4518 | 211165.222 | -8963.2304
148.52 | 12.4694 | 6.0735 |  | 43261.9249 | -120602.281 | 764583.785 | 4085245.89 | 1691171.73 | -58517.2782 | 74384.3492 | -8377.0037 | 337007.916 | 163976.317 | 1237265.68 | -36941.1002 | 32981.3469 | 59.8989 | 77272.719 | 16370.1942 | 191350.593 | -11699.3191
148.72 | 12.4044 | 5.9383 |  | 87618.9172 | -112880.599 | 761758.92 | 3942526.12 | 2520997.22 | -59438.266 | 78581.821 | 295.5689 | 335923.862 | 94262.0255 | 1114397.02 | -34347.7718 | 25145.069 | 238.8427 | 76752.332 | 17683.7597 | 144179.013 | -10488.9782
148.92 | 12.3442 | 5.7884 |  | 118833.938 | -90588.1511 | 743228.169 | 3665902.47 | 3079051.75 | -57000.6732 | 80564.5659 | 5997.8652 | 330074.679 | 11478.9794 | 1092967.72 | -34982.1018 | 23892.3659 | 2081.7883 | 75963.3157 | 7211.7032 | 132491.408 | -11097.4788
149.12 | 12.265 | 5.685 |  | 141027.748 | -71921.1613 | 721814.506 | 3214241.16 | 3527888.86 | -52781.7902 | 78763.5846 | 14121.71 | 322677.49 | -80613.9835 | 1108444.2 | -32663.5895 | 25055.53 | 3585.7881 | 73829.5403 | 1675.5965 | 149182.62 | -11101.4768
149.32 | 12.1876 | 5.5511 |  | 171690.447 | -52439.7458 | 679909.917 | 3023328.8 | 4209523.92 | -59419.2634 | 88322.9478 | 20520.9382 | 311275.715 | -148281.864 | 1141614.93 | -39527.8149 | 22473.4624 | 4443.7996 | 72107.7038 | -2513.987 | 127635.676 | -13254.0492
149.52 | 12.1436 | 5.3651 |  | 196282.609 | -50152.5216 | 650223.565 | 2717382.96 | 4656773.88 | -61328.7083 | 80786.4203 | 28689.8843 | 302772.254 | -253036.594 | 1020016.28 | -33219.1616 | 22054.3016 | 6228.2235 | 70196.1436 | -10700.6719 | 123774.881 | -8846.8299
149.72 | 12.0493 | 5.1715 |  | 171622.65 | 11245.2604 | 594152.76 | 1586075.96 | 4291619.37 | -46220.9315 | 72983.0944 | 32866.3983 | 289155.865 | -281014.878 | 1293616.83 | -26301.4133 | 33821.3194 | 6827.4221 | 68485.7478 | -15728.9456 | 174535.787 | -10256.1414
149.92 | 11.9777 | 4.8556 |  | 196832.48 | -22225.8777 | 560782.82 | 2171293.31 | 4665355.09 | -64194.7971 | 70032.6874 | 32474.6611 | 281040.088 | -255953.09 | 1177036.34 | -32666.6455 | 34076.1932 | 5248.1634 | 66718.3494 | -5519.0628 | 204995.315 | -10550.839
150.12 | 11.9279 | 4.4709 |  | 189881.494 | -31957.4619 | 512577.429 | 2539387.16 | 4694764.76 | -58518.5385 | 80586.7814 | 30719.3556 | 267443.298 | -249772.613 | 1220100.74 | -36184.899 | 31092.347 | 5284.616 | 63647.8955 | -6181.6235 | 175477.651 | -9677.6036
150.32 | 11.8514 | 4.0945 |  | 168400.462 | -45081.1783 | 467470.756 | 2853289.75 | 4351965.64 | -50867.303 | 81998.1125 | 25038.2231 | 256982.187 | -208653.244 | 1340113.82 | -27846.2541 | 36227.729 | 5216.4126 | 62508.6366 | -9462.9515 | 203828.954 | -9134.3288
150.52 | 11.7825 | 3.7067 |  | 161871.467 | -79034.5238 | 437075.666 | 3873651.13 | 4292907.64 | -44973.69 | 96979.654 | 14957.391 | 249302.845 | -81642.1588 | 1455468.38 | -28083.1989 | 36951.2892 | 2589.7807 | 60999.451 | 4054.4284 | 214982.698 | -9251.8358
150.72 | 11.7314 | 3.4106 |  | 145378.115 | -139920.346 | 409162.394 | 5403200.35 | 4149092.63 | -51791.7339 | 117615.421 | 2922.4338 | 242242.119 | 17298.9465 | 1606162.67 | -33527.0907 | 35343.8858 | 2080.6971 | 59632.1485 | 3391.681 | 188420.066 | -9344.6188
150.92 | 11.6727 | 3.143 |  | 109747.612 | -151470.626 | 382061.395 | 6096815.53 | 3673813.32 | -36391.7949 | 131937.699 | -8688.8921 | 233423.052 | 196433.386 | 1931060.29 | -29482.7404 | 43301.6741 | -1563.9623 | 58661.6573 | 18473.0305 | 212849.996 | -9983.4112
151.12 | 11.6307 | 2.8201 |  | 84796.4754 | -201734.877 | 373121.389 | 7380243.97 | 3233824.97 | -45961.7096 | 138124.901 | -21831.3654 | 229505.423 | 345330.819 | 2123549.74 | -31865.5967 | 53602.1543 | -4630.6852 | 58207.9005 | 32143.903 | 281921.214 | -10740.378
151.32 | 11.5866 | 2.5028 |  | 65150.6361 | -246498.774 | 367670.581 | 8583895.72 | 2928698.46 | -50028.0283 | 147797.402 | -32953.5685 | 225347.57 | 483335.667 | 2246094.36 | -34391.8539 | 58925.9858 | -7958.9861 | 56435.6916 | 52787.6486 | 333107.217 | -10940.147
151.52 | 11.5507 | 2.2128 |  | 36436.9572 | -279053.074 | 372282.793 | 9509940.29 | 2455675.19 | -53622.3377 | 163737.75 | -46875.7335 | 224621.125 | 581585.58 | 2328917.77 | -35676.7692 | 56010.0527 | -7623.2246 | 55992.0016 | 47487.2049 | 309488.613 | -12124.5481
151.72 | 11.5092 | 1.9875 |  | 19061.123 | -320595.889 | 394084.058 | 10163334.8 | 2086638.45 | -60824.3454 | 158939.264 | -52030.9433 | 230163.612 | 665060.286 | 2258177.53 | -30139.4215 | 55048.1599 | -10229.0172 | 56920.1055 | 62049.1323 | 309846.846 | -8543.0001
151.92 | 11.4639 | 1.781 |  | -19976.2994 | -313331.155 | 411425.523 | 10170861 | 1294964.93 | -52935.2831 | 157784.674 | -61763.3394 | 231163.146 | 779327.151 | 2395090.42 | -28486.5214 | 61474.3723 | -11978.4495 | 57168.317 | 64472.7504 | 330780.217 | -9484.4315
152.12 | 11.4383 | 1.5938 |  | -22938.9995 | -348311.411 | 443423.372 | 10899169.7 | 1248302.47 | -66514.2727 | 165025.245 | -66678.0161 | 238585.268 | 838472.253 | 2362828.59 | -32353.9461 | 55817.2372 | -12615.3384 | 58280.297 | 70886.9084 | 306547.837 | -9125.1237
152.32 | 11.4024 | 1.4541 |  | -29784.1377 | -346769.762 | 473805.042 | 10799504.8 | 1105485.8 | -59961.2055 | 161441.677 | -66620.4518 | 242729.455 | 838712.878 | 2347821.51 | -32533.6724 | 57832.6525 | -12941.0524 | 58412.1421 | 73755.8871 | 321828.373 | -9916.704
152.52 | 11.3477 | 1.3013 |  | -47941.4001 | -309112.66 | 507238.608 | 9961214.12 | 735591.322 | -50427.355 | 154854.579 | -65520.0232 | 247959.323 | 834682.071 | 2398636.14 | -30463.0503 | 60071.1683 | -12339.1697 | 59289.8916 | 72016.8252 | 342184.16 | -10100.5124
152.72 | 11.3203 | 1.1864 |  | -30836.3206 | -289249.194 | 539667.952 | 9331085.35 | 948276.09 | -57503.1256 | 142763.961 | -57783.1484 | 253644.232 | 825234.577 | 2294950.39 | -33259.7658 | 61942.3812 | -15145.1461 | 59934.1742 | 91823.6682 | 359076.196 | -9483.0243
152.92 | 11.2907 | 1.1695 |  | -37747.8576 | -256009.607 | 573138.053 | 8329326.64 | 759767.626 | -48377.9601 | 125553.851 | -49820.5119 | 258976.927 | 692358.991 | 2178166.45 | -30953.5509 | 61592.4517 | -11395.9688 | 59939.7703 | 72995.3317 | 363099.558 | -9755.405
153.12 | 11.2323 | 1.1718 |  | -18137.3558 | -217585.958 | 598526.224 | 7224019.55 | 909864.379 | -34479.1967 | 111569.076 | -41560.4338 | 266259.686 | 626356.659 | 1975012.41 | -23414.0677 | 57345.2541 | -11485.374 | 62089.8853 | 73929.4431 | 331916.023 | -6365.3729
153.32 | 11.2264 | 1.1728 |  | 1171.3369 | -175503.011 | 623199.137 | 6271014.82 | 1227500.11 | -29575.338 | 106682.276 | -33126.8333 | 269084.336 | 554605.633 | 1941070.24 | -24898.4593 | 56477.081 | -10621.5969 | 61548.5228 | 68901.221 | 317146.716 | -6754.2386
153.52 | 11.1939 | 1.1729 |  | 28261.279 | -153936.737 | 630667.338 | 5762351.23 | 1836712.81 | -43614.7202 | 108795.231 | -22397.6868 | 270292.777 | 376168.448 | 1923322.29 | -27977.664 | 53969.3056 | -5628.9769 | 61766.895 | 44494.4545 | 318105.693 | -7699.9383
153.72 | 11.1469 | 1.1728 |  | 78090.1107 | -153513.63 | 638498.876 | 5579785.83 | 2799813.28 | -55640.1754 | 110037.906 | -9741.0768 | 274127.82 | 220773.783 | 1756655.28 | -35962.3384 | 45469.0153 | -2629.6195 | 62819.9636 | 32526.1423 | 265175.528 | -9225.2246
153.92 | 11.1225 | 1.1728 |  | 95687.4426 | -97195.1327 | 636132.901 | 4274928.44 | 2960521.7 | -33686.2798 | 95489.1589 | -760.6519 | 273282.542 | 140345.733 | 1623098.3 | -25640.2846 | 45378.7557 | -2114.7214 | 62575.2375 | 29265.1927 | 269730.06 | -7538.5029
154.12 | 11.1118 | 1.1728 |  | 122239.175 | -83255.0819 | 621316.917 | 3674528.52 | 3344722.61 | -44235.0076 | 81130.4403 | 9089.2586 | 268710.413 | 17961.4539 | 1513554.06 | -19071.1364 | 44636.5897 | 183.8309 | 61319.8638 | 18441.7037 | 264777.414 | -6303.8605
154.32 | 11.0668 | 1.1728 |  | 155254.529 | -66663.4485 | 603447.667 | 3522886.91 | 4058309.1 | -46302.035 | 92309.9521 | 15498.0577 | 265612.134 | -74956.829 | 1446654.44 | -27101.6082 | 36167.9253 | 2611.0291 | 61075.3027 | 6409.0131 | 219118.588 | -8386.7127
154.52 | 11.0445 | 1.1728 |  | 183502.421 | -65371.4036 | 576002.615 | 3575763.8 | 4744799.5 | -43089.5493 | 103041.582 | 21882.1178 | 259130.561 | -172999.617 | 1457588.61 | -25495.4089 | 31842.5402 | 4858.2728 | 59718.8011 | -6510.2339 | 170708.799 | -6491.8179
154.72 | 11.0195 | 1.1728 |  | 198180.629 | -52292.1198 | 544294.452 | 3440227.99 | 5061360.14 | -39335.691 | 106910.425 | 24525.5647 | 252824.704 | -214386.118 | 1555928.82 | -25277.5481 | 34357.4735 | 6214.4888 | 59371.1095 | -14203.9001 | 189519.252 | -8305.234
154.92 | 10.9993 | 1.1728 |  | 212079.374 | -49831.2049 | 509491.192 | 3450088.38 | 5390961.7 | -42516.9709 | 110280.374 | 27993.3894 | 244106.047 | -212305.363 | 1596259.45 | -27328.173 | 33811.2975 | 5153.9211 | 57391.4432 | -7223.4611 | 181918.655 | -8441.7242
155.12 | 10.9732 | 1.1728 |  | 208133.838 | -54240.1242 | 471555.12 | 3514579.86 | 5277182.99 | -44262.2435 | 106744.6 | 26596.2683 | 235407.829 | -230822.578 | 1566453.74 | -26944.1448 | 35545.334 | 6064.7649 | 56151.2569 | -13766.4679 | 195050.596 | -8206.271
155.32 | 10.9263 | 1.1728 |  | 200423.036 | -46739.8948 | 431225.503 | 3321496.77 | 5045659.92 | -41070.1759 | 100242.128 | 25039.0887 | 224969.141 | -177995.238 | 1556539.96 | -24648.2746 | 38758.6685 | 3782.4408 | 54309.47 | -1581.2696 | 215548.48 | -7517.4993
155.52 | 10.9019 | 1.1728 |  | 188627.92 | -55635.0128 | 395272.698 | 3561353.41 | 4869822.76 | -35235.4345 | 102554.972 | 21294.5026 | 214613.171 | -152751.788 | 1568380.27 | -21770.924 | 39741.8524 | 3325.4665 | 51764.4159 | 1962.5579 | 231239.393 | -6884.1621
155.72 | 10.8662 | 1.1728 |  | 181883.678 | -79813.7955 | 362910.937 | 4160332.75 | 4893468.06 | -36329.9442 | 110350.484 | 18137.6557 | 207448.084 | -130168.094 | 1624042.91 | -24812.8197 | 38379.8742 | 3589.9453 | 50746.4932 | -1322.9688 | 218959.304 | -7246.5522
155.92 | 10.814 | 1.1728 |  | 154350.308 | -94836.7738 | 334203.738 | 4515135.87 | 4393560.31 | -43887.6754 | 111046.568 | 11239.9196 | 200387.493 | -54918.5452 | 1707922.17 | -28719.2274 | 41264.515 | 2619.1238 | 49728.3898 | 1154.5296 | 233093.256 | -9259.7143
156.12 | 10.7939 | 1.1728 |  | 128209.42 | -102206.845 | 317176.481 | 4656078.01 | 3798267.26 | -30592.6014 | 106359.852 | 3138.1027 | 195966.893 | 82270.7374 | 1693725.41 | -21473.9945 | 45534.2171 | -1886.3031 | 49058.2647 | 25533.5624 | 262476.344 | -5868.3788
156.32 | 10.777 | 1.1728 |  | 85173.1227 | -124126.031 | 300999.864 | 5354116.52 | 3073988.37 | -23637.8057 | 113339.881 | -9340.4885 | 190263.997 | 177838.025 | 1846774.78 | -20418.9011 | 50426.8477 | -2235.258 | 47364.9433 | 22840.0332 | 285302.074 | -7007.5593
156.52 | 10.7404 | 1.1728 |  | 76335.8243 | -179765.919 | 294843.488 | 6766135.43 | 3054046.99 | -33477.4064 | 132488.933 | -20153.672 | 190551.312 | 320243.945 | 1988483.24 | -24412.5719 | 47735.7952 | -4580.2296 | 48530.1367 | 32232.5982 | 256071.985 | -7602.8793
156.72 | 10.7086 | 1.1728 |  | 43670.7264 | -208910.003 | 295195.76 | 7730883.84 | 2502461.25 | -33647.2811 | 145629.573 | -34323.8311 | 188830.17 | 470101.492 | 2172882.66 | -27647.4247 | 52316.0473 | -6828.0075 | 47939.3197 | 41298.1885 | 274387.647 | -8822.9535
156.92 | 10.6991 | 1.1728 |  | 16831.6111 | -230102.292 | 303798.64 | 8188303.11 | 1928467.09 | -37702.1535 | 144334.818 | -43610.3909 | 188859.314 | 601282.636 | 2220190.72 | -28287.0642 | 56082.1789 | -9894.5426 | 47847.9113 | 56460.4998 | 304549.327 | -9169.0461
157.12 | 10.645 | 1.1728 |  | -11736.0587 | -238291.185 | 318076.523 | 8280396.42 | 1285862.73 | -40809.8924 | 141205.707 | -51157.5368 | 189788.26 | 699309.196 | 2247978.17 | -26782.288 | 58115.7287 | -11689.177 | 47283.2729 | 67557.4971 | 329060.612 | -8382.2588
157.32 | 10.6025 | 1.1728 |  | -34957.1986 | -258545.593 | 337141.752 | 8643189.24 | 798228.884 | -43019.122 | 139705.324 | -58437.4261 | 193413.96 | 747596.098 | 2170029 | -26747.3217 | 55890.1583 | -11809.0028 | 47867.0249 | 69235.5873 | 318679.936 | -9546.9832
157.52 | 10.5439 | 1.1728 |  | -40537.6292 | -286116.245 | 370763.919 | 8892425.07 | 564092.065 | -48338.7541 | 131739.167 | -59916.0239 | 201367.273 | 769922.567 | 1981019.12 | -24592.3619 | 50411.3848 | -12593.0286 | 48996.2067 | 72198.1678 | 291459.272 | -7373.9658
157.72 | 10.4772 | 1.1728 |  | -64324.9668 | -273381.421 | 391419.253 | 8518846.19 | 53664.8016 | -40096.3296 | 121965.453 | -61002.1089 | 203661.933 | 779968.049 | 1926219.44 | -21591.672 | 50881.9815 | -12716.7618 | 49158.1782 | 71243.4654 | 288373.531 | -6972.4383
157.92 | 10.4366 | 1.1728 |  | -56531.1883 | -277790.026 | 425066.565 | 8495900.61 | 147132.561 | -36994.4823 | 118102.988 | -59408.2604 | 210509.704 | 784593.144 | 1859066.2 | -17177.0911 | 50508.6466 | -13850.9234 | 50103.6081 | 78969.6743 | 295533.708 | -4672.4845
158.12 | 10.3807 | 1.1728 |  | -55785.9256 | -287315.305 | 456279.041 | 8803331.89 | 252542.097 | -39952.2002 | 126090.779 | -60365.4268 | 216700.534 | 732076.88 | 1904981.13 | -23786.9238 | 48983.5493 | -10657.9721 | 50708.8201 | 61289.3608 | 282246.379 | -8286.8369
158.32 | 10.3219 | 1.1728 |  | -35579.9727 | -282162.39 | 484013.247 | 8779524.43 | 653450.963 | -37802.2001 | 133662.625 | -58507.7869 | 223555.39 | 736596.894 | 1925639.11 | -19165.729 | 46699.7563 | -11721.695 | 52628.7738 | 67972.944 | 262946.043 | -5267.859
158.52 | 10.3236 | 1.1728 |  | -23241.7805 | -266846.85 | 505747.724 | 8591542.95 | 952115.402 | -37437.3724 | 132011.566 | -52883.5899 | 224924.411 | 708464.831 | 2054460.95 | -20967.6533 | 53035.8538 | -11850.0291 | 52398.1511 | 68593.8135 | 291823.414 | -7156.6241
158.72 | 10.3168 | 1.1728 |  | 684.1998 | -251050.38 | 528338.518 | 8169108.82 | 1466857.66 | -41984.9208 | 127792.044 | -42444.574 | 229423.769 | 608538.027 | 2080417.32 | -26979.1058 | 56622.5148 | -10638.694 | 53271.4413 | 64176.5643 | 310125.477 | -7937.5514
158.92 | 10.2754 | 1.1728 |  | 18392.706 | -199454.704 | 543109.937 | 7037586.83 | 1737267.99 | -32498.3177 | 122534.573 | -33380.0362 | 231436.911 | 542124.625 | 2096372.69 | -25353.8957 | 57147.7425 | -10251.2862 | 53474.9629 | 65944.9005 | 314369.366 | -7635.9642
159.12 | 10.2636 | 1.1728 |  | 41436.2882 | -174889.251 | 558246.718 | 6268951.76 | 2031620.57 | -32409.9375 | 111673.837 | -24932.5241 | 235241.988 | 452901.285 | 1935452.6 | -22693.7902 | 53940.4799 | -9225.3201 | 53925.1544 | 64113.8083 | 309732.722 | -5114.0511
159.32 | 10.2485 | 1.1728 |  | 63944.0854 | -143341.818 | 558509.047 | 5415893.38 | 2356332.93 | -35428.4958 | 103063.545 | -15369.6009 | 234223.991 | 325268.597 | 1814532.17 | -26065.6713 | 50580.0544 | -6222.4812 | 53352.693 | 48106.6418 | 286252.876 | -6801.802
159.52 | 10.1865 | 1.1728 |  | 85522.626 | -121506.243 | 556043.252 | 4533499.51 | 2656157.77 | -41374.7124 | 87242.9413 | -3767.3375 | 233641.521 | 161397.337 | 1561102.72 | -23126.07 | 44660.5664 | -2568.3819 | 53192.2532 | 29926.4284 | 262650.688 | -6857.0245
159.72 | 10.135 | 1.1728 |  | 115275.831 | -90717.2557 | 542043.331 | 3711370.86 | 3089677.78 | -35187.8132 | 78594.3847 | 5382.2497 | 230490.477 | 63890.871 | 1377456.5 | -17287.7332 | 38313.4805 | -1186.6403 | 52648.1819 | 23585.9257 | 231307.629 | -4286.7625
159.92 | 10.0998 | 1.1728 |  | 142048.416 | -75105.4298 | 524818.594 | 3313451.59 | 3626444.55 | -40987.5893 | 78451.8766 | 13939.1014 | 225560.071 | -71734.4912 | 1255363.87 | -22070.7072 | 32249.9862 | 2228.6847 | 51251.519 | 6610.9862 | 203833.683 | -5687.6592
160.12 | 10.0549 | 1.1728 |  | 164470.461 | -59291.5445 | 502333.585 | 3018211.04 | 4160499.68 | -36220.9154 | 80967.4726 | 21782.8149 | 220905.657 | -176891.326 | 1223374.83 | -17832.4907 | 31113.1185 | 4053.6675 | 50558.9576 | -2727.8342 | 191201.638 | -4789.9777
160.32 | 10.0251 | 1.1728 |  | 190512.36 | -68237.8414 | 473410.259 | 3481591.05 | 4813900.49 | -41119.6933 | 95848.0219 | 24305.2798 | 215470.052 | -217934.599 | 1343450.15 | -23389.4386 | 30734.1556 | 4998.4504 | 50253.4576 | -8651.5776 | 170283.822 | -6494.4946
160.52 | 10.0327 | 1.1728 |  | 214745.411 | -72916.2638 | 444395.481 | 3844735.57 | 5397843.14 | -38913.6053 | 105008.742 | 26992.7078 | 208359.875 | -228363.625 | 1424617.19 | -22908.746 | 32296.1185 | 4600.7517 | 48843.9807 | -4193.2183 | 178781.519 | -6126.8889
160.72 | 10.0448 | 1.1728 |  | 211008.711 | -66068.6336 | 409730.517 | 3940958.68 | 5466890.58 | -28731.2335 | 113944.019 | 25405.257 | 200241.689 | -246375.291 | 1627480.62 | -20926.8098 | 35950.5503 | 6668.2437 | 47602.7387 | -18167.4295 | 189428.255 | -6683.314
160.92 | 10.0311 | 1.1728 |  | 216970.182 | -60739.9659 | 375995.589 | 3900920.3 | 5587941.66 | -34739.6718 | 112405.628 | 26822.8551 | 192604.688 | -196144.542 | 1670480.91 | -24681.2198 | 40865.8047 | 3415.6326 | 46596.0134 | -409.2496 | 219362.827 | -7665.1886
161.12 | 10.0533 | 1.1728 |  | 198980.106 | -48072.4636 | 345966.874 | 3511928.19 | 5139961.1 | -28222.3751 | 102719.376 | 24354.0648 | 183862.95 | -177095.848 | 1669255.55 | -17277.9969 | 44535.5394 | 3271.1825 | 44371.0324 | 140.2436 | 253892.058 | -5975.5616
161.32 | 10.0548 | 1.1728 |  | 186402.572 | -51383.3664 | 314115.479 | 3456957.75 | 4919240.33 | -34446.7966 | 98894.8182 | 24124.042 | 176706.842 | -176917.268 | 1604946.51 | -21527.2486 | 42542.7789 | 3155.8071 | 43052.7398 | 3784.2527 | 253640.093 | -7120.9213
161.52 | 10.0212 | 1.1728 |  | 173972.106 | -68438.9854 | 294275.533 | 3585701.95 | 4572838.58 | -34871.1544 | 94976.4005 | 19649.4459 | 173812.961 | -144667.298 | 1453416.01 | -15601.4543 | 36531.9618 | 3091.9153 | 42754.8195 | 2989.7294 | 221714.538 | -3370.6611
161.72 | 10.0345 | 1.1728 |  | 147061.587 | -90451.371 | 268920.659 | 4153970.6 | 4073659.28 | -28788.6889 | 97875.0046 | 10461.1492 | 168213.248 | -57324.3223 | 1478634.65 | -15969.0304 | 36496.4694 | 1965.1638 | 41797.5457 | 3106.1237 | 207801.006 | -5243.0486
161.92 | 10.0289 | 1.1728 |  | 133619.417 | -125684.257 | 253911.409 | 4996886.52 | 3876033.97 | -34258.8058 | 107230.685 | 2656.0463 | 165313.881 | 23369.5755 | 1487913.57 | -23016.2417 | 35071.1019 | 359.7351 | 41617.2888 | 9847.802 | 190116.114 | -5877.5174
162.12 | 10.0011 | 1.1728 |  | 96219.845 | -137967.764 | 240267.394 | 5328561.19 | 3169467.67 | -26839.2686 | 108552.735 | -7756.413 | 160670.83 | 131506.127 | 1628726.03 | -18752.4964 | 39981.0745 | -748.921 | 40515.5958 | 12429.3642 | 218351.49 | -7436.421
162.32 | 10.0032 | 1.1728 |  | 74220.2015 | -167833.366 | 235462.425 | 6073098.29 | 2756000.79 | -26482.1878 | 113219.791 | -17152.4978 | 160312.075 | 262580.87 | 1705483.69 | -18478.8104 | 41745.168 | -3669.0723 | 41088.8219 | 26617.7068 | 229911.915 | -5986.0166
162.52 | 10.0226 | 1.1728 |  | 53640.2986 | -191311.768 | 236424.636 | 6752953.9 | 2427879.49 | -26402.0318 | 119095.356 | -25206.8687 | 158463.063 | 380196.169 | 1852666.67 | -17961.2391 | 46007.6856 | -6078.0619 | 40005.8822 | 37438.7904 | 245019.033 | -6416.1078
162.72 | 10.0326 | 1.1728 |  | 26774.1741 | -227431.095 | 246168.293 | 7569232.85 | 2074394.05 | -33859.869 | 125720.408 | -32013.8905 | 161723.235 | 405701.978 | 1902667.36 | -21774.7273 | 46529.0718 | -5014.2931 | 41019.5946 | 29950.9159 | 247192.821 | -7515.4577
162.92 | 10.0348 | 1.1728 |  | 9705.7335 | -243003.625 | 264260.39 | 7889553.77 | 1716052.7 | -41629.1602 | 125128.602 | -37635.5679 | 166539.431 | 511826.996 | 1924854.83 | -26471.6996 | 49582.6164 | -8443.7195 | 42113.3317 | 50152.6038 | 273175.427 | -8524.2634
163.12 | 10.0632 | 1.1729 |  | -21577.7859 | -250420.766 | 291803.746 | 7874957.37 | 1021628.21 | -30550.3576 | 118142.526 | -44103.494 | 172531.117 | 574542.344 | 1857665.34 | -19810.3985 | 50408.8389 | -9778.2935 | 42513.985 | 57895.0395 | 289403.547 | -6806.9189
163.32 | 10.086 | 1.1741 |  | -39360.0625 | -255686.244 | 316840.823 | 8157050.83 | 630106.602 | -23217.5348 | 126365.387 | -54830.5147 | 180486.867 | 667071.554 | 1851469.61 | -14406.3391 | 45164.9782 | -9837.4125 | 44418.111 | 53802.7758 | 254819.555 | -4803.1909
163.52 | 10.0852 | 1.177 |  | -47835.5445 | -274997.31 | 343275.291 | 8706087.77 | 480758.578 | -34113.1501 | 135115.652 | -60799.6908 | 186699.569 | 732908.434 | 1890784.68 | -20088.1324 | 42582.1501 | -10524.9535 | 45684.8553 | 56174.2422 | 225709.848 | -6355.7615
163.72 | 10.1081 | 1.1806 |  | -48634.4729 | -279791.911 | 377043.427 | 8727259.58 | 477272.486 | -41591.2821 | 131130.318 | -58678.1062 | 192477.343 | 754677.442 | 1926731.71 | -22638.8186 | 46652.2661 | -12421.1711 | 46431.8517 | 69417.245 | 258331.782 | -7167.6372
163.92 | 10.1382 | 1.1832 |  | -47696.5568 | -270373.012 | 409670.333 | 8410165.54 | 569135.277 | -36425.1234 | 126971.521 | -53457.7945 | 198860.206 | 671377.96 | 1916800.79 | -21232.0684 | 48579.5144 | -10472.1229 | 47052.0727 | 60433.5853 | 271627.191 | -7000.0991
164.12 | 10.1441 | 1.1856 |  | -43792.5882 | -258556.099 | 448418.829 | 7905934.17 | 603787.291 | -40067.3757 | 117569.178 | -47361.0069 | 209498.861 | 590333.81 | 1816716.46 | -23105.2526 | 46586.1147 | -8480.4822 | 49255.1415 | 51737.5299 | 267357.912 | -8072.2626
164.32 | 10.1493 | 1.1885 |  | -32485.2535 | -237375.523 | 478773.753 | 7226821.5 | 626379.866 | -39018.6508 | 104262.295 | -42071.5702 | 217596.098 | 574865.229 | 1672163.98 | -23341.3232 | 44270.6339 | -9387.9962 | 50763.6073 | 58883.4272 | 257590.353 | -8388.8239
164.52 | 10.1719 | 1.1914 |  | -28103.0096 | -219348.47 | 510738.867 | 6571004.42 | 515364.394 | -30388.1978 | 90622.9315 | -37823.2634 | 225354.842 | 501239.273 | 1456501.25 | -13918.6426 | 40675.2657 | -8028.5521 | 51728.6639 | 54135.5092 | 248698.169 | -3718.9618
164.72 | 10.1928 | 1.1936 |  | -8338.7535 | -192815.617 | 530449.451 | 6104243.29 | 897151.806 | -24382.8938 | 93692.2153 | -32859.8545 | 229323.547 | 458184.284 | 1494788.02 | -15000.7531 | 40103.8933 | -7167.1802 | 52418.7579 | 48493.8472 | 237043.397 | -5420.6755
164.92 | 10.1905 | 1.1964 |  | 29271.0252 | -193122.879 | 548248.706 | 6326557.82 | 1719417.77 | -32076.9474 | 107959.717 | -27678.8128 | 234209.264 | 380467.815 | 1612283.5 | -19847.8269 | 36449.6063 | -4163.4015 | 53802.7609 | 29190.9048 | 191011.238 | -6315.0556
165.12 | 10.2311 | 1.2002 |  | 75849.8607 | -194516.72 | 559708.663 | 6412849.63 | 2772979.64 | -38114.2963 | 117391.397 | -16410.3803 | 236219.56 | 245917.22 | 1600519.66 | -24932.7366 | 34432.2973 | -2249.1123 | 53569.7871 | 23114.3627 | 183003.888 | -7913.1082
165.32 | 10.2702 | 1.2031 |  | 96866.0254 | -160838.101 | 562160.727 | 5632965.19 | 3303110.07 | -40218.1943 | 112694.857 | -2980.674 | 237390.298 | 86081.9637 | 1654023.42 | -26329.2074 | 38035.3197 | 910.4855 | 54224.7849 | 8312.3625 | 202881.79 | -8833.4677
165.52 | 10.2895 | 1.2059 |  | 118666.603 | -116966.647 | 561232.295 | 4663870.49 | 3608739.68 | -35188.4255 | 104446.847 | 5115.1817 | 239353.572 | 19860.2833 | 1610649.33 | -20980.3783 | 38078.9443 | 1600.2442 | 54990.7863 | 6502.3364 | 208728.299 | -7545.4076
165.72 | 10.3578 | 1.2093 |  | 154314.949 | -117137.024 | 560567.676 | 4590993.19 | 4213637.77 | -40783.7251 | 101493.214 | 12603.8877 | 241130.41 | -62006.2872 | 1433474.94 | -20314.2106 | 33785.1449 | 2009.6534 | 55056.9034 | 7942.9114 | 197008.74 | -5233.7383
165.92 | 10.3996 | 1.212 |  | 171004.706 | -98284.1828 | 539701.705 | 4279740.15 | 4520767.38 | -31905.9934 | 105087.656 | 15743.7769 | 237544.8 | -143176.909 | 1443721.5 | -19630.9254 | 32054.4787 | 4867.5831 | 54660.3638 | -8779.6941 | 178706.091 | -5766.0318
166.12 | 10.4308 | 1.2153 |  | 192298.281 | -76336.346 | 517540.061 | 3925132.81 | 4927611.55 | -29165.5614 | 104562.028 | 21247.4601 | 233059.086 | -165565.905 | 1496340.25 | -17506.2808 | 35706.28 | 4011.5453 | 54153.7056 | -4869.736 | 187701.128 | -5707.5625
166.32 | 10.4756 | 1.2192 |  | 212856.398 | -75116.2297 | 494998.987 | 4008428.25 | 5458813.87 | -34563.7718 | 112298.364 | 25614.6749 | 228086.349 | -195170.079 | 1661209.97 | -21515.7317 | 37771.0275 | 4762.7082 | 53437.6775 | -7681.8728 | 201211.573 | -5640.411
166.52 | 10.5091 | 1.2227 |  | 222598.059 | -64907.5752 | 463479.648 | 3890826.82 | 5821791.22 | -44693.1408 | 114814.863 | 31663.3597 | 220271.334 | -241624.222 | 1823069.73 | -30431.9626 | 45095.1441 | 4832.4871 | 51982.4758 | -6486.9882 | 244611.499 | -8952.4536
166.72 | 10.5253 | 1.2265 |  | 223409.271 | -60361.6705 | 429984.541 | 3679947.11 | 5817188.73 | -43519.5095 | 107837.143 | 34442.4067 | 213911.412 | -292786.244 | 1735377.23 | -26356.8337 | 45661.1809 | 5648.8351 | 51122.0153 | -7578.345 | 265617.76 | -8031.8502
166.92 | 10.5587 | 1.227 |  | 219623.536 | -56515.5117 | 401611.116 | 3523621.73 | 5628047.74 | -37048.1348 | 100376.214 | 33334.5794 | 209445.109 | -257235.747 | 1629088.48 | -19616.7555 | 44750.3985 | 3778.9825 | 50421.8536 | 3459.9981 | 266673.626 | -4051.8967
167.12 | 10.6081 | 1.2236 |  | 197945.067 | -51930.3993 | 371220.341 | 3642638.49 | 5242440.36 | -27673.9563 | 103770.336 | 26562.2102 | 202342.549 | -174930.858 | 1800022.35 | -18319.4883 | 49198.4998 | 2890.101 | 49210.1094 | 2970.5097 | 278977.785 | -5637.3761
167.32 | 10.6474 | 1.2194 |  | 193580.939 | -79966.4312 | 344400.472 | 4409549.73 | 5271948.06 | -29916.2265 | 116159.299 | 20786.406 | 197470.879 | -110169.886 | 1863459.59 | -22469.7688 | 47228.2368 | 1871.2182 | 48635.6294 | 8797.1661 | 271014.868 | -6225.7963
167.52 | 10.7303 | 1.2162 |  | 186383.365 | -111544.464 | 323544.047 | 5157004.74 | 5277960.25 | -33114.3475 | 127205.742 | 15609.4044 | 193084.34 | -63402.9882 | 1918610.47 | -23007.3111 | 45952.8665 | 1448.7591 | 47740.9322 | 7685.978 | 250709.687 | -5890.5431
167.72 | 10.7897 | 1.2119 |  | 154738.53 | -120390.619 | 309957.031 | 5281873.08 | 4780836.54 | -37227.5265 | 123868.338 | 12516.9618 | 191788.643 | -52037.6123 | 1942425.7 | -31963.1837 | 50014.7483 | 1530.6963 | 48230.501 | 7796.4339 | 275947.255 | -8807.8931
167.92 | 10.8276 | 1.2082 |  | 113210.412 | -111964.813 | 305062.68 | 4802134.78 | 3753301.03 | -35142.6005 | 106312.671 | 5025.1925 | 191805.866 | 59162.3168 | 1898477.41 | -24090.7671 | 53802.7095 | -933.2322 | 48107.2032 | 21372.8087 | 315718.091 | -8512.1259
168.12 | 10.8637 | 1.2061 |  | 77410.8448 | -139234.203 | 308211.062 | 5181057.6 | 2844253.87 | -39005.0121 | 97134.462 | -6246.7607 | 195180.875 | 195019.516 | 1749998.21 | -22589.5332 | 50967.775 | -3881.039 | 48822.7196 | 36334.9971 | 304944.822 | -6512.5347
168.32 | 10.8957 | 1.2047 |  | 47450.6886 | -177020.199 | 316957.423 | 5944854.61 | 2189669.88 | -43080.4666 | 99814.991 | -17976.3367 | 197607.064 | 315744.852 | 1669296.58 | -24921.0947 | 46660.5625 | -5632.03 | 48957.7825 | 42818.4215 | 277596.776 | -6936.5095
168.52 | 10.9163 | 1.2044 |  | 21588.8509 | -202565.679 | 324178.034 | 6663657.78 | 1773484.08 | -36417.0979 | 112019.158 | -28925.4968 | 199145.336 | 372777.045 | 1643973.86 | -27029.301 | 41344.0673 | -4711.1272 | 49092.5307 | 35815.0455 | 252990.293 | -8966.4761
168.72 | 10.9345 | 1.2055 |  | 4899.1746 | -239975.352 | 349467.098 | 7290341.07 | 1471463.33 | -46515.8948 | 109553.315 | -33375.217 | 206569.654 | 407713.835 | 1565143.7 | -25746.9467 | 38697.086 | -4923.3175 | 50657.0746 | 34982.6353 | 230892.078 | -8239.5026
168.92 | 10.9749 | 1.2001 |  | -20381.7791 | -242227.186 | 373600.003 | 7389559.23 | 1028840.18 | -41981.7481 | 112426.962 | -38623.248 | 212696.708 | 474707.363 | 1610886.51 | -26859.8115 | 38704.5768 | -6104.1562 | 51881.5201 | 40536.6044 | 227247.494 | -9486.0831
169.12 | 11.017 | 1.1778 |  | -33932.568 | -263146.756 | 412736.259 | 7733234.71 | 714928.251 | -41087.5714 | 111172.134 | -43500.0682 | 223807.21 | 502473.773 | 1547876.58 | -20914.9077 | 39495.9618 | -6540.6198 | 53931.6133 | 43022.9698 | 235349.359 | -6840.7768
169.32 | 11.0667 | 1.1724 |  | -50594.462 | -257948.434 | 446417.031 | 7969576.76 | 489732.045 | -29396.3593 | 121348.006 | -50017.3174 | 232873.45 | 615976.896 | 1787446.73 | -17198.725 | 42497.3537 | -8449.4171 | 56329.0349 | 52334.8158 | 239642.485 | -6488.6749
169.52 | 11.1258 | 1.1726 |  | -38033.0968 | -294209.366 | 490435.585 | 8816491.34 | 734535.071 | -57606.8967 | 129938.505 | -52885.9902 | 243566.357 | 659147.131 | 1868284.87 | -31518.5332 | 42987.7938 | -8783.1739 | 57942.3623 | 52208.6963 | 237931.879 | -10994.7985
169.72 | 11.1711 | 1.1728 |  | -27563.1625 | -287977.272 | 526551.627 | 8529863.63 | 905287.881 | -60587.8639 | 122531.978 | -47100.9088 | 250302.141 | 626850.236 | 1806626.27 | -31727.4267 | 44326.1924 | -9479.6946 | 58731.9728 | 58648.3999 | 248966.047 | -10371.8863
169.92 | 11.2044 | 1.1728 |  | -37327.995 | -246114.553 | 560997.781 | 7330714.17 | 639297.596 | -44034.5024 | 102694.582 | -39482.2573 | 257450.259 | 521737.104 | 1724749.24 | -25560.4003 | 48581.038 | -7397.0748 | 59687.0241 | 51235.506 | 293530.935 | -9586.584
170.12 | 11.227 | 1.1728 |  | -18535.1288 | -202649.83 | 590319.622 | 6285753.59 | 849016.518 | -33462.9921 | 95504.9303 | -32179.6531 | 264956.873 | 481283.701 | 1666729.49 | -19942.3265 | 47380.2628 | -7802.6755 | 61337.2668 | 55496.7996 | 287672.389 | -6903.1544
170.32 | 11.2408 | 1.1728 |  | 10572.2787 | -213153.684 | 622991.548 | 6552659.15 | 1468726.36 | -39977.9243 | 107397.711 | -28816.7306 | 274327.011 | 365870.573 | 1561093.43 | -23858.4051 | 39435.5743 | -3974.2511 | 62644.3748 | 36545.8528 | 243734.521 | -7931.0896
170.52 | 11.2579 | 1.1728 |  | 54479.1046 | -226447.859 | 641057.813 | 6864633.42 | 2321316.22 | -52398.5993 | 111065.418 | -20649.3428 | 281082.38 | 295168.319 | 1494153.02 | -27995.248 | 34672.4291 | -3355.2796 | 64714.0122 | 33609.8811 | 212658.745 | -8467.8139
170.72 | 11.2826 | 1.1728 |  | 68815.2654 | -174241.807 | 648093.303 | 6031587.33 | 2519563.35 | -33018.8637 | 113230.509 | -18013.9057 | 281115.21 | 265952.047 | 1672120.02 | -21243.2767 | 38533.8882 | -1592.3813 | 64744.5791 | 20851.3061 | 204817.049 | -8443.0903
170.92 | 11.3149 | 1.1727 |  | 116407.491 | -173800.624 | 654008.727 | 6074795.09 | 3559656.17 | -46691.476 | 119176.33 | -6188.1839 | 282324.268 | 158612.679 | 1650210.63 | -24103.6078 | 35169.2971 | -369.8651 | 64469.5088 | 17938.6146 | 192810.2 | -8130.6646
171.12 | 11.3652 | 1.1688 |  | 149783.746 | -161260.391 | 643942.515 | 5865688.1 | 4368286.72 | -42269.3558 | 123543.045 | 5331.8166 | 280689.037 | -19821.0586 | 1646658.87 | -25073.2639 | 35492.125 | 3175.1253 | 64271.0957 | 862.7789 | 192796.083 | -8529.3046
171.32 | 11.397 | 1.1622 |  | 181892.628 | -139198.975 | 634041.661 | 5482351.96 | 4990843.59 | -41203.2216 | 124291.939 | 13516.2715 | 281772.163 | -113152.099 | 1680308.68 | -26660.9928 | 36652.5289 | 4841.2173 | 65457.1903 | -6895.874 | 204088.314 | -7814.2863
171.52 | 11.4272 | 1.1558 |  | 205027.608 | -117279.63 | 611000.899 | 5062550.13 | 5393200.85 | -38041.2445 | 120305.794 | 19635.3331 | 276651.07 | -136786.599 | 1730058.35 | -21740.6201 | 42090.2127 | 3735.4157 | 64142.1955 | -230.6386 | 232423.699 | -6873.9978
171.72 | 11.4535 | 1.1492 |  | 216335.49 | -115762.429 | 586202.584 | 5162619.12 | 5633934.32 | -38932.9964 | 124619.789 | 20537.6136 | 272435.12 | -164859.68 | 1813298.75 | -25277.3894 | 45639.2698 | 4548.7337 | 63988.4986 | -4140.1932 | 258013.168 | -8072.3295
171.92 | 11.473 | 1.1418 |  | 239763.369 | -117769.343 | 550700.152 | 5389074.62 | 6194548.82 | -40978.9238 | 133484.057 | 24134.4933 | 264096.53 | -136055.258 | 1963739.86 | -27455.7464 | 48526.55 | 2203.0984 | 62499.3434 | 9136.9713 | 264802.279 | -7127.3499
172.12 | 11.4908 | 1.1343 |  | 237756.183 | -110157.991 | 509791.723 | 5563836.1 | 6336418.29 | -36888.0152 | 141878.992 | 24114.7895 | 253107.12 | -148685.511 | 2184398.9 | -31003.4551 | 54943.7223 | 3010.6023 | 60778.6841 | 3505.3597 | 290566.665 | -9110.9354
172.32 | 11.5145 | 1.1269 |  | 241636.384 | -112107.449 | 473666.232 | 5543013.06 | 6451145.74 | -37317.6074 | 139577.627 | 26015.8405 | 245080.022 | -147788.295 | 2169657.35 | -29835.8891 | 56305.8785 | 2162.5613 | 59287.4925 | 11429.7059 | 319468.188 | -8410.6647
172.52 | 11.5437 | 1.1196 |  | 216399.98 | -98014.7447 | 440837.193 | 5307721.17 | 5986138.98 | -27317.8453 | 137941.655 | 21490.5246 | 236877.242 | -120552.521 | 2262184.16 | -24144.9995 | 59976.7796 | 2654.4581 | 57412.3237 | 4703.0437 | 338309.521 | -8271.7394
172.72 | 11.5602 | 1.1391 |  | 207321.791 | -118093.51 | 417335.952 | 5673762.58 | 5771145.67 | -36567.4555 | 137286.018 | 17361.8592 | 235406.689 | -36616.3502 | 2229373.33 | -29907.8046 | 60412.0645 | -540.1728 | 58542.5302 | 21821.8174 | 333993.24 | -7633.0062
172.92 | 11.5864 | 1.1911 |  | 173344.476 | -132085.029 | 394447.618 | 5872969.57 | 5087204.25 | -29416.5213 | 134009.567 | 9391.5222 | 228748.123 | 37463.5307 | 2179939.19 | -25287.3804 | 60583.6891 | -1816.264 | 55946.9495 | 27610.5001 | 342678.367 | -6698.2253
173.12 | 11.6126 | 1.2748 |  | 145427.495 | -154217.28 | 375869.715 | 6432852.85 | 4547656.39 | -33912.7482 | 136819.743 | -1007.235 | 226901.506 | 141825.054 | 2190465.71 | -26326.358 | 60221.4335 | -3060.2954 | 56833.48 | 33527.5465 | 350306.475 | -5636.9323
173.32 | 11.631 | 1.3695 |  | 112270.345 | -178839.594 | 370301.052 | 7065627.9 | 3962518.11 | -33468.4748 | 143563.596 | -12027.2205 | 223359.127 | 252715.45 | 2320521.86 | -26829.8714 | 60706.531 | -3482.8274 | 55112.4208 | 33250.1582 | 345228.965 | -9637.0368
173.52 | 11.6513 | 1.4643 |  | 99688.9441 | -236486.701 | 370398.321 | 8430438.86 | 3815401.71 | -45224.2411 | 158683.309 | -23576.6993 | 228115.676 | 365595.301 | 2372421.37 | -28432.4618 | 56187.3543 | -4406.4229 | 57623.5045 | 30757.4442 | 298423.237 | -8055.89
173.72 | 11.6835 | 1.5843 |  | 64674.319 | -249302.689 | 380670.47 | 8710974.68 | 3186093.06 | -48496.2663 | 156605.034 | -30090.4701 | 228126.664 | 453155.881 | 2421104.6 | -38103.4245 | 61207.478 | -6657.9075 | 56891.7319 | 44507.7291 | 330402.431 | -11837.9066
173.92 | 11.6998 | 1.7318 |  | 18520.5691 | -239732.654 | 395826.566 | 8274799.03 | 2119466.9 | -44046.6936 | 138947.865 | -36946.0859 | 231337.719 | 559043.265 | 2442667.28 | -30384.724 | 68839.5443 | -9600.0811 | 58129.2338 | 56728.091 | 371320.993 | -9413.9275
174.12 | 11.7358 | 1.8556 |  | 2054.1021 | -270874.114 | 429326.832 | 8801626.39 | 1731502.56 | -50883.3561 | 142746.104 | -45427.3092 | 240361.659 | 627177.794 | 2219394.3 | -32601.8082 | 58433.9456 | -10125.9129 | 58321.8309 | 67729.4807 | 354053.701 | -10363.9176
174.32 | 11.7749 | 2.0374 |  | -7734.8365 | -314001.235 | 467458.41 | 9494628.37 | 1495353.76 | -52075.1702 | 144601.062 | -50903.2831 | 253197.04 | 626868.658 | 2030857.91 | -24362.559 | 47630.1671 | -8528.8637 | 61045.2923 | 55276.6214 | 280946.98 | -5796.661
174.52 | 11.796 | 2.2319 |  | -30428.1108 | -302889.875 | 500149.571 | 9332494.85 | 1045086.55 | -48836.9282 | 145690.773 | -55260.0739 | 260766.379 | 678128.913 | 2119002.78 | -26421.3038 | 48544.5918 | -8574.8806 | 63047.7922 | 51263.6513 | 266149.021 | -8717.3888
174.72 | 11.8209 | 2.3693 |  | -19703.1722 | -314055.57 | 545659.864 | 9361806.64 | 1131214.08 | -65501.3953 | 138341.981 | -53404.0038 | 271392.963 | 708008.26 | 2048438.05 | -33689.2292 | 50469.7241 | -10722.2665 | 64838.2545 | 64159.6426 | 278994.425 | -9978.2033
174.92 | 11.8553 | 2.5142 |  | -34743.1928 | -271983.525 | 584645.403 | 8276594.69 | 789829.077 | -50467.5119 | 120235.254 | -46720.3142 | 276984.25 | 645943.351 | 2047251.44 | -28038.2601 | 57346.5902 | -10258.3594 | 64947.9903 | 64193.9928 | 325080.772 | -9122.0339
175.12 | 11.8621 | 2.6636 |  | -28437.8702 | -244193.406 | 618452.683 | 7499778.91 | 825751.324 | -52262.9019 | 107490.171 | -40025.7235 | 285252.913 | 590928.98 | 2020575.67 | -30453.3042 | 59772.2536 | -9651.9366 | 66714.8156 | 64901.0649 | 348965.452 | -9865.4919
175.32 | 11.8836 | 2.7619 |  | -6759.6435 | -230748.628 | 655797.074 | 7210615.45 | 1273436.66 | -45372.1568 | 112819.259 | -33958.3084 | 295436.463 | 500988.978 | 1834928.37 | -31436.3362 | 50552.1312 | -7888.7738 | 68128.269 | 56561.4171 | 294563.848 | -8302.5966
175.52 | 11.9115 | 2.8901 |  | 24585.5936 | -211709.597 | 683641.011 | 6789998.42 | 1768452.4 | -36467.8815 | 109233.811 | -28104.9163 | 302739.194 | 436597.34 | 1830805.05 | -19150.4154 | 50982.9667 | -6591.3306 | 69962.1254 | 44261.1339 | 276944.457 | -6353.9963
175.72 | 11.9357 | 3.0373 |  | 67037.8297 | -221227.091 | 703240.964 | 7226337.73 | 2742964.6 | -41767.5798 | 125394.065 | -21099.9126 | 308676.414 | 308374.07 | 1845081.83 | -24120.9116 | 45366.3464 | -2811.7525 | 70878.3777 | 27551.0736 | 250713.829 | -7370.8003
175.92 | 11.9885 | 3.1965 |  | 117616.471 | -224862.348 | 714164.771 | 7494707.13 | 3953610.58 | -53425.5578 | 140857.208 | -9536.7375 | 312860.205 | 194722.993 | 1946901.49 | -36443.3601 | 44242.7007 | -1218.5768 | 72262.2024 | 22502.6749 | 229781.871 | -10268.5046
176.12 | 12.0036 | 3.4042 |  | 135821.045 | -179507.491 | 706700.625 | 6511849.28 | 4296645.34 | -52421.4606 | 131482.656 | 1039.0367 | 309979.339 | 88700.926 | 2016642.2 | -34798.088 | 50684.0462 | 590.5347 | 71703.3774 | 14406.1163 | 277229.415 | -12045.3836
176.32 | 12.0301 | 3.5721 |  | 164302.547 | -141875.218 | 700716.42 | 5611009.97 | 4613960.63 | -45179.7003 | 117367.28 | 9814.3913 | 310237.416 | 18442.4621 | 1874643.58 | -29486.5356 | 49732.0879 | 571.3193 | 71923.6183 | 17927.3041 | 284015.663 | -8930.9314
176.52 | 12.0521 | 3.7506 |  | 185153.41 | -116751.982 | 681226.994 | 4961458.92 | 4923166.22 | -43930.9298 | 112526.925 | 17095.8461 | 305249.571 | -75412.4201 | 1733951 | -29758.1111 | 46479.7392 | 2104.5514 | 70177.817 | 10529.69 | 265132.838 | -8983.0805
176.72 | 12.0442 | 3.9048 |  | 199920.872 | -100359.539 | 653611.972 | 4501003.28 | 5159216.41 | -34799.5233 | 107793.66 | 22411.7359 | 301344.355 | -157965.977 | 1660521.32 | -16051.7334 | 45718.238 | 3324.3346 | 70425.2928 | 2402.7843 | 252617.159 | -3442.2193
176.92 | 12.0362 | 3.9862 |  | 225960.747 | -103917.964 | 620180.99 | 4749719.23 | 5757323.14 | -46713.8942 | 113805.172 | 27344.0823 | 293339.396 | -199559.113 | 1691759.24 | -30377.0103 | 44495.8197 | 4068.4048 | 68725.7838 | 2924.0918 | 259326.914 | -8050.5103
177.12 | 12.0334 | 4.0528 |  | 239269.678 | -106448.912 | 575985.383 | 4986521.56 | 6203220.88 | -51336.7049 | 123394.113 | 30528.7529 | 282999.278 | -240633.1 | 1793294.45 | -34958.8021 | 44504.1161 | 5152.0445 | 66886.7932 | -3915.0477 | 250929.906 | -8998.2548
177.32 | 12.0292 | 4.1271 |  | 232341.513 | -93086.1272 | 540705.86 | 4711654.02 | 6111966.62 | -43298.368 | 119080.885 | 31696.5045 | 274812.618 | -250623.147 | 1898760.29 | -30902.5587 | 52400.7381 | 5032.9885 | 66062.2702 | -4962.768 | 288030.925 | -10484.4288
177.52 | 12.0383 | 4.1895 |  | 222295.823 | -86744.8252 | 508100.295 | 4685255.6 | 5867983.13 | -32838.8794 | 121810.202 | 26016.0072 | 268056.811 | -177832.507 | 1977101.45 | -26224.3814 | 53314.6302 | 3886.1797 | 64671.2917 | -324.069 | 298391.135 | -9752.1351
177.72 | 12.0604 | 4.3109 |  | 210943.543 | -114251.711 | 471550.822 | 5322432.77 | 5824574.74 | -40791.867 | 132762.963 | 22832.6467 | 260441.793 | -166115.674 | 1907380.6 | -34507.5788 | 44424.1488 | 4300.963 | 63180.9433 | -2235.5815 | 236210.66 | -9608.6036
177.92 | 12.061 | 4.4615 |  | 179702.729 | -128169.481 | 447109.524 | 5403107.85 | 5132893.09 | -37619.4048 | 125932.589 | 15257.3034 | 256740.548 | -99782.8213 | 1856141.09 | -27088.6981 | 45574.0622 | 3352.5836 | 63389.0147 | -571.8401 | 244281.649 | -7890.3905
178.12 | 12.0613 | 4.5588 |  | 140498.045 | -130614.054 | 425400.996 | 5552840.26 | 4302153.39 | -33996.1464 | 121003.568 | 4880.5575 | 251821.191 | 45097.2858 | 1897318.76 | -27937.8619 | 50530.2886 | -69.1484 | 62669.2021 | 16969.5154 | 285938.906 | -8445.4153
178.32 | 12.0584 | 4.6659 |  | 107802.077 | -154486.28 | 417022.263 | 5966668.59 | 3571606.18 | -45506.421 | 118474.087 | -6088.6619 | 247763.284 | 173817.5 | 1891199.2 | -38346.85 | 51162.0298 | -1852.0763 | 60623.0107 | 26228.2377 | 303218.549 | -13233.6574
178.52 | 12.0384 | 4.7543 |  | 72437.9952 | -180577.722 | 412901.597 | 6323502.3 | 2866158.23 | -43577.16 | 116290.422 | -14643.7502 | 247789.693 | 261048.261 | 1810645.77 | -29910.7383 | 46978.9313 | -3428.5904 | 61232.8318 | 31331.2771 | 269486.969 | -7816.9324
178.72 | 12.0132 | 4.7652 |  | 31416.1744 | -184524.377 | 418903.949 | 6294579.77 | 1977451.7 | -45706.499 | 109726.106 | -23719.1692 | 247142.101 | 366435.209 | 1823697.22 | -33090.3994 | 48489.1282 | -4752.4956 | 61073.2734 | 35410.4442 | 271408.971 | -12026.8767
178.92 | 12.0017 | 4.7408 |  | 11338.7906 | -219389.072 | 438702.616 | 6825121.82 | 1542317.23 | -54127.5271 | 107459.868 | -30290.6303 | 252054.63 | 420850.688 | 1658554.75 | -34881.0604 | 42410.9367 | -5430.5024 | 61551.1195 | 39265.1144 | 239281.924 | -11124.9488
179.12 | 11.9699 | 4.7463 |  | -21725.0466 | -230118.752 | 461535.249 | 6945285.77 | 834932.977 | -45923.6319 | 103965.33 | -37875.7278 | 258061.073 | 469221.156 | 1551546.37 | -29587.181 | 39371.4025 | -5531.8821 | 62652.3894 | 37965.5748 | 228215.764 | -9476.8841
179.32 | 11.949 | 4.7066 |  | -39577.0457 | -242150.954 | 494203.218 | 7068159.61 | 357103.317 | -50246.1289 | 100658.903 | -44688.597 | 265682.153 | 572673.299 | 1481994.57 | -30570.996 | 37554.9416 | -7945.324 | 64225.5301 | 50094.2196 | 221830.425 | -10510.2674
179.52 | 11.9372 | 4.6837 |  | -58143.8712 | -235789.956 | 523381.935 | 6866446.38 | -92602.8326 | -47410.5585 | 95791.2552 | -48064.4676 | 269973.501 | 610556.161 | 1450361.38 | -31607.8646 | 37505.6894 | -8414.9973 | 64512.1987 | 51441.6183 | 211419.233 | -10622.307
179.72 | 11.9073 | 4.6878 |  | -71315.0997 | -216006.298 | 559447.987 | 6243055.29 | -410986.558 | -43675.7157 | 83001.4647 | -45531.1166 | 275901.272 | 596854.26 | 1437436.33 | -30941.4319 | 41853.2404 | -8524.7674 | 65097.586 | 52920.8472 | 240049.064 | -11670.9998
179.92 | 11.8797 | 4.6385 |  | -62586.1979 | -210689.545 | 597346.924 | 5910940.86 | -351762.378 | -48487.952 | 75398.5938 | -41894.741 | 284195.431 | 549390.336 | 1314827.75 | -29891.9649 | 37926.3386 | -7436.2649 | 66427.3101 | 48392.2156 | 224692.528 | -10320.8182
180.12 | 11.8592 | 4.5736 |  | -43935.986 | -202043.109 | 632083.055 | 5644752.02 | -7915.2836 | -42239.8819 | 73449.1344 | -35764.576 | 291633.037 | 482681.76 | 1183827.09 | -26284.2133 | 32683.7779 | -6603.2506 | 67306.5184 | 47094.2216 | 206219.764 | -8095.9593
180.32 | 11.8191 | 4.5064 |  | -31817.2973 | -191377.037 | 660958.785 | 5502512.17 | 281722.232 | -44158.4687 | 78622.776 | -32175.2516 | 298562.809 | 408069.645 | 1208451.09 | -28888.9421 | 31983.6026 | -4221.6859 | 68881.2553 | 32092.8016 | 177970.952 | -10601.8226
180.52 | 11.7845 | 4.3799 |  | 9881.655 | -193272.089 | 679208.268 | 5739426.87 | 1092480.7 | -42270.8566 | 88988.198 | -27672.4589 | 303109.863 | 378973.989 | 1223965.99 | -23093.283 | 29410.2185 | -4623.5137 | 70025.3159 | 37112.4878 | 170961.203 | -8121.4831
180.72 | 11.7607 | 4.2492 |  | 37949.1997 | -176400.497 | 691900.117 | 5603014.8 | 1728547.75 | -58253.4675 | 94652.3639 | -19953.2662 | 302833.744 | 296217.524 | 1320737.73 | -36956.6092 | 30257.3148 | -2728.5873 | 69337.2606 | 27694.0185 | 162976.819 | -13050.9458
180.92 | 11.7252 | 4.1085 |  | 68191.3777 | -146062.962 | 692197.679 | 4934146.44 | 2283801.66 | -51796.2651 | 91286.3429 | -10162.1871 | 301601.196 | 193035.352 | 1312710.13 | -31850.9865 | 31164.2617 | -1266.9886 | 69158.1652 | 21713.0837 | 173641.676 | -9499.7593
181.12 | 11.6928 | 3.9342 |  | 95262.0701 | -104840.271 | 685895.845 | 4126470.15 | 2860838.86 | -48854.7791 | 88214.8567 | 1167.5168 | 298130.303 | 81067.5125 | 1367674.04 | -28979.399 | 35383.0817 | 129.3198 | 68175.1364 | 16916.6979 | 202676.896 | -9010.3516
181.32 | 11.6558 | 3.7621 |  | 134721.008 | -90512.7014 | 670528.556 | 3922515.95 | 3733197.72 | -53624.4429 | 92258.3602 | 11791.8636 | 294318.534 | -39775.5133 | 1435677.82 | -31593.1543 | 36154.8242 | 2392.4646 | 67488.4111 | 5885.7084 | 202052.452 | -9733.1192
181.52 | 11.6255 | 3.5775 |  | 173520.262 | -100245.395 | 655707.517 | 4080024.55 | 4517931.76 | -58574.167 | 90237.6494 | 21042.0238 | 292022.725 | -153053.024 | 1362983.89 | -29829.2398 | 36866.1652 | 3980.388 | 67258.8412 | 183.2119 | 214328.92 | -8742.3079
181.72 | 11.6007 | 3.4091 |  | 185992.039 | -74002.2027 | 621315.562 | 3837711.57 | 4829971.37 | -39705.7944 | 102426.657 | 22330.3366 | 284697.581 | -168070.677 | 1514197.53 | -24946.6855 | 38705.9638 | 4158.3204 | 66343.4913 | -1839.1631 | 216789.992 | -7317.2165
181.92 | 11.5649 | 3.2553 |  | 209626.558 | -82264.2693 | 588513.105 | 4208182.43 | 5254249.56 | -48608.7921 | 109075.498 | 21802.0695 | 276328.137 | -153179.407 | 1594906.49 | -30402.023 | 39099.4333 | 4163.9174 | 64780.1622 | -1907.6132 | 224318.671 | -9935.8986
182.12 | 11.5435 | 3.0784 |  | 224954.524 | -86792.893 | 541306.338 | 4385333.93 | 5693251.23 | -49427.2951 | 115967.016 | 26083.7671 | 262977.628 | -181608.248 | 1631663.85 | -33284.7041 | 37978.4966 | 3881.3728 | 62019.4233 | -193.492 | 202802.853 | -8957.7689
182.32 | 11.5028 | 2.9154 |  | 209337.803 | -66487.8636 | 500008.396 | 3841965.34 | 5375850.32 | -41041.9945 | 106432.578 | 27063.1842 | 252391.303 | -219872.65 | 1697853.72 | -25465.7226 | 44312.2038 | 5390.6474 | 60517.1081 | -10487.0015 | 241663.067 | -8743.3754
182.52 | 11.4622 | 2.7033 |  | 211137.934 | -66796.8412 | 465803.979 | 3934444.08 | 5422558.21 | -31451.9168 | 107554.781 | 25915.11 | 244804.177 | -161879.935 | 1730751.67 | -19545.8366 | 45435.9307 | 2965.9481 | 59007.849 | 3921.4861 | 259414.661 | -6160.46
182.72 | 11.4336 | 2.4764 |  | 196342.02 | -105902.439 | 430768.385 | 4950019.69 | 5292261.36 | -39227.1822 | 120723.386 | 18377.8469 | 236719.933 | -123460.569 | 1850468.54 | -26522.7172 | 46063.3857 | 3666.8039 | 57561.5634 | -2646.1193 | 250661.054 | -8231.8439
182.92 | 11.4018 | 2.2717 |  | 190858.191 | -133049.074 | 394366.85 | 5900285.95 | 5330006.14 | -36585.4381 | 137928.602 | 10076.4186 | 228859.757 | -10023.1311 | 1951178.01 | -30485.6717 | 44134.9602 | 1191.5089 | 56772.3346 | 9399.788 | 237836.925 | -8134.1485
183.12 | 11.3716 | 2.0575 |  | 157378.522 | -157420.976 | 371710.677 | 6484601.74 | 4652400.07 | -33686.354 | 139989.833 | -1834.8917 | 221271.286 | 89375.2975 | 2067589.93 | -27678.6949 | 50243.9828 | 436.5208 | 54891.8204 | 9992.9477 | 272939.128 | -9019.1557
183.32 | 11.3546 | 1.8556 |  | 130115.655 | -168193.254 | 347784.203 | 6924730.04 | 4233897.11 | -37151.7252 | 144115.367 | -9434.0169 | 214596.925 | 258675.574 | 2234522.27 | -30682.4933 | 56577.4719 | -4881.4227 | 54419.5641 | 36240.9963 | 297750.652 | -9142.7021
183.52 | 11.3493 | 1.6953 |  | 87324.8842 | -177746.772 | 336961.331 | 7088678.47 | 3389602.37 | -35990.5234 | 137114.945 | -18414.6235 | 207797.286 | 332364.564 | 2307688.81 | -28890.9996 | 64804.1413 | -5670.4496 | 51863.8049 | 40801.2628 | 367378.375 | -10192.5289
183.72 | 11.3314 | 1.5694 |  | 69196.4994 | -217513.875 | 340633.26 | 7823998.89 | 3084080.49 | -43815.1333 | 140713.158 | -24514.4365 | 210825.211 | 393066.237 | 2196914.57 | -30902.6607 | 56629.8336 | -6321.7035 | 52662.5104 | 47182.4685 | 330642.827 | -8991.2771
183.92 | 11.3142 | 1.4178 |  | 31131.2173 | -229628.111 | 353591.048 | 7882604.48 | 2230215.73 | -49890.5369 | 133388.433 | -33315.8253 | 213701.854 | 483328.879 | 2187011.36 | -35887.7473 | 57461.0638 | -7185.3246 | 53342.479 | 46592.8581 | 320440.768 | -10702.4196
184.12 | 11.2981 | 1.2567 |  | -8993.2675 | -222858.653 | 371752.778 | 7406699.53 | 1331667.06 | -44167.6396 | 120345.396 | -38311.4865 | 216353.06 | 557613.337 | 2053235.66 | -31748.1385 | 56170.6598 | -9107.6619 | 53366.3616 | 58676.7474 | 326230.709 | -11657.1823
184.32 | 11.2815 | 1.1021 |  | -26635.7002 | -242252.873 | 396720.794 | 7659128.6 | 871086.38 | -40921.2923 | 117096.173 | -44681.1503 | 223931.25 | 601359.267 | 1865154.38 | -23889.3166 | 49953.5567 | -9779.5684 | 54676.6188 | 58914.1144 | 281292.196 | -6435.696
184.52 | 11.2522 | 1.0362 |  | -40092.695 | -258930.45 | 431310.223 | 7904766.89 | 554680.75 | -46658.3992 | 117593.375 | -49568.8131 | 232456.719 | 640711.481 | 1790520.13 | -28046.8479 | 45783.9354 | -9726.5834 | 56409.2346 | 58803.8203 | 260864.71 | -7912.7746
184.72 | 11.2343 | 1.0316 |  | -52244.0591 | -265593.645 | 461228.21 | 7917275.63 | 263184.453 | -46101.307 | 109852.524 | -51175.9753 | 237906.126 | 652628.522 | 1712437.44 | -27689.9163 | 46997.7295 | -10048.1675 | 56740.9271 | 61322.9736 | 277608.178 | -8966.7117
184.92 | 11.2284 | 1.0336 |  | -58295.7155 | -251073.942 | 492388.11 | 7585045.45 | 109408.214 | -41042.9344 | 107172.773 | -50958.1615 | 244081.304 | 657893.441 | 1704856.63 | -25953.6358 | 45773.9872 | -9938.4374 | 58027.5691 | 59724.9526 | 265420.151 | -9485.1367
185.12 | 11.229 | 1.0341 |  | -49944.9427 | -254398.222 | 533601.691 | 7555108.5 | 308275.281 | -37982.0191 | 108768.998 | -47892.2532 | 253932.466 | 592206.84 | 1600419.83 | -23589.6293 | 39709.8874 | -8029.613 | 59322.8719 | 50457.9646 | 230067.718 | -7391.452
185.32 | 11.209 | 1.0341 |  | -34990.0708 | -243023.775 | 567412.605 | 7261583.04 | 526324.906 | -42161.7768 | 105920.608 | -43906.3188 | 262370.529 | 563415.661 | 1572288.73 | -23804.8559 | 38867.713 | -7825.9982 | 61290.5941 | 48743.8892 | 217678.208 | -7953.6861
185.52 | 11.2352 | 1.0341 |  | -20500.5177 | -218869.005 | 596027.1 | 6785734.51 | 819770.197 | -35996.757 | 106736.026 | -38295.1835 | 267359.388 | 509818.525 | 1612384.33 | -24856.34 | 38665.2872 | -6692.4245 | 61752.5381 | 43918.7472 | 214519.916 | -8782.8451
185.72 | 11.2463 | 1.0341 |  | 8447.0594 | -202871.028 | 620950.977 | 6365552.65 | 1411462.72 | -41947.0499 | 102711.1 | -27440.0464 | 273244.785 | 397608.993 | 1602680.38 | -24781.2521 | 41473.0401 | -5510.6696 | 62985.1794 | 40228.011 | 228877.892 | -7757.9769
185.92 | 11.2206 | 1.0341 |  | 25761.5472 | -165671.267 | 638843.217 | 5588647.87 | 1700869.42 | -38967.6768 | 96870.6257 | -19514.0036 | 276975.141 | 306934.724 | 1599399.86 | -29829.8315 | 44085.3842 | -3714.741 | 63626.1012 | 34286.2104 | 257639.544 | -10336.9548
186.12 | 11.2119 | 1.0341 |  | 51191.0152 | -129986.744 | 643185.207 | 4737314.27 | 2062332.59 | -43762.4184 | 88027.7379 | -11094.0642 | 277362.566 | 251402.735 | 1531082.97 | -30422.2123 | 43724.3856 | -3790.5406 | 63595.006 | 36490.4398 | 259492.23 | -9566.7761
186.32 | 11.2314 | 1.0341 |  | 88473.8224 | -111184.55 | 643263.143 | 4235675.91 | 2701092.07 | -41729.5778 | 84371.0424 | -1378.0361 | 276297.501 | 126410.793 | 1430617.38 | -22500.9696 | 39833.2879 | -1258.6322 | 62822.8259 | 24262.8304 | 241139.871 | -7204.1482
186.52 | 11.2251 | 1.0341 |  | 130431.492 | -110588.843 | 641406.471 | 4282385.37 | 3714181.21 | -48985.4834 | 97390.0891 | 9727.7856 | 277335.565 | -43078.8416 | 1398665.15 | -25687.1857 | 30616.9765 | 3010.5522 | 63243.2515 | 2829.1529 | 169447.694 | -6944.3403
186.72 | 11.2125 | 1.0341 |  | 162163.71 | -94497.0263 | 622414.761 | 4089863.84 | 4398156.31 | -51036.2568 | 102796.153 | 17372.8675 | 275125.478 | -121642.552 | 1465576.17 | -31214.549 | 32912.6501 | 3925.5184 | 63608.9934 | -1199.9692 | 187927.212 | -8937.5216
186.92 | 11.2372 | 1.0341 |  | 177169.49 | -53153.6049 | 598790.674 | 3208599.9 | 4557791.36 | -49914.0737 | 90723.3368 | 23998.359 | 268461.044 | -157297.063 | 1468027.24 | -30836.5923 | 39514.2734 | 3466.4293 | 62213.7194 | 2787.414 | 229228.009 | -10444.4163
187.12 | 11.2278 | 1.0341 |  | 187048.582 | -39518.077 | 569130.737 | 2822559.93 | 4746599.68 | -47046.7518 | 87694.874 | 29081.3154 | 261963.732 | -238554.396 | 1405666.14 | -26179.1257 | 37414.7694 | 5270.8627 | 60842.0474 | -5605.7461 | 219834.775 | -7284.8252
187.32 | 11.2223 | 1.0341 |  | 206344.934 | -34033.139 | 536994.584 | 2774591.58 | 5083030.45 | -48584.7553 | 87610.3004 | 31542.2186 | 255513.118 | -250432.057 | 1381616.22 | -24857.7506 | 37572.061 | 4771.141 | 60128.9043 | -3571.7074 | 218559.319 | -6964.4273
187.52 | 11.2399 | 1.0341 |  | 213166.775 | -32809.6883 | 503643.117 | 2869713.07 | 5354124.46 | -43260.7747 | 95787.4093 | 33401.2422 | 246847.987 | -271988.921 | 1525721.56 | -24358.9439 | 40688.0088 | 5208.8564 | 58099.133 | -6720.3325 | 225653.471 | -7378.1476
187.72 | 11.2387 | 1.0341 |  | 215534.105 | -50645.1978 | 462697.209 | 3483497.2 | 5614492.59 | -40829.3951 | 109034.852 | 31903.0771 | 239356.069 | -284143.858 | 1694849.52 | -25804.0015 | 42125.6545 | 6616.6425 | 57617.1019 | -15898.2997 | 228179.64 | -7519.1981
187.92 | 11.2411 | 1.0341 |  | 217943.848 | -74401.577 | 428853.709 | 4203320.13 | 5735421.39 | -45344.6974 | 117641.069 | 27422.4642 | 231896.782 | -210724.51 | 1771110.51 | -28066.496 | 45379.8814 | 4107.679 | 56233.7689 | -1021.4164 | 256524.213 | -9253.3559
188.12 | 11.2734 | 1.0341 |  | 207700.388 | -117793.768 | 405884.984 | 5235141.62 | 5593204.78 | -37558.9525 | 125465.466 | 19586.3219 | 228901.481 | -139563.58 | 1846032.59 | -24350.1012 | 46738.7595 | 2951.4656 | 56593.9973 | 92.4193 | 242788.151 | -5057.7077
188.32 | 11.2898 | 1.0341 |  | 174313.468 | -127122.215 | 370554.856 | 5710089.77 | 5107073.34 | -39096.7989 | 129549.989 | 12168.3069 | 218609.456 | -346.1158 | 2115033.16 | -30673.7506 | 56118.9632 | -351.9127 | 54548.4009 | 16214.1863 | 299293.894 | -8622.952
188.52 | 11.2885 | 1.0341 |  | 143546.56 | -136528.305 | 352811.347 | 5991420.33 | 4382929.17 | -34970.7593 | 123084.858 | 1385.6756 | 212835.52 | 174695.039 | 2284299.28 | -26787.5557 | 67535.8263 | -4974.1409 | 53611.615 | 43004.4617 | 394287.223 | -7768.1729
188.72 | 11.3174 | 1.0341 |  | 118069.84 | -164168.499 | 337666.276 | 6782772.71 | 4000512.97 | -49925.1554 | 133519.511 | -8552.4335 | 206617.869 | 313057.718 | 2431628.09 | -39071.5047 | 70804.8716 | -7751.7375 | 51363.6604 | 59416.6799 | 406985.248 | -11432.0786
188.92 | 11.3439 | 1.0341 |  | 87543.0927 | -202652.808 | 338799.669 | 7350658.45 | 3478143.66 | -48353.3189 | 134764.453 | -15032.778 | 208407.14 | 314649.886 | 2271857.25 | -35395.8884 | 63522.8261 | -6032.4528 | 51919.414 | 49180.4508 | 369318.466 | -10191.4524
189.12 | 11.3457 | 1.0341 |  | 54034.3739 | -206145.8 | 348561.47 | 7294298.97 | 2715044.35 | -35527.9075 | 127673.649 | -23339.1278 | 212256.013 | 403161.382 | 2177274.41 | -24525.3837 | 60852.1469 | -7513.0876 | 52757.1098 | 52549.2023 | 356521.787 | -6856.358
189.32 | 11.3696 | 1.0341 |  | 17743.3816 | -215607.516 | 362891.404 | 7456189.42 | 1945523.13 | -46429.2945 | 125052.976 | -32688.7431 | 216755.214 | 490609.776 | 2133699.76 | -34199.7262 | 59320.3689 | -8082.8705 | 54020.1506 | 55793.3495 | 344880.692 | -11057.1928
189.52 | 11.3909 | 1.0341 |  | -5698.8284 | -236028.713 | 392746.706 | 7410891.5 | 1328849.73 | -56031.8047 | 112612.591 | -36201.8188 | 224814.566 | 510862.476 | 1861634.1 | -35542.3966 | 52453.9466 | -8222.9184 | 54902.5134 | 55707.4364 | 305497.47 | -10497.3807
189.72 | 11.3962 | 1.0341 |  | -43369.0816 | -208707.938 | 420987.094 | 6659359.04 | 434725.832 | -33211.3223 | 97812.6813 | -41584.5512 | 231207.948 | 596704.038 | 1816624.22 | -20645.2075 | 54861.2855 | -10466.6136 | 56251.6386 | 62046.9104 | 312976.523 | -6812.8763
189.92 | 11.4383 | 1.0359 |  | -51458.6142 | -225711.049 | 459796.507 | 6922199.57 | 287544.888 | -41093.8708 | 98012.0554 | -43145.1465 | 240835.798 | 578920.268 | 1676513.33 | -27438.2718 | 47997.3637 | -9007.0609 | 57477.8124 | 59448.9069 | 293389.143 | -8505.2032
190.12 | 11.4659 | 1.1465 |  | -50576.9304 | -233882.737 | 499689.246 | 6978123.48 | 331823.109 | -46959.3325 | 101377.491 | -42580.1203 | 251705.347 | 544194.378 | 1573620.88 | -30409.6026 | 40953.5944 | -7382.3615 | 59597.5963 | 49034.312 | 245647.434 | -9333.4269
190.32 | 11.4787 | 1.2843 |  | -62228.3586 | -210374.46 | 539586.346 | 6498197.57 | 35806.0129 | -32133.9141 | 98831.9687 | -44042.3739 | 262724.864 | 552065.217 | 1571121.22 | -22938.2716 | 40127.0341 | -7005.8451 | 62190.3725 | 44098.3092 | 226372.308 | -7843.6484
190.52 | 11.5072 | 1.3074 |  | -49142.0034 | -204437.242 | 578158.848 | 6220725.7 | 132526.26 | -42952.5105 | 91455.8341 | -40906.8206 | 271533.366 | 562035.837 | 1498178.37 | -28201.8753 | 39370.82 | -8366.901 | 63549.9305 | 53996.355 | 227413.56 | -9051.2305
190.72 | 11.5192 | 1.3017 |  | -47985.9487 | -184488.872 | 611499.564 | 5697239.97 | 118103.173 | -34996.9988 | 83247.2771 | -36477.8483 | 278077.294 | 498511.229 | 1450030.43 | -25016.2747 | 41938.9262 | -7071.6569 | 64301.3568 | 47000.2193 | 241373.768 | -7812.6434
190.92 | 11.5184 | 1.2981 |  | -17503.7509 | -172114.904 | 637636.015 | 5457626.09 | 668164.289 | -40754.5116 | 84246.2435 | -29699.0342 | 283660.532 | 434154.141 | 1460595.08 | -27887.0316 | 42770.95 | -6204.1513 | 65364.4635 | 46145.2584 | 264093.965 | -9656.6889
191.12 | 11.5309 | 1.2976 |  | 18484.0154 | -163477.982 | 662212.955 | 5364809.5 | 1475623.1 | -42605.8382 | 92763.6076 | -20590.4549 | 288896.75 | 320188.117 | 1457955.45 | -29596.8205 | 37724.3204 | -3787.0678 | 65866.9393 | 35517.5556 | 226145.741 | -9254.0349
191.32 | 11.5217 | 1.2981 |  | 47543.9684 | -141978.368 | 671640.422 | 4970091.01 | 2097489.06 | -41830.3269 | 95027.9883 | -11139.0002 | 292241.442 | 200313.56 | 1468221 | -30706.2199 | 37413.0909 | -1430.7283 | 67079.1653 | 23575.378 | 215827.723 | -8789.831
191.52 | 11.5325 | 1.2988 |  | 75351.0292 | -106201.488 | 677677.166 | 4136116.66 | 2525393.31 | -45119.5732 | 84163.7116 | -1593.3383 | 293041.667 | 137946.224 | 1453846.41 | -31442.9907 | 41929.8008 | -1589.3529 | 67028.6939 | 26542.1395 | 245527.781 | -10202.2645
191.72 | 11.546 | 1.2933 |  | 98088.9513 | -73115.9308 | 671478.139 | 3350084.52 | 2887253.31 | -50810.3017 | 76800.3925 | 7441.9014 | 291100.209 | 22376.7547 | 1387964.46 | -32013.1675 | 40942.3334 | 884.8012 | 66503.449 | 15018.8874 | 246689.659 | -10374.5337
191.92 | 11.5263 | 1.2854 |  | 135077.592 | -61874.0333 | 657044.471 | 3025409.15 | 3548597.48 | -51091.1604 | 76268.7038 | 16181.7185 | 289201.636 | -86905.5912 | 1229679.83 | -27606.5056 | 33815.4103 | 2698.0011 | 66347.5654 | 6698.5716 | 204220.216 | -6697.6415
192.12 | 11.5338 | 1.2782 |  | 164183.409 | -47496.3717 | 638268.775 | 2647049.23 | 4066919.12 | -57317.9515 | 71370.7077 | 24068.9884 | 284344.799 | -172116.421 | 1184885.84 | -29289.8464 | 33867.1549 | 4162.3198 | 65312.5772 | -1233.1797 | 206203.652 | -8768.2458
192.32 | 11.5275 | 1.2702 |  | 183037.497 | -39179.7953 | 604206.809 | 2487836.38 | 4576931.35 | -57161.828 | 74902.4215 | 32175.347 | 276686.129 | -282385.117 | 1220322.85 | -27965.5686 | 33704.0655 | 6311.674 | 63898.0166 | -11053.7527 | 201398.839 | -8879.7746
192.52 | 11.4916 | 1.2631 |  | 207698.375 | -50794.1042 | 574568.356 | 2800321.17 | 5053789.52 | -57630.5809 | 79503.5855 | 34558.7806 | 272463.736 | -321502.573 | 1158803.53 | -29418.7567 | 29667.477 | 7065.3012 | 63931.8314 | -14305.5446 | 186852.238 | -8383.0056
192.72 | 11.4895 | 1.2567 |  | 210027.265 | -42705.9141 | 532491.389 | 2911372.38 | 5143299.72 | -44796.8228 | 91181.149 | 31480.5994 | 262611.256 | -264475.371 | 1324422.49 | -23140.124 | 31051.0982 | 5577.1912 | 62165.0721 | -7806.5515 | 178217.189 | -5938.1175
192.92 | 11.4811 | 1.2493 |  | 213167.119 | -67774.2795 | 494558.489 | 3744665.81 | 5385262.38 | -42889.2348 | 103826.889 | 28414.5086 | 253472.63 | -255261.384 | 1476235.72 | -26892.5726 | 35825.2392 | 5871.216 | 60407.9806 | -9479.9691 | 209900.93 | -8899.2512
193.12 | 11.4401 | 1.2426 |  | 217883.264 | -103825.118 | 460717.123 | 4674336.87 | 5535447.12 | -46301.6892 | 116712.848 | 21709.1525 | 246169.778 | -184193.009 | 1612614.24 | -28766.8837 | 36851.4188 | 4966.9836 | 59520.7111 | -6203.4122 | 217183.645 | -8668.396
193.32 | 11.428 | 1.2372 |  | 199055.716 | -104139.711 | 417776.407 | 5019096.95 | 5306492.65 | -36451.2332 | 125895.611 | 15023.9553 | 233978.301 | -61040.8346 | 1857945.17 | -27913.7759 | 44412.7194 | 1890.0054 | 57350.356 | 8600.6343 | 247118.726 | -9084.1872
193.52 | 11.4003 | 1.2316 |  | 161420.326 | -101597.088 | 385304.954 | 5055301.46 | 4680031.53 | -32650.1491 | 123322.705 | 9789.5851 | 223332.176 | 8940.9701 | 2028984.65 | -27895.2393 | 54472.8744 | 138.2015 | 55383.9072 | 14598.7415 | 299800.396 | -8928.4609
193.72 | 11.3513 | 1.2266 |  | 139757.343 | -120989.729 | 361765.573 | 5593914.91 | 4284474.5 | -33112.7809 | 127291.455 | 1079.3701 | 217517.373 | 151949.473 | 2137736.89 | -26002.2691 | 56877.7209 | -3455.1304 | 54322.6798 | 33235.5277 | 320930.004 | -6613.6276
193.92 | 11.3273 | 1.2222 |  | 114571.44 | -164659.327 | 345132.414 | 6766277.12 | 3916518.2 | -38585.3362 | 139523.549 | -11123.4919 | 212407.47 | 244397.578 | 2232464.85 | -32273.0275 | 57454.0689 | -3443.0311 | 53175.4057 | 30038.1752 | 317783.506 | -9293.0502
194.12 | 11.2881 | 1.2178 |  | 87971.4814 | -190260.504 | 337347.358 | 7373173.44 | 3464258.18 | -40943.6943 | 147273.09 | -20596.7266 | 209876.009 | 346970.682 | 2271738.5 | -34936.5618 | 55878.8883 | -4874.9096 | 52832.8256 | 38118.5554 | 314469.714 | -11161.8566
194.32 | 11.2428 | 1.2145 |  | 38047.8257 | -186232.885 | 337779.626 | 7146456.2 | 2372578.83 | -36697.2209 | 133622.856 | -29718.9551 | 209009.431 | 461370.37 | 2220181.26 | -30453.2458 | 60351.2042 | -7823.3843 | 52689.2083 | 52481.1779 | 343745.654 | -8884.4153
194.52 | 11.2178 | 1.2109 |  | -4368.3448 | -178400.698 | 349200.54 | 6602034.78 | 1272756.96 | -45154.4278 | 111398.269 | -36172.4204 | 208270.686 | 568803.197 | 2093520.52 | -36338.6617 | 61615.8949 | -10246.9786 | 51826.6483 | 65094.9652 | 352512.452 | -12747.7129
194.72 | 11.1684 | 1.2064 |  | -32617.5993 | -191344.377 | 368863.376 | 6386088.91 | 574027.598 | -40380.1913 | 98124.4287 | -39578.5249 | 213032.317 | 565179.076 | 1768239.18 | -27938.129 | 51025.4407 | -9571.3514 | 52162.1761 | 61083.9965 | 300521.38 | -7809.9981
194.92 | 11.1172 | 1.2021 |  | -58411.6537 | -185799.237 | 393900.208 | 5906885.28 | -88876.9512 | -31651.3746 | 82768.5487 | -42210.0625 | 218669.309 | 594366.274 | 1594396.38 | -21741.5364 | 48805.9448 | -10250.4758 | 53056.4205 | 62739.6174 | 291728.463 | -6553.5253
195.12 | 11.0845 | 1.1985 |  | -79130.9892 | -186316.544 | 423171.627 | 5698269.76 | -566534.9 | -31358.1507 | 73158.0864 | -43984.0791 | 224296.302 | 598555.438 | 1496818.52 | -23069.482 | 48673.1239 | -9854.5487 | 53483.662 | 62764.7736 | 307901.732 | -7712.7
195.32 | 11.0305 | 1.1951 |  | -87342.9884 | -191055.477 | 452878.602 | 5852405.29 | -696296.883 | -34607.9876 | 79732.7946 | -46828.8513 | 231597.744 | 617476.495 | 1476547.49 | -27652.5912 | 42659.1765 | -9399.6614 | 55166.459 | 59243.9393 | 264832.309 | -8874.6492
195.52 | 10.9919 | 1.1925 |  | -78861.153 | -205725.549 | 489543.813 | 6105041.78 | -622476.773 | -36946.0074 | 81209.6255 | -48655.9199 | 239842.233 | 634610.002 | 1376292.72 | -27101.527 | 38304.4641 | -9657.6119 | 56707.1149 | 57785.0125 | 226311.456 | -8673.4029
195.72 | 10.9555 | 1.1898 |  | -80702.4105 | -195475.784 | 519304.824 | 5804309.61 | -684780.294 | -34108.2617 | 77090.8428 | -46511.6857 | 244464.456 | 604441.775 | 1341392.95 | -25800.7767 | 37462.7797 | -8823.0467 | 56973.9684 | 53105.1736 | 220134.167 | -9589.1816
195.92 | 10.8875 | 1.1871 |  | -65821.574 | -187734.273 | 547608.13 | 5463618.42 | -531656.169 | -34710.758 | 67811.586 | -41863.4318 | 250321.295 | 564451.163 | 1244775.38 | -21362.6446 | 37528.4937 | -8836.4437 | 58246.2023 | 55733.8031 | 224426.386 | -7345.394
196.12 | 10.8404 | 1.1852 |  | -48247.3492 | -172016.38 | 570965.259 | 5124765.5 | -213623.959 | -35027.746 | 65466.335 | -36053.8643 | 252962.257 | 502712.528 | 1192531.17 | -23794.9413 | 36798.8153 | -7814.6757 | 57852.1623 | 52612.3131 | 230003.141 | -8740.3647
196.32 | 10.7941 | 1.1832 |  | -19333.7948 | -159056.346 | 585613.621 | 4882887.13 | 399225.81 | -32729.1419 | 73182.0173 | -28817.4562 | 255255.795 | 397942.268 | 1174322.39 | -23033.331 | 32616.0037 | -5450.7968 | 58261.2428 | 40834.5766 | 204003.27 | -8323.6482
196.52 | 10.7266 | 1.1815 |  | 11577.736 | -148412.021 | 601527.9 | 4697806.51 | 1049086.2 | -36331.8054 | 76790.7388 | -20634.8031 | 258532.234 | 300534.952 | 1170464.43 | -22548.7122 | 30971.3561 | -3760.9608 | 58870.8799 | 33322.8784 | 189077.223 | -7106.9516
196.72 | 10.6831 | 1.1806 |  | 44917.5093 | -139956.339 | 601831.879 | 4642446.43 | 1733488.68 | -42993.4917 | 80045.6764 | -13491.1808 | 257681.946 | 229628.539 | 1225431.29 | -26353.444 | 32835.9951 | -2704.6164 | 58879.5694 | 27526.2287 | 191935.221 | -8382.3149
196.92 | 10.6464 | 1.1801 |  | 81006.7822 | -130571.942 | 600983.708 | 4499044.14 | 2458617.89 | -42887.3904 | 81629.4456 | -4550.4995 | 255772.443 | 131365.804 | 1235333.87 | -25265.1267 | 33232.4974 | -1279.8343 | 58211.1572 | 22470.4971 | 195370.715 | -7730.9125
197.12 | 10.5964 | 1.1792 |  | 114947.953 | -118636.527 | 589541.352 | 4302029.14 | 3191759.17 | -49306.795 | 87100.2969 | 3809.7657 | 252298.45 | 24097.2444 | 1244843.19 | -28700.774 | 30237.8738 | 1193.147 | 57464.9475 | 9605.9361 | 177209.029 | -8817.9633
197.32 | 10.5604 | 1.1785 |  | 137118.31 | -89586.1657 | 569848.592 | 3714170.76 | 3591161.68 | -39776.8144 | 84811.9518 | 10749.7787 | 247476.391 | -65363.11 | 1230449.34 | -23088.0933 | 29411.2188 | 3109.5907 | 56631.1713 | 421.6337 | 175105.126 | -7400.3188
197.52 | 10.5249 | 1.1779 |  | 157019.403 | -57813.2634 | 547083.264 | 3040966.66 | 3977104.4 | -41334.9775 | 81033.7575 | 19135.7379 | 240914.61 | -121025.635 | 1258939.3 | -21765.4831 | 30920.4104 | 3089.8436 | 55311.1487 | 1715.3009 | 179764.432 | -7571.7369
197.72 | 10.4677 | 1.1776 |  | 173998.596 | -53862.3487 | 518765.185 | 2955718.98 | 4320717.17 | -40964.1581 | 81011.3513 | 23640.8689 | 234357.789 | -199493.104 | 1245172.31 | -22560.1856 | 30666.6678 | 5065.9713 | 54251.0593 | -9737.3332 | 173362.597 | -7074.9749
197.92 | 10.4273 | 1.178 |  | 192607.475 | -36411.7446 | 483405.221 | 2737248.8 | 4709016.2 | -41617.8423 | 87606.5063 | 26927.2129 | 225518.477 | -201418.085 | 1296170.32 | -24148.8852 | 29588.0462 | 4251.6426 | 52796.7282 | -4168.9209 | 161372.249 | -6990.186
198.12 | 10.3935 | 1.1782 |  | 192314.378 | -34847.8904 | 444703.428 | 2698398.56 | 4771886.97 | -42017.3121 | 85652.2525 | 29186.355 | 214924.805 | -256721.363 | 1326928.89 | -22450.6836 | 32293.3492 | 5751.9721 | 50419.1903 | -11263.1744 | 183428.187 | -7108.8267
198.32 | 10.3454 | 1.1779 |  | 203206.162 | -43149.9123 | 412389.547 | 3090741.42 | 5039505.09 | -32359.5151 | 95188.8257 | 27019.0863 | 208895.947 | -247692.228 | 1357859.25 | -17856.3894 | 31353.0017 | 5699.371 | 49912.3378 | -10113.5863 | 186008.75 | -5084.9786
198.52 | 10.3109 | 1.1776 |  | 204610.278 | -71097.6714 | 376249.656 | 3951976.93 | 5198629.15 | -32466.0441 | 109291.832 | 21560.6455 | 199921.143 | -187580.981 | 1518657.73 | -21425.7061 | 34623.5344 | 4597.8777 | 48034.3967 | -5742.2437 | 194143.805 | -7831.4826
198.72 | 10.2851 | 1.177 |  | 196962.249 | -90470.402 | 339789.418 | 4627897.25 | 5150918.08 | -32469.331 | 118707.987 | 15347.3235 | 190777.376 | -98204.9439 | 1706663.09 | -23254.7021 | 40383.8694 | 2621.3541 | 47044.5109 | 1169.9352 | 220705.03 | -7007.5516
198.92 | 10.2496 | 1.1762 |  | 172993.785 | -90408.4389 | 304022.221 | 4741719.24 | 4778649.73 | -31381.9492 | 118122.96 | 11336.5231 | 179060.932 | -1063.4977 | 1911643.6 | -23427.5647 | 51240.0535 | -683.0335 | 44630.5723 | 18135.856 | 282471.334 | -6915.131
199.12 | 10.2172 | 1.1763 |  | 152450.851 | -103733.514 | 279376.976 | 4985440.39 | 4359527.24 | -37424.5531 | 112990.658 | 6318.2629 | 171214.508 | 65252.9016 | 1960590.68 | -27977.0613 | 55537.6659 | -1888.4143 | 42862.2339 | 27134.0424 | 325479.326 | -9322.2506
199.32 | 10.1823 | 1.1767 |  | 126237.773 | -108199.798 | 258851.79 | 5015382.62 | 3875884.79 | -33167.5579 | 111928.926 | 1625.1919 | 165654.967 | 129360.736 | 1874472.82 | -28790.8656 | 52590.2235 | -3710.0084 | 41386.1197 | 37106.3114 | 303958.489 | -8540.6021
199.52 | 10.143 | 1.1771 |  | 89416.4539 | -122004.814 | 250581.354 | 4979028.78 | 3007656.05 | -31865.243 | 102443.308 | -6256.7208 | 164611.378 | 152530.277 | 1687260.4 | -19898.5364 | 46609.7689 | -2481.8793 | 41541.2601 | 27033.2947 | 269959.598 | -4883.1842
199.72 | 10.1034 | 1.1782 |  | 56949.4113 | -134559.375 | 241896.993 | 5219114.46 | 2373807.74 | -24394.3286 | 100815.827 | -14310.2242 | 162031.831 | 257319.971 | 1658878.17 | -17303.0518 | 44298.4637 | -4418.4574 | 40859.8544 | 33324.5806 | 251992.287 | -5308.9428
199.92 | 10.0705 | 1.1798 |  | 34167.0041 | -170101.026 | 245616.189 | 5924338.83 | 1877610.45 | -33462.7452 | 101739.172 | -23997.8513 | 163298.952 | 361206.145 | 1647831.21 | -21777.7332 | 43076.2569 | -5772.6187 | 41288.9764 | 37107.8377 | 243097.207 | -7208.7357
200.12 | 10.0538 | 1.1819 |  | 10165.6442 | -195565.013 | 253198.496 | 6470576.01 | 1458695.09 | -36649.2784 | 103578.757 | -30541.9896 | 163837.535 | 424499.9 | 1599689.04 | -21438.9284 | 39081.733 | -6434.6704 | 40950.3865 | 39464.446 | 211032.475 | -6720.9977
200.32 | 10.0527 | 1.1842 |  | -15756.1551 | -207754.364 | 268932.805 | 6554120.81 | 930763.819 | -32094.4994 | 97299.4107 | -34845.8271 | 166991.853 | 439741.31 | 1500905.61 | -22675.4965 | 38811.3897 | -6134.5562 | 41550.5759 | 36706.8629 | 215356.65 | -8130.7988
200.52 | 10.0604 | 1.186 |  | -34580.3661 | -205951.426 | 290037.705 | 6372664.53 | 548128.028 | -26348.6414 | 91454.4616 | -36788.1289 | 172338.514 | 458820.556 | 1404174.31 | -19635.1736 | 36823.3211 | -6679.7644 | 42414.1888 | 39427.9373 | 206449.124 | -6484.7784
200.72 | 10.0552 | 1.1873 |  | -56695.4089 | -199266.647 | 320987.282 | 6140186.16 | 29198.1632 | -19466.1643 | 91448.1676 | -43032.496 | 180879.655 | 509706.659 | 1374814.61 | -15588.2307 | 35224.5056 | -6948.3943 | 44051.0428 | 41027.0793 | 204938.855 | -5972.4259
200.92 | 10.0599 | 1.1889 |  | -65114.8683 | -205907.365 | 352622.942 | 6147771.72 | -253278.205 | -34276.0118 | 87687.8439 | -46124.8614 | 188226.308 | 587896.612 | 1366463.74 | -21677.6836 | 35646.0136 | -9111.5529 | 45580.3357 | 52033.9796 | 202262.439 | -7760.5803
201.12 | 10.0574 | 1.1904 |  | -76504.1723 | -208908.361 | 381694.656 | 6084106.94 | -512225.096 | -32678.4143 | 80176.5135 | -46236.9234 | 193693.229 | 583973.851 | 1306516.79 | -20097.1883 | 36182.932 | -9028.0043 | 45895.896 | 54089.9588 | 217897.304 | -7387.1957
201.32 | 10.0198 | 1.1925 |  | -78934.769 | -203736.473 | 412752.64 | 5924869.88 | -655708.393 | -27534.2224 | 78150.0018 | -47598.473 | 200996.223 | 603876.507 | 1308926.62 | -17922.5456 | 36338.4385 | -9177.1576 | 47681.9606 | 52300.6918 | 212741.786 | -7065.6587
201.52 | 10.0022 | 1.1957 |  | -58485.2996 | -222924.622 | 446489.118 | 6337996.52 | -220662.403 | -35702.189 | 85629.6964 | -45680.4482 | 207717.899 | 579199.856 | 1279529.79 | -22941.8821 | 30963.7158 | -8396.9237 | 48303.3596 | 49440.8669 | 179973.973 | -8065.3011
201.72 | 9.98 | 1.1979 |  | -55843.707 | -198236.977 | 468165.313 | 5920948.18 | -82503.8532 | -27253.816 | 85810.8375 | -40787.2041 | 212011.927 | 533488.648 | 1374298.87 | -18622.7681 | 36447.2347 | -8209.9843 | 49431.4354 | 48464.9077 | 199320.633 | -6174.7421
201.92 | 9.9633 | 1.1995 |  | -41060.1958 | -174093.585 | 493147.749 | 5584358.6 | 205960.989 | -23444.8754 | 89450.1945 | -37452.1969 | 216566.235 | 514459.622 | 1505496.16 | -20122.2339 | 39847.8561 | -7919.1809 | 50072.7342 | 48102.7678 | 220457.881 | -7491.2253
202.12 | 9.9847 | 1.2005 |  | 5036.7562 | -197982.684 | 521092.633 | 6179679.19 | 1202406.65 | -32062.2583 | 101972.282 | -31850.7433 | 223665.301 | 426197.853 | 1438428.02 | -16589.0755 | 33888.3934 | -6006.637 | 50984.7422 | 40068.59 | 186498.796 | -5113.3776
202.32 | 10.0239 | 1.2 |  | 33591.7473 | -201087.543 | 536774.4 | 6452054.96 | 1957819.26 | -33131.7153 | 111177.37 | -23725.5611 | 228562.888 | 286490.324 | 1504851.82 | -20340.9658 | 32925.4081 | -2189.6571 | 52006.595 | 21840.6993 | 180627.222 | -5692.4339
202.52 | 10.0442 | 1.1991 |  | 51923.1786 | -164012.54 | 548021.046 | 5741449.41 | 2298045.95 | -29488.3639 | 105587.71 | -15174.2151 | 231384.998 | 243031.784 | 1620250.58 | -22954.4484 | 41177.7705 | -2890.2141 | 53155.4665 | 26306.0228 | 224484.452 | -8485.4674
202.72 | 10.0767 | 1.1986 |  | 82163.671 | -141899.158 | 551301.041 | 5244871.75 | 2813907.09 | -30545.8309 | 99795.3477 | -7036.0456 | 231617.455 | 197634.979 | 1631277.48 | -21109.4999 | 45476.4242 | -3791.8532 | 53039.8505 | 35070.5717 | 260423.567 | -6120.3949
202.92 | 10.1117 | 1.1976 |  | 110649.585 | -118911.331 | 544863.97 | 4887250.05 | 3386660.63 | -33273.6255 | 103818.979 | -539.6144 | 229257.946 | 115600.657 | 1689462.32 | -23253.116 | 45907.3869 | -1779.7148 | 52068.2861 | 25190.8431 | 262623.606 | -8200.4835
203.12 | 10.1103 | 1.1964 |  | 148542.692 | -132702.773 | 540255.365 | 4972495.89 | 4153598.85 | -48369.6785 | 106768.604 | 8882.6768 | 230729.147 | -36327.7345 | 1524204.6 | -27893.7613 | 36527.6941 | 2039.8938 | 52877.8915 | 6563.4415 | 201757.947 | -7619.8756
203.32 | 10.0933 | 1.1968 |  | 158768.24 | -92340.9613 | 520418.544 | 3926828.45 | 4162149.46 | -39833.3132 | 90613.0502 | 16075.8951 | 226059.324 | -103496.814 | 1386450.8 | -22267.5146 | 36797.2371 | 2550.297 | 51927.8618 | 4814.8297 | 214611.155 | -7248.7168
203.52 | 10.1095 | 1.1979 |  | 167052.582 | -43445.5205 | 495406.627 | 2784825.67 | 4157542.5 | -35838.5391 | 79667.5949 | 21907.5839 | 219501.383 | -142600.873 | 1331238.05 | -17931.3064 | 36991.6966 | 2512.9034 | 50762.577 | 6901.7383 | 225073.722 | -5660.1208
203.72 | 10.1062 | 1.1982 |  | 186303.477 | -45369.5052 | 471506.892 | 2794824.77 | 4655458.64 | -35991.6366 | 84639.0008 | 28071.8701 | 214221.509 | -256342.396 | 1254328.25 | -17387.4522 | 30662.0385 | 5671.0534 | 49195.7328 | -9899.4944 | 183073.772 | -4110.0635
203.92 | 10.1059 | 1.1989 |  | 209851.144 | -56053.6339 | 445545.832 | 3168242.48 | 5200442.35 | -40273.3297 | 95394.6385 | 30253.8041 | 211253.828 | -284030.553 | 1315542.01 | -21213.048 | 27926.2384 | 6562.0505 | 49890.2047 | -15700.5511 | 155533.606 | -4959.1208
204.12 | 10.1373 | 1.1993 |  | 216017.812 | -50492.8994 | 409039.636 | 3388986.84 | 5452317.27 | -30695.0517 | 104693.564 | 29224.1624 | 201866.369 | -270992.333 | 1484138.87 | -17825.6311 | 32469.1632 | 6491.611 | 47593.9138 | -16325.0859 | 171164.208 | -6439.1017
204.32 | 10.1803 | 1.1986 |  | 223956.036 | -82911.3518 | 383225.378 | 4235903.64 | 5736636.19 | -31865.568 | 116600.234 | 26139.0506 | 198910.125 | -272368.728 | 1569440.43 | -19414.2764 | 33144.0995 | 7181.0367 | 48155.5127 | -20143.8039 | 182124.703 | -5567.8712
204.52 | 10.201 | 1.1981 |  | 223965.251 | -97179.7607 | 351551.507 | 4831203.02 | 5820953.32 | -36843.6883 | 126391.245 | 21486.1182 | 191934.876 | -172066.882 | 1748891.77 | -24278.5443 | 38389.8026 | 4515.9238 | 46995.7396 | -8172.7356 | 201840.863 | -7294.2653
204.72 | 10.2313 | 1.1985 |  | 202255.966 | -99808.9114 | 320374.552 | 4985893.48 | 5441515.2 | -34313.2729 | 124069.659 | 17139.3031 | 182760.066 | -87480.5847 | 1912505.65 | -24802.2213 | 48056.6008 | 1857.5595 | 45342.2495 | 5056.5462 | 259421.6 | -7851.4406
204.92 | 10.2773 | 1.1986 |  | 182752.107 | -96888.9081 | 295338.868 | 4936960.76 | 5152926.96 | -33326.6396 | 122438.381 | 15563.5957 | 175858.902 | -48961.6366 | 1950492.48 | -26025.3472 | 49331.8174 | 747.1669 | 43749.9219 | 11503.1521 | 271863.976 | -8058.5433
205.12 | 10.2924 | 1.1984 |  | 155158.999 | -101909.234 | 278774.955 | 4724571.28 | 4526123.88 | -37184.3314 | 106366.162 | 13435.4496 | 173417.122 | -28113.3908 | 1854052.75 | -22924.8214 | 51355.8452 | -101.0489 | 43488.2537 | 16816.6186 | 290804.755 | -6082.911
205.32 | 10.3133 | 1.1996 |  | 114037.602 | -93273.5372 | 268762.818 | 4300820.46 | 3577845.32 | -30090.5355 | 94997.5455 | 6325.5905 | 171138.746 | 60950.136 | 1764862.81 | -19998.2129 | 51058.7709 | -1753.4919 | 42622.5457 | 25626.092 | 300445.649 | -6692.545
205.52 | 10.345 | 1.2015 |  | 95713.2163 | -133189.995 | 265293.407 | 5096707.52 | 3188719.6 | -33376.3005 | 102078.976 | -3896.2285 | 173015.906 | 113413.957 | 1595796.05 | -18994.6939 | 39943.116 | -738.302 | 43214.4008 | 17288.6425 | 240690.439 | -5380.5488
205.72 | 10.3644 | 1.2031 |  | 72023.7164 | -168902.507 | 267901.942 | 5785395.26 | 2778833.6 | -39524.9325 | 105719.498 | -11003.1126 | 175101.528 | 166792.034 | 1520392.13 | -26537.9385 | 36427.2263 | -1344.6257 | 43733.5963 | 17629.9717 | 207304.239 | -7654.6351
205.92 | 10.3939 | 1.2048 |  | 28579.6757 | -163270.046 | 275324.048 | 5499506.36 | 1850727.75 | -31881.6469 | 96343.6802 | -18158.036 | 176852.47 | 258695.843 | 1498994.85 | -22757.6504 | 38517.0387 | -3288.5368 | 44338.7452 | 26881.5744 | 218247.478 | -8445.3674
206.12 | 10.4408 | 1.2062 |  | 2040.2312 | -174118.973 | 291403.32 | 5642306.36 | 1236895.53 | -27615.1731 | 94798.8186 | -27264.2052 | 181824.213 | 339086.637 | 1395533.33 | -19263.4508 | 34515.964 | -4062.6025 | 45125.2649 | 28347.1187 | 197565.309 | -6845.8199
206.32 | 10.4936 | 1.2068 |  | -14365.6358 | -193256.022 | 319287.417 | 5893636.17 | 914277.908 | -36462.0821 | 92897.1961 | -30637.1951 | 188898.928 | 395481.624 | 1367817.41 | -21841.4548 | 33414.0509 | -5403.362 | 46445.921 | 34978.6007 | 189159.55 | -7169.2783
206.52 | 10.5418 | 1.2073 |  | -40825.089 | -199015.017 | 344850.543 | 6053221.81 | 494235.304 | -28986.5111 | 92184.921 | -34928.8641 | 195869.874 | 407685.394 | 1381339.13 | -20765.0694 | 35496.1724 | -4709.0465 | 47640.7268 | 31300.9604 | 205704.428 | -8134.3855
206.72 | 10.5822 | 1.2077 |  | -43412.2003 | -227729.673 | 383971.037 | 6574031.57 | 376513.347 | -39099.5799 | 93929.5087 | -39294.1997 | 208170.999 | 468759.009 | 1344864.41 | -24334.8188 | 31645.3745 | -5678.8786 | 50379.6747 | 36254.1091 | 190821.319 | -8677.5932
206.92 | 10.6254 | 1.2085 |  | -54267.2207 | -230390.475 | 424203.182 | 6714403.43 | 102179.008 | -32947.0818 | 96836.8625 | -44863.1917 | 217942.569 | 552210.427 | 1388885.38 | -20769.4426 | 31481.356 | -7365.8959 | 52115.9101 | 45009.8252 | 186212.817 | -8130.0178
207.12 | 10.6618 | 1.2091 |  | -59504.4058 | -250042.311 | 454937.584 | 7179653.14 | -26577.7156 | -39180.9853 | 96792.8837 | -48325.0916 | 225522.801 | 565028.296 | 1411507.55 | -21879.2775 | 35257.7371 | -7153.2613 | 53403.2185 | 42902.0112 | 205069.388 | -8644.4224
207.32 | 10.693 | 1.2096 |  | -39762.9035 | -255405.312 | 490133.868 | 7362474.02 | 383189.669 | -44308.7151 | 102227.754 | -45031.1415 | 232959.275 | 579660.832 | 1425181.98 | -23743.2782 | 34409.6917 | -8971.7629 | 54626.4933 | 55836.5791 | 198744.997 | -8255.4241
207.52 | 10.7152 | 1.2096 |  | -37097.079 | -254669.466 | 526019.882 | 7348400.31 | 504530.989 | -42379.6371 | 100627.501 | -41095.4863 | 240954.399 | 485390.683 | 1452677.95 | -22782.8157 | 36506.5417 | -5847.0327 | 55658.7437 | 38925.6451 | 209985.594 | -8151.4684
207.72 | 10.7391 | 1.2098 |  | -11599.2995 | -237021.822 | 552649.675 | 7122683.89 | 999470.757 | -37864.7503 | 108143.172 | -37300.8718 | 248290.75 | 475671.581 | 1558056.06 | -20163.212 | 38911.391 | -6567.7187 | 57818.5278 | 42866.5984 | 217669.565 | -7429.2035
207.92 | 10.7968 | 1.2095 |  | 20667.5197 | -242475.42 | 584036.127 | 7568487.01 | 1785584.76 | -32775.6221 | 126134.526 | -34584.4809 | 255760.029 | 406190.701 | 1669636.3 | -17604.0398 | 36585.5584 | -4305.2055 | 58333.0123 | 34056.5387 | 207558.179 | -6710.9916
208.12 | 10.8362 | 1.2079 |  | 59098.5576 | -260185.11 | 600521.172 | 8337933.65 | 2705927.24 | -43472.8552 | 147422.399 | -31851.2993 | 264122.541 | 349666.312 | 1839672.81 | -26648.4432 | 37354.5415 | -2346.527 | 61386.8967 | 22558.8294 | 205356.287 | -7160.3972
208.32 | 10.879 | 1.2065 |  | 78703.7778 | -218198.22 | 610765.676 | 7610369.05 | 3019673.88 | -41505.0815 | 141320.179 | -24958.0502 | 262819.395 | 359213.947 | 1998117.98 | -30459.6244 | 47466.4482 | -4512.2854 | 60437.1205 | 37702.9203 | 262598.943 | -12002.0254
208.52 | 10.9376 | 1.2054 |  | 99962.3137 | -183078.514 | 612555.115 | 6775918.19 | 3378739.04 | -27532.0187 | 127255.859 | -13858.6626 | 261515.74 | 290283.461 | 2057083 | -14711.1977 | 55747.9133 | -5275.8958 | 60050.9468 | 42565.9493 | 317098.695 | -4821.2317
208.72 | 10.978 | 1.2041 |  | 149002.454 | -188280.588 | 607373.89 | 7022273.56 | 4502704.41 | -39991.7007 | 139680.122 | -2930.0596 | 261253.753 | 139571.178 | 2082382.4 | -24583.56 | 51645.9715 | -1556.0121 | 59957.5429 | 26453.6447 | 286167.79 | -7931.8365
208.92 | 11.0075 | 1.2034 |  | 187699.707 | -183160.569 | 600897.014 | 7014186.27 | 5348365.22 | -46833.1244 | 149512.55 | 4526.844 | 263366.276 | 17170.8167 | 2117049.5 | -25962.7567 | 47730.6651 | 1975.8706 | 61026.1718 | 6758.8548 | 253382.304 | -6573.6599
209.12 | 11.0305 | 1.2031 |  | 194114.093 | -134332.304 | 576089.952 | 6113012.02 | 5444608.12 | -32444.4491 | 146118.483 | 9098.5618 | 257620.633 | 3493.0486 | 2260417.51 | -23540.0143 | 56799.0485 | 936.568 | 60668.7334 | 11835.3356 | 303407.596 | -8624.8667
209.32 | 11.0762 | 1.2034 |  | 213982.591 | -117221.678 | 555856.634 | 5752478.01 | 5732171.05 | -30278.7963 | 140848.987 | 14049.9745 | 252927.936 | -7628.5989 | 2186128.87 | -22449.244 | 57439.1771 | -748.7272 | 59271.1054 | 26895.5168 | 326000.203 | -7365.9582
209.52 | 11.0901 | 1.2038 |  | 223572.801 | -121738.556 | 526566.003 | 5684023.87 | 5886447.18 | -33926.6751 | 137167.713 | 17704.7882 | 247275.803 | -86199.2246 | 2066713.24 | -22266.5551 | 54170.4503 | 1204.4272 | 58088.6442 | 18568.1666 | 317070.143 | -5651.1841
209.72 | 11.1234 | 1.2055 |  | 228537.611 | -95797.905 | 484860.235 | 5317657.18 | 5994285.22 | -16716.9167 | 138783.454 | 18436.9389 | 237495.145 | -76832.0516 | 2131550.43 | -18095.8425 | 52940.6567 | 1588.0247 | 56775.7417 | 11092.0585 | 288505.735 | -5937.5636
209.92 | 11.1781 | 1.2066 |  | 242344.085 | -111105.383 | 458348.893 | 5578274.61 | 6416506.92 | -22565.1051 | 140289.367 | 23812.2014 | 232530.951 | -129260.903 | 2162367.22 | -21206.0881 | 56165.5336 | 1447.7825 | 55869.8327 | 12426.8665 | 313939.424 | -4874.1448
210.12 | 11.204 | 1.2066 |  | 234055.493 | -110128.472 | 427843.782 | 5613645.73 | 6399482.81 | -26402.9236 | 141535.582 | 24811.7285 | 226738.799 | -130411.961 | 2335905.66 | -22296.0133 | 62214.5684 | 1693.8377 | 55285.8906 | 11604.0941 | 348035.348 | -6142.0573
210.32 | 11.2454 | 1.2067 |  | 223012.403 | -121601.645 | 399405.542 | 6046281.46 | 6280359.92 | -31012.9616 | 147128.038 | 20901.7274 | 221899.74 | -53799.7768 | 2407594.05 | -33072.0722 | 63813.2383 | -572.4488 | 54690.0538 | 26722.643 | 355891.685 | -9350.0003
210.52 | 11.3077 | 1.2057 |  | 195674.954 | -136342.646 | 375726.788 | 6193591.23 | 5652474.92 | -39799.0376 | 141260.619 | 13364.6871 | 217289.354 | 5257.5219 | 2307582.98 | -34960.317 | 63626.6378 | -1205.297 | 53726.4803 | 29007.8054 | 367334.894 | -10170.5841
210.72 | 11.3406 | 1.2037 |  | 156534.285 | -129746.647 | 354536.817 | 5951548.74 | 4795818.97 | -28702.7215 | 133820.56 | 5485.8457 | 213514.039 | 88802.1395 | 2210283.15 | -22861.9082 | 60377.0661 | -2743.618 | 53111.4624 | 35469.9917 | 349125.66 | -4891.9912
210.92 | 11.3667 | 1.2022 |  | 131593.24 | -162521.525 | 350989.342 | 6527091.4 | 4220837.99 | -32996.4991 | 132230.707 | -4699.8009 | 213757.505 | 189087.812 | 2157171.79 | -23652.2037 | 58013.5834 | -3520.4726 | 52970.3459 | 35648.2011 | 340198.696 | -6292.9204
211.12 | 11.4236 | 1.2008 |  | 106743.423 | -193025.854 | 346932.052 | 7297953.48 | 3891869.58 | -42358.7546 | 145281.763 | -13690.3832 | 213729.947 | 255037.331 | 2232568.87 | -33050.926 | 54005.1518 | -2912.1575 | 53492.6294 | 27732.9156 | 298435.171 | -9699.5881
211.32 | 11.4564 | 1.1983 |  | 72686.7093 | -202573.575 | 353358.428 | 7239501.73 | 3242474.52 | -46645.6359 | 135222.718 | -16850.0841 | 216601.159 | 279337.281 | 2130502.91 | -35379.6915 | 54703.6631 | -3439.1997 | 54034.4272 | 30747.1014 | 309152.491 | -10640.8764
211.52 | 11.477 | 1.1961 |  | 24698.1644 | -187856.37 | 376031.701 | 6451209.49 | 2058978.31 | -45186.5426 | 111830.289 | -22366.8024 | 223447.217 | 366673.707 | 1966121.27 | -32635.9455 | 54939.4582 | -5695.9348 | 55545.7888 | 42255.5383 | 312848.792 | -10851.1368
211.72 | 11.5052 | 1.1939 |  | -17188.8912 | -182793.876 | 400270.757 | 5999247.79 | 933005.369 | -37884.4092 | 96122.275 | -31828.5208 | 231405.384 | 468996.471 | 1678200.41 | -26342.3042 | 47950.7241 | -7686.1466 | 56866.7783 | 51461.6044 | 286275.181 | -7168.0706
211.92 | 11.5285 | 1.1914 |  | -47194.8432 | -196138.4 | 430801.456 | 6015435.57 | 165015.632 | -32568.6929 | 85078.4273 | -38984.0271 | 238283.218 | 542518.167 | 1524390.26 | -19649.6161 | 46169.9887 | -9068.5496 | 57677.2214 | 56836.1317 | 272685.081 | -5195.273
212.12 | 11.5481 | 1.1894 |  | -50527.0495 | -235906.816 | 463539.38 | 6756294.5 | 144131.135 | -53746.5742 | 86376.6404 | -41449.346 | 245838.014 | 541154.281 | 1438741.34 | -31737.182 | 41596.7363 | -7694.9715 | 58701.7503 | 51194.0918 | 261809.971 | -10826.4991
212.32 | 11.5697 | 1.1873 |  | -50438.2593 | -234658.599 | 503530.857 | 6715669.08 | 180124.509 | -46218.5969 | 88902.0734 | -40696.4409 | 255681.323 | 537843.226 | 1403850.02 | -27669.4826 | 39258.9395 | -8049.2904 | 60765.5962 | 51857.5922 | 234868.404 | -8382.138
212.52 | 11.5831 | 1.1847 |  | -64078.959 | -231279.447 | 542245.126 | 6725487.53 | 19147.0118 | -38930.3352 | 90310.0516 | -41444.5951 | 265138.179 | 505803.903 | 1473680.01 | -25058.1798 | 41922.304 | -6227.5223 | 62354.7691 | 41868.4974 | 245655.194 | -10111.6219
212.72 | 11.6121 | 1.1815 |  | -36933.9383 | -250105.335 | 582049.866 | 7289885.46 | 512514.475 | -47183.7556 | 101285.853 | -42131.5189 | 277257.022 | 549135.818 | 1536919.11 | -26652.561 | 41150.8163 | -7967.5512 | 65408.9287 | 54397.8567 | 251415.885 | -9592.0402
212.92 | 11.6585 | 1.1778 |  | -20449.4541 | -258461.984 | 616951.02 | 7924998.32 | 1054981.16 | -47001.1156 | 122204.628 | -41730.0044 | 283842.406 | 533057.268 | 1712201.98 | -30646.9263 | 42330.4465 | -7455.6283 | 65634.7281 | 50238.0916 | 244255.525 | -9251.761
213.12 | 11.6751 | 1.174 |  | 14523.362 | -276927.827 | 643632.297 | 8375088.42 | 1746343.23 | -58835.5635 | 129201.315 | -37549.6441 | 291021.867 | 477319.123 | 1795298.56 | -33537.2323 | 42136.2821 | -5632.9179 | 67715.5006 | 41716.0597 | 250313.714 | -10123.6578
213.32 | 11.7002 | 1.1711 |  | 37628.8885 | -243770.504 | 666629.051 | 7897457.43 | 2227846.62 | -43678.9145 | 134387.808 | -32251.7588 | 294484.676 | 444313.312 | 1947725.6 | -27142.5296 | 46510.5327 | -5420.8857 | 68042.1865 | 39749.9007 | 250445.042 | -9525.3188
213.52 | 11.7139 | 1.1679 |  | 77165.5771 | -243320.054 | 679057.644 | 7940827.26 | 3015112.02 | -50035.7778 | 139129.061 | -24154.8476 | 297864.442 | 342285.13 | 1959438.01 | -31056.7873 | 46243.2295 | -3612.6705 | 68687.4517 | 33825.7803 | 260258.102 | -9386.8368
213.72 | 11.7259 | 1.1645 |  | 112376.925 | -217806.083 | 686033.486 | 7422066.57 | 3673720.59 | -42575.2741 | 139043.043 | -15122.7667 | 299199.5 | 262363.12 | 1991174.46 | -25318.0673 | 46281.1907 | -2422.1532 | 68866.5708 | 29190.1971 | 256966.904 | -7679.6255
213.92 | 11.7223 | 1.1618 |  | 135750.848 | -200143.567 | 680596.558 | 7281530.77 | 4213902.26 | -30792.0974 | 142743.828 | -8677.4747 | 298383.096 | 205451.192 | 2185104.15 | -17496.4083 | 53761.7311 | -1627.713 | 69270.2576 | 23834.359 | 285006.987 | -6593.8441
214.12 | 11.7064 | 1.1602 |  | 174278.848 | -208813.988 | 664206.802 | 7917631.07 | 5009417.24 | -41276.328 | 158629.541 | -7159.7214 | 296636.308 | 220044.562 | 2354593.73 | -25672.5512 | 56702.4363 | -2943.2061 | 69905.6201 | 28596.3413 | 291606.595 | -7043.0852
214.32 | 11.7098 | 1.1591 |  | 209300.868 | -205591.053 | 637163.345 | 8215890.8 | 5692743.26 | -39690.7262 | 171277.293 | -6424.7477 | 286939.05 | 227884.997 | 2502050.38 | -27003.6019 | 61767.161 | -4043.161 | 67294.7015 | 38777.5794 | 336603.64 | -7678.6949
214.52 | 11.7241 | 1.1572 |  | 218199.416 | -173718.718 | 599735.326 | 7740945.79 | 6026125.39 | -31670.8239 | 170000.161 | 1224.4381 | 273780.464 | 187850.723 | 2765522.82 | -26342.3957 | 73910.312 | -4835.6236 | 65028.7547 | 45062.9096 | 403149.929 | -8140.6844
214.72 | 11.7538 | 1.1544 |  | 247361.765 | -159193.082 | 565565.692 | 7607715.41 | 6723856.73 | -24420.0997 | 175284.968 | 9430.1674 | 264439.338 | 88937.223 | 2734169.45 | -29747.0411 | 70756.7951 | -2826.0774 | 62166.0093 | 42680.5075 | 403323.073 | -11261.3313
214.92 | 11.7702 | 1.1513 |  | 260680.338 | -169640.436 | 542452.176 | 7553011.59 | 7042678.42 | -22602.8486 | 173112.32 | 14800.9736 | 264726.901 | -25030.2986 | 2571576.41 | -21802.6842 | 65399.8765 | -215.8586 | 62796.6216 | 23888.4085 | 363343.027 | -3966.7179
215.12 | 11.7944 | 1.1516 |  | 236044.484 | -134083.968 | 498602.165 | 6773908.5 | 6511498.75 | -18404.5677 | 166483.567 | 13637.3241 | 255250.715 | -42256.0215 | 2565658.45 | -24843.7498 | 64758.3704 | 1572.8662 | 61873.451 | 16864.5993 | 370086.029 | -8513.8473
215.32 | 11.8036 | 1.1531 |  | 231979.129 | -134578.308 | 475859.816 | 6549888.69 | 6237021.14 | -9098.8754 | 152674.122 | 12570.9877 | 252994.138 | 48620.2024 | 2392169.27 | -14058.8988 | 64721.7645 | -3322.7593 | 61504.2963 | 39288.8961 | 361973.791 | -2748.6253
215.52 | 11.8173 | 1.1543 |  | 204176.924 | -179164.82 | 444886.48 | 7451009.99 | 5670259.67 | -27264.6227 | 157414.044 | 1763.4714 | 247113.054 | 67995.8079 | 2321927.61 | -26365.4818 | 57583.696 | -58.3394 | 60245.2627 | 21640.8549 | 337176.168 | -6492.8303
215.72 | 11.7735 | 1.1554 |  | 186441.936 | -174341.02 | 406083.171 | 7209336.61 | 5312310.4 | -38361.9509 | 150093.998 | 738.3206 | 236162.055 | 150601.93 | 2269861.22 | -34614.7098 | 57849.4017 | -3462.2242 | 58792.5414 | 37561.8882 | 322338.239 | -8550.1511
215.92 | 11.7303 | 1.1563 |  | 142098.561 | -133204.545 | 386245.584 | 6128169.68 | 4358364.52 | -27946.9419 | 134749.702 | -3433.7528 | 225384.823 | 213886.148 | 2383007.83 | -26038.5308 | 68011.0426 | -4898.0356 | 55392.1813 | 45618.9753 | 399695.154 | -7961.4427
216.12 | 11.7203 | 1.1568 |  | 115814.281 | -151906.851 | 371966.68 | 6470974.77 | 4090150.68 | -38440.4113 | 137827.245 | -5243.2097 | 223109.949 | 238594.141 | 2436278.09 | -30449.799 | 67480.0229 | -5088.731 | 55155.6251 | 46030.6381 | 385972.51 | -8917.7081
216.32 | 11.7117 | 1.1567 |  | 93998.7306 | -200821.768 | 377554.552 | 7374806.27 | 3672352.92 | -50413.9738 | 140926.6 | -14119.2487 | 228625.093 | 262940.249 | 2268404.31 | -35226.7248 | 60315.5143 | -3552.0235 | 56710.9888 | 35517.1124 | 351550.166 | -10379.6635
216.52 | 11.693 | 1.156 |  | 51716.2026 | -224139.235 | 382322.66 | 7815993.64 | 2739043.54 | -45924.3014 | 136774.489 | -26560.0133 | 232125.592 | 395845.01 | 2154700.27 | -30455.8936 | 56853.4842 | -5850.2409 | 57643.9274 | 43969.5834 | 332201.999 | -9535.9156
216.72 | 11.6904 | 1.1552 |  | 11657.9761 | -242237.901 | 399813.728 | 8137097.34 | 1708125.61 | -38250.8274 | 131958.706 | -42335.8443 | 237289.759 | 591079.588 | 2071829.84 | -23255.3046 | 54835.1931 | -9845.8822 | 59128.731 | 59788.5143 | 314775.452 | -6176.5694
216.92 | 11.7155 | 1.1545 |  | -9843.2274 | -266488.419 | 418885.571 | 8541476.45 | 1232236.58 | -54098.6625 | 128484.736 | -48633.4065 | 237492.62 | 669734.833 | 2003045.07 | -33833.3663 | 53241.4649 | -10969.3578 | 57891.5278 | 66951.3399 | 309210.141 | -10849.4035
217.12 | 11.7058 | 1.1536 |  | -35178.7604 | -262420.957 | 446253.953 | 8160984.55 | 825380.505 | -55211.267 | 122296.087 | -46703.1359 | 242338.185 | 589520.736 | 1898239.7 | -37040.9339 | 50447.1909 | -8044.9531 | 58472.6274 | 51541.3802 | 286356.686 | -12448.3099
217.32 | 11.6806 | 1.1518 |  | -40729.8264 | -247016.795 | 488947.722 | 7278939.51 | 547374.009 | -50461.0709 | 102181.499 | -41631.8309 | 253698.186 | 553355.122 | 1653855.23 | -29871.2304 | 46064.2327 | -8168.8314 | 60461.3673 | 54293.0736 | 280809.935 | -9409.4459
217.52 | 11.6379 | 1.1494 |  | -74687.3045 | -212076.859 | 528898.628 | 6309367.92 | -309546.479 | -33516.3459 | 84979.3957 | -43953.2698 | 263890.153 | 568319.126 | 1559713.37 | -21649.7677 | 47228.3689 | -8089.3718 | 62357.2045 | 53426.9357 | 292410.302 | -7863.7363
217.72 | 11.6182 | 1.1465 |  | -66899.2683 | -218703.235 | 564774.737 | 6548712.03 | -313340.941 | -38337.2368 | 89169.7167 | -48628.0457 | 272749.488 | 658949.877 | 1526785.72 | -24504.2458 | 45408.2062 | -10651.4679 | 64375.6368 | 65988.2566 | 278182.199 | -8270.302
217.92 | 11.6082 | 1.1439 |  | -39128.099 | -251997.206 | 601852.377 | 7538251.38 | 345398.194 | -45427.5392 | 112156.927 | -50512.3698 | 279871.024 | 638662.022 | 1581314.2 | -27279.5133 | 38500.9464 | -9056.3949 | 65028.7081 | 57810.4846 | 235478.72 | -7912.3719
218.12 | 11.5792 | 1.1408 |  | -17950.6696 | -255262.112 | 622854.661 | 7770680.22 | 915226.948 | -51541.568 | 121021.326 | -45676.4266 | 282828.536 | 577187.663 | 1747042.54 | -28907.951 | 41098.0499 | -7131.1883 | 65886.6418 | 46300.5882 | 224043.138 | -9938.3738
218.32 | 11.5792 | 1.1369 |  | 12796.524 | -230410.546 | 641404.265 | 7398799.32 | 1604342.36 | -38509.6773 | 122209.84 | -35734.9942 | 284565.901 | 491047.016 | 1804480.66 | -25816.8955 | 44970.989 | -6735.9736 | 65596.8522 | 46879.5378 | 251110.605 | -9488.4664
218.52 | 11.6164 | 1.1335 |  | 56299.9137 | -236254.537 | 666517.747 | 7406141.65 | 2579186.5 | -50374.9989 | 125757.78 | -22615.3315 | 291169.087 | 303461.59 | 1731983.27 | -29504.2632 | 40746.6075 | -2647.6661 | 66546.1478 | 29204.4652 | 236156.21 | -9203.0012
218.72 | 11.6149 | 1.1303 |  | 82854.4987 | -213635.995 | 677439.986 | 7021944.91 | 3159993.06 | -40778.9772 | 129709.153 | -14311.1304 | 296798.371 | 196819.755 | 1794852.25 | -24632.528 | 39732.4129 | -23.6972 | 68428.278 | 14103.0152 | 217180.241 | -7784.8723
218.92 | 11.6071 | 1.1272 |  | 106727.948 | -186169.062 | 680470.753 | 6657869.18 | 3486232.03 | -38998.933 | 125960.085 | -10792.2468 | 298649.373 | 236869.591 | 1945905.89 | -22171.7642 | 49025.6478 | -2765.4965 | 69785.6282 | 29984.8549 | 275756.445 | -7168.6499
219.12 | 11.6181 | 1.1237 |  | 143963.53 | -194067.844 | 666576.717 | 7257935.9 | 4273041.54 | -42038.8703 | 142989.64 | -8903.0998 | 293234.967 | 221269.646 | 2110186.19 | -25151.684 | 49948.3876 | -2613.5537 | 67876.3284 | 30862.3823 | 267492.986 | -7731.8812
219.32 | 11.6016 | 1.1204 |  | 179435.094 | -200506.729 | 648014.878 | 7673445.1 | 5051543.06 | -45202.3431 | 157679.475 | -6158.1368 | 289596.167 | 175523.116 | 2276086.01 | -28150.579 | 51364.6907 | -1043.5984 | 68324.2313 | 19444.8328 | 254151.122 | -6313.4173
219.52 | 11.5758 | 1.1172 |  | 200287.563 | -164738.725 | 612427.129 | 7063975.42 | 5435259.94 | -39720.0242 | 155614.727 | -22.223 | 275546.647 | 138721.357 | 2389929.21 | -30082.5776 | 59407.0428 | -1452.9106 | 64431.483 | 26913.9188 | 328335.864 | -11568.2328
219.72 | 11.5965 | 1.1142 |  | 227798.136 | -145984.223 | 583814.309 | 6509666.87 | 6033113.24 | -30420.4188 | 147294.329 | 12195.3498 | 268470.233 | 37648.3555 | 2349343.54 | -20372.9915 | 60417.6302 | -1177.527 | 63085.8011 | 27519.54 | 334845.621 | -5975.1437
219.92 | 11.6007 | 1.111 |  | 231395.885 | -120265.479 | 551408.121 | 6068599.76 | 6266306.72 | -21688.6688 | 147960.155 | 18695.3149 | 261351.705 | -77763.9496 | 2395203.66 | -19855.7929 | 63273.1895 | 1670.9728 | 61622.8016 | 11603.5203 | 345194.928 | -6310.9083
220.12 | 11.586 | 1.1081 |  | 240772.868 | -129609.014 | 516993.16 | 6354563.63 | 6441320.73 | -27501.241 | 152415.476 | 17143.6772 | 258165.744 | -39663.0335 | 2416232.75 | -19038.8347 | 61835.2758 | 435.5138 | 62012.5759 | 22253.2609 | 357161.165 | -5117.9804
220.32 | 11.6257 | 1.1054 |  | 241164.519 | -147386.026 | 484126.545 | 6905407.37 | 6453272.81 | -28567.1058 | 162489.729 | 11141.5276 | 250331.023 | 9551.8374 | 2463416.42 | -25339.6163 | 59916.4961 | 461.1326 | 60558.4963 | 18555.9317 | 332627.475 | -7265.1546
220.52 | 11.6216 | 1.103 |  | 219615.689 | -140118.747 | 440808.139 | 6893892.89 | 6145799.3 | -14333.4946 | 166146.598 | 7371.562 | 239131.283 | 74899.2982 | 2577564.96 | -23558.177 | 65115.3353 | -1825.208 | 58990.8663 | 26889.6163 | 349448.315 | -7515.2175
220.72 | 11.6215 | 1.1002 |  | 204095.804 | -162289.393 | 409912.958 | 7246091.42 | 5788148.45 | -31718.7827 | 159866.378 | 2983.6806 | 231121.339 | 98016.5633 | 2501423.05 | -31840.9569 | 63901.6084 | -1065.7272 | 56875.9296 | 25586.9552 | 371776.114 | -10025.6665
220.92 | 11.605 | 1.0964 |  | 181363.276 | -162271.399 | 385018.425 | 6832662.33 | 5308153.95 | -41375.0113 | 146809.091 | 4029.6085 | 224478.541 | 104831.502 | 2313769.03 | -34464.6204 | 59819.7048 | -1913.7728 | 55041.4375 | 32072.7069 | 349321.352 | -10159.7723
221.12 | 11.5903 | 1.1759 |  | 133099.949 | -146101.298 | 368190.175 | 6091444.47 | 4329258.39 | -25751.062 | 128209.639 | 2126.4197 | 221046.072 | 104158.319 | 2170953.07 | -22507.439 | 61422.6788 | -2523.2099 | 54531.8247 | 34995.4889 | 364079.224 | -6208.0266
221.32 | 11.619 | 1.4056 |  | 111270.535 | -165373.847 | 369477.279 | 6460414.13 | 3832650.12 | -23209.9431 | 129885.261 | -7953.069 | 224249.224 | 212997.579 | 2128072.6 | -18234.8594 | 57549.3486 | -3642.5278 | 55287.84 | 36583.3003 | 344689.639 | -5322.6293
221.52 | 11.6374 | 1.6631 |  | 93676.5314 | -241565.19 | 373840.559 | 8147099.23 | 3664406.69 | -44612.5709 | 146470.821 | -18819.2943 | 228838.129 | 266699.7 | 2089936.52 | -23334.1123 | 47702.0034 | -1914.7745 | 56598.5835 | 22293.5952 | 270835.798 | -7019.9007
221.72 | 11.6486 | 1.9263 |  | 64159.6658 | -286946.364 | 383863.378 | 9214382.03 | 3064224.38 | -54313.7902 | 154180.577 | -31715.2402 | 235767.689 | 387809.004 | 2076781.08 | -33820.2972 | 47445.9799 | -4193.722 | 59376.8802 | 32804.1036 | 264921.074 | -8640.7579
221.92 | 11.6876 | 2.2288 |  | 21519.2477 | -264379.965 | 398521.933 | 8771991.88 | 2006322.4 | -42801.3705 | 145566.435 | -44056.0159 | 234252.159 | 618657.101 | 2225691.59 | -28315.1427 | 55605.8848 | -10052.2197 | 58297.3004 | 61163.2438 | 311846.726 | -9419.0856
222.12 | 11.7418 | 2.6297 |  | -1191.5854 | -281668.188 | 423081.279 | 8965877.2 | 1632998.8 | -56559.4625 | 142643.645 | -46687.9209 | 237442.542 | 626103.604 | 2214057.12 | -34845.2773 | 56014.2793 | -9214.7303 | 57898.6479 | 58256.0652 | 324334.204 | -10838.7245
222.32 | 11.7518 | 3.1063 |  | -11402.5415 | -285854.372 | 460131.282 | 8694193.18 | 1466760.35 | -52083.1775 | 133014.889 | -42609.8965 | 247095.202 | 562925.394 | 2085516.36 | -25904.3658 | 52445.9475 | -7816.369 | 59490.1453 | 51866.4559 | 303192.043 | -7749.8112
222.52 | 11.7635 | 3.5905 |  | -30170.6593 | -275197.194 | 500694.82 | 8283650.36 | 1053326 | -57014.8345 | 125073.001 | -43061.8509 | 259138.107 | 568123.631 | 2022734.81 | -34114.9155 | 52124.8921 | -7687.9261 | 62374.287 | 50031.8013 | 297799.725 | -11198.0349
222.72 | 11.7913 | 4.0634 |  | -34137.486 | -271547.987 | 546790.089 | 7909473.89 | 681374.825 | -46476.1581 | 112812.104 | -45193.9165 | 272005.663 | 605704.646 | 1787467.05 | -21339.7716 | 47743.1254 | -9307.3759 | 64670.1967 | 60044.3396 | 283940.212 | -5970.8094
222.92 | 11.8218 | 4.4956 |  | -31089.3085 | -279992.786 | 591475.227 | 8085818.07 | 624915.726 | -49949.9128 | 112870.98 | -48258.9358 | 282714.836 | 623939.947 | 1755197.45 | -24222.75 | 46803.8121 | -8946.8288 | 66586.57 | 55943.733 | 272291.204 | -6910.2236
223.12 | 11.8268 | 4.893 |  | -19278.4843 | -264904.664 | 617783.46 | 8052906.49 | 1045956.91 | -50456.043 | 125702.564 | -44073.0938 | 287009.308 | 583864.963 | 1854401.59 | -34359.2239 | 45340.2658 | -8133.9407 | 67002.5611 | 54090.7443 | 259788.952 | -11274.0972
223.32 | 11.8341 | 5.2526 |  | 6264.9531 | -249694.522 | 650391.698 | 7413190.68 | 1362835.33 | -62914.5296 | 113535.058 | -36096.4983 | 293597.488 | 480879.748 | 1676212.94 | -36825.5611 | 42119.3061 | -5746.0137 | 68166.347 | 40573.7387 | 237576.333 | -13106.3623
223.52 | 11.8491 | 5.6251 |  | 19149.3097 | -198133.776 | 680375.991 | 5921944.67 | 1429657.79 | -38573.7742 | 92005.172 | -23594.3359 | 300048.515 | 352551.685 | 1417360.35 | -18112.8884 | 37179.8514 | -4497.8305 | 68739.3422 | 38511.3848 | 223316.854 | -4393.6714
223.72 | 11.8654 | 6.0176 |  | 36568.0019 | -151341.969 | 695064.659 | 4972027.72 | 1833297.54 | -30288.6115 | 88875.8694 | -12606.4484 | 304306.313 | 232023.159 | 1483184.62 | -18478.4771 | 39944.5007 | -2387.6676 | 69802.0131 | 27833.8047 | 222566.045 | -5753.1478
223.92 | 11.8734 | 6.3918 |  | 89550.292 | -159263.641 | 711594.474 | 5158037.87 | 2892620.93 | -51190.055 | 93860.4251 | -2445.4978 | 310059.703 | 95375.5115 | 1387100.51 | -28311.4404 | 34793.5704 | 709.2587 | 70724.6354 | 13718.8753 | 204635.534 | -9227.6329
224.12 | 11.8798 | 6.7654 |  | 124659.425 | -148041.942 | 707643.005 | 5065034.11 | 3632134.36 | -47571.5766 | 102238.536 | 5193.7557 | 310617.812 | 6307.7571 | 1386455.44 | -24823.3055 | 29576.7393 | 2452.1124 | 71216.3017 | 4778.9661 | 155680.972 | -7925.9129
224.32 | 11.8739 | 7.0846 |  | 147589.889 | -134909.711 | 695413.187 | 5061302.38 | 4029686.85 | -38517.7016 | 109118.411 | 6060.3412 | 310398.184 | -44976.3032 | 1432865.23 | -22208.7386 | 30355.7475 | 4228.8663 | 71878.3914 | -5818.2715 | 154070.017 | -7206.6117
224.52 | 11.8793 | 7.3337 |  | 183963.032 | -137262.851 | 673632.936 | 5386032.87 | 4820862.56 | -45837.937 | 119776.329 | 11346.8976 | 304048.242 | -45880.7278 | 1572969.3 | -30708.9828 | 32657.7467 | 2708.2332 | 70383.5181 | 5141.8 | 163206.295 | -11275.8578
224.72 | 11.8805 | 7.5687 |  | 214753.563 | -143463.428 | 639654.236 | 5552216.01 | 5459222.72 | -56434.8644 | 126989.051 | 16812.2914 | 293584.596 | -173723.06 | 1433671.52 | -39469.8999 | 23474.6264 | 6253.1292 | 67664.2871 | -11876.2544 | 119517.272 | -13664.649
224.92 | 11.8478 | 7.7614 |  | 204250.361 | -86558.364 | 601684.104 | 4001193.41 | 5095489.36 | -42431.5007 | 102180.711 | 25182.9681 | 284994.899 | -240580.393 | 1321689.83 | -24407.3959 | 27699.673 | 6418.427 | 67302.7952 | -14535.881 | 136689.851 | -7266.9009
225.12 | 11.8119 | 7.8391 |  | 195666.225 | -40684.6198 | 567727.382 | 2697361.24 | 4731434.52 | -47718.883 | 75465.4835 | 31524.8734 | 274931.688 | -268055.842 | 1200071.92 | -25078.8931 | 33625.1918 | 5653.266 | 64581.9214 | -7209.8654 | 202918.921 | -9256.7117
225.32 | 11.7953 | 7.8982 |  | 197666.263 | -33781.9034 | 528538.912 | 2432769.45 | 4833988.69 | -50736.6366 | 73484.2445 | 35860.3057 | 265830.728 | -331440.45 | 1089479.65 | -22197.3622 | 28781.4689 | 6729.4279 | 62411.7165 | -11381.8374 | 182641.768 | -5427.0816
225.52 | 11.742 | 7.9872 |  | 193215.965 | -50317.165 | 489998.763 | 2955648.15 | 4942661.52 | -52306.4259 | 89725.1051 | 32985.7211 | 259555.157 | -361583.33 | 1106687.64 | -27561.2337 | 20951.1585 | 8981.3342 | 61873.7439 | -26564.1071 | 112335.936 | -6566.3955
225.72 | 11.7016 | 7.9879 |  | 189207.156 | -77887.2055 | 459409.757 | 3732665.63 | 4829437.28 | -45602.6766 | 93701.9859 | 24193.2574 | 255757.212 | -211681.687 | 1263350.88 | -23571.1541 | 28418.5672 | 5145.5605 | 63219.6057 | -9862.2585 | 152269.384 | -6570.1559
225.92 | 11.7113 | 8.0335 |  | 171699.317 | -101742.722 | 421155.881 | 4420314.06 | 4617126.62 | -60582.9821 | 100869.632 | 17386.067 | 241350.669 | -112660.037 | 1431946.61 | -44993.2341 | 31915.8819 | 3673.3146 | 58803.9156 | -2078.2123 | 169024.791 | -16578.0662
226.12 | 11.6772 | 8.1991 |  | 136121.143 | -104396.298 | 398227.859 | 3922806.07 | 3692623.2 | -65827.592 | 80818.0551 | 12515.5046 | 234030.208 | -89236.9491 | 1189198.59 | -42514.6468 | 29126.6199 | 3810.2179 | 57393.6756 | -4910.6877 | 161326.726 | -13652.9528
226.32 | 11.6443 | 8.2801 |  | 69714.8987 | -60743.6547 | 379459.723 | 2580501.6 | 2187766.3 | -33560.4369 | 54281.0234 | 6880.9428 | 228928.352 | 1207.2153 | 1023368.02 | -20365.2523 | 30652.6792 | 962.6778 | 56151.3065 | 9722.2328 | 187868.078 | -7873.3574
226.52 | 11.6379 | 8.3321 |  | 45702.9012 | -90788.6518 | 381856.305 | 3018054.13 | 1603597.06 | -32946.7238 | 53329.2972 | -2541.8741 | 231664.179 | 74737.9146 | 890705.383 | -18449.8765 | 24447.4309 | 550.7381 | 56681.1171 | 9120.1242 | 152017.902 | -4933.105
226.72 | 11.5979 | 8.4221 |  | 30949.4955 | -143699.359 | 389840.859 | 4168551.5 | 1491412.11 | -51497.9561 | 66284.7055 | -9334.3964 | 233625.51 | 157084.173 | 933411.122 | -29455.1593 | 20941.8968 | -1032.6975 | 56858.0516 | 16857.8475 | 111502.651 | -8736.5689
226.92 | 11.5406 | 8.4224 |  | 240.4868 | -193449.604 | 398107.331 | 5316109.01 | 870429.421 | -54135.1154 | 72711.0865 | -23404.3105 | 237590.277 | 272376.908 | 954260.708 | -31786.0065 | 20817.7492 | -1875.5717 | 58694.231 | 18267.3473 | 117580.661 | -10145.7667
227.12 | 11.5121 | 8.3363 |  | -17758.3216 | -217252.512 | 415967.994 | 5762627.57 | 255228.294 | -56696.847 | 65187.7245 | -34161.6916 | 238444.892 | 473257.344 | 919506.329 | -34570.4511 | 24024.2884 | -7422.997 | 58474.5445 | 46912.5077 | 142520.505 | -12629.8104
227.32 | 11.489 | 8.315 |  | -57416.2868 | -222571.308 | 433030.64 | 5914491.82 | -426424.882 | -43061.4889 | 68240.3442 | -41810.9366 | 238607.852 | 496351.296 | 941471.349 | -31546.6746 | 22771.9059 | -5963.7239 | 57086.9922 | 37583.1699 | 142415.337 | -11535.0821
227.52 | 11.4569 | 8.3121 |  | -54617.7655 | -222475.931 | 465396.838 | 5801285.7 | -430557.607 | -45990.0321 | 65433.2521 | -42241.0282 | 244957.849 | 536219.368 | 976779.123 | -27266.0752 | 26604.2106 | -7545.9072 | 58792.4658 | 45540.5147 | 152981.987 | -11340.3672
227.72 | 11.4543 | 8.2982 |  | -54784.4621 | -221490.951 | 500319.294 | 5733021.89 | -275762.876 | -48388.5807 | 71420.293 | -38856.8365 | 250501.88 | 456771.252 | 927680.791 | -31681.6349 | 20453.2056 | -5027.6511 | 58223.1186 | 33659.4766 | 120422.916 | -11232.7191
227.92 | 11.4421 | 8.3452 |  | -58597.9634 | -205323.241 | 542215.834 | 5204666.04 | -375227.619 | -38323.7642 | 63354.8904 | -34887.5294 | 263443.494 | 411814.987 | 907054.225 | -20751.1881 | 23042.2333 | -4369.8072 | 62121.9563 | 29960.7868 | 127413.853 | -7328.0306
228.12 | 11.4098 | 8.3502 |  | -51534.6078 | -201025.3 | 574852.213 | 5246893.74 | -268108.801 | -49775.2738 | 66755.9665 | -35045.6289 | 271265.566 | 441856.909 | 962055.249 | -30770.79 | 23156.1976 | -5310.5022 | 63174.4834 | 36272.6382 | 121433.433 | -11766.2802
228.32 | 11.3944 | 8.2953 |  | -30197.1695 | -217594.078 | 608443.525 | 5643309.21 | 11731.4378 | -50966.136 | 67016.3391 | -36066.8324 | 279168.039 | 457028.604 | 893862.5 | -27004.1989 | 21734.374 | -5731.8909 | 64915.7184 | 37494.2404 | 109703.864 | -7977.0592
228.52 | 11.372 | 8.2657 |  | -19277.5707 | -200558.978 | 625944.674 | 5398678.06 | 221631.242 | -49558.8493 | 66878.5053 | -31987.257 | 279669.718 | 413693.389 | 942810.748 | -29735.6658 | 24835.4514 | -5035.9666 | 64038.3355 | 35684.6903 | 139620.989 | -10782.6205
228.72 | 11.3421 | 8.2147 |  | 2251.0196 | -169308.405 | 642866.664 | 5021384.97 | 871033.782 | -38691.9787 | 79150.7746 | -23639.1598 | 282137.574 | 336927.19 | 1111036.09 | -27150.1405 | 25338.1421 | -4022.2054 | 64689.1402 | 32015.9097 | 135231.64 | -8964.3262
228.92 | 11.3246 | 8.1365 |  | 50143.4589 | -158000.349 | 654332.3 | 4879966.23 | 1857797.98 | -44898.148 | 82759.2367 | -12837.6423 | 284054.584 | 213435.884 | 1212428.03 | -25099.5692 | 29303.3466 | -1653.1739 | 65293.796 | 20803.1758 | 157948.371 | -7106.1733
229.12 | 11.3067 | 8.0615 |  | 78460.9757 | -119280.739 | 655912.485 | 4399814.71 | 2692842.16 | -43238.5404 | 93377.8883 | -1066.4099 | 282420.642 | 93538.5159 | 1467619.52 | -28909.2458 | 35910.2176 | 466.0864 | 64314.2498 | 12775.6643 | 192689.316 | -11470.7532
229.32 | 11.3133 | 7.9831 |  | 134591.493 | -141166.212 | 654767.408 | 5111028.1 | 3965485.93 | -45542.7568 | 109395.933 | 7410.9376 | 285909.639 | -35169.8258 | 1444901.39 | -26453.7903 | 30812.3064 | 3164.483 | 65759.2387 | 402.2837 | 163509.519 | -6817.1444
229.52 | 11.3066 | 7.9373 |  | 150405.732 | -124541.408 | 643692.681 | 4987438.87 | 4260226.4 | -45629.8329 | 113071.172 | 9706.2511 | 284130.01 | -49958.1598 | 1619721.82 | -30556.876 | 36536.7912 | 3601.4989 | 65865.2841 | -3009.3805 | 185472.798 | -11182.9019
229.72 | 11.2891 | 7.8532 |  | 174690.345 | -118024.456 | 616873.698 | 4830560.88 | 4543989.07 | -48514.3906 | 107186.892 | 12505.6332 | 275977.982 | -44020.2033 | 1503494.87 | -31150.238 | 35406.5558 | 2030.3542 | 64001.0696 | 7926.4728 | 197474.307 | -11301.084
229.92 | 11.2926 | 7.7555 |  | 180714.898 | -78100.6341 | 581197.306 | 3944133.09 | 4507409.13 | -39759.8778 | 97971.438 | 16859.8189 | 263674.188 | -120861.623 | 1367904.06 | -25244.5582 | 31618.2965 | 3648.1098 | 60599.9878 | 523.1427 | 173455.335 | -10427.8423
230.12 | 11.2749 | 7.7039 |  | 195750.736 | -66413.3951 | 552866.449 | 3337579.93 | 4830342.52 | -36516.48 | 89511.4787 | 27418.2894 | 258646.15 | -274510.723 | 1174694 | -16184.3559 | 26029.6965 | 6768.114 | 60352.9615 | -16386.3162 | 138192.851 | -2796.3688
230.32 | 11.242 | 7.5617 |  | 206665.885 | -49791.8233 | 516619.851 | 2998148.33 | 5161121.92 | -55643.0439 | 89235.9899 | 34359.5034 | 250197.931 | -343422.085 | 1193761.62 | -32975.6537 | 25192.4578 | 8048.6267 | 58347.8639 | -21437.9144 | 141728.106 | -12014.3953
230.52 | 11.233 | 7.3679 |  | 218219.296 | -55816.7466 | 484843.601 | 2846672.32 | 5275629.39 | -60567.1644 | 79558.0143 | 37583.9181 | 244426.158 | -375682.436 | 988251.307 | -28830.6863 | 21643.1933 | 7856.3174 | 58206.1951 | -20507.5048 | 124808.533 | -7148.3634
230.72 | 11.2051 | 7.2324 |  | 180484.182 | -29876.4676 | 448055.119 | 2287642.13 | 4495138.25 | -42753.6864 | 73753.8244 | 32141.2118 | 236985.098 | -337836.645 | 1088439.04 | -22937.8334 | 24908.5675 | 8494.2732 | 56852.4366 | -26851.0562 | 131346.844 | -8180.9605
230.92 | 11.178 | 7.0479 |  | 173611.029 | -42680.4853 | 411968.58 | 2607359.62 | 4296891.69 | -45623.2747 | 72991.8577 | 26297.7602 | 229267.652 | -199568.241 | 1120085.48 | -24791.6889 | 27820.4393 | 3899.0251 | 56120.7964 | -3097.4265 | 154980.213 | -7663.252
231.12 | 11.1845 | 6.8766 |  | 162096.695 | -67836.0247 | 384905.512 | 3250008.29 | 4161078.3 | -49474.6305 | 79750.6845 | 20884.3083 | 219581.967 | -163340.874 | 1210105.4 | -26737.117 | 30581.9424 | 3964.2236 | 53146.1779 | -3509.1723 | 177845.121 | -8516.8993
231.32 | 11.1803 | 6.7884 |  | 149150.196 | -93005.0956 | 355855.176 | 3948973.25 | 4238693.54 | -52514.9729 | 95639.1168 | 18241.5173 | 213002.271 | -172401.106 | 1318740.04 | -35340.921 | 29532.6083 | 5220.463 | 52098.7913 | -12208.7516 | 154467.583 | -11377.6842
231.52 | 11.1813 | 6.6695 |  | 123411.136 | -102224.456 | 346260.773 | 4046634.99 | 3754429.68 | -50030.8205 | 91999.1718 | 12702.4928 | 212805.405 | -89823.3834 | 1359282.12 | -31056.5945 | 32666.9229 | 3319.3684 | 53166.806 | -3699.4972 | 177701.564 | -9377.5215
231.72 | 11.2048 | 6.5662 |  | 74831.1318 | -102857.37 | 338836.366 | 4031988.38 | 2732661.19 | -39808.8209 | 85945.1282 | 1890.824 | 211191.874 | 35511.3081 | 1385912.41 | -27004.5287 | 35580.5366 | 1191.7761 | 52458.6742 | 6562.0506 | 202035.781 | -10193.7147
231.92 | 11.2147 | 6.5336 |  | 50666.9432 | -152928.71 | 348441.045 | 5001388.71 | 2126425.77 | -41518.4994 | 86797.2608 | -11113.2611 | 216257.317 | 174757.316 | 1282660.19 | -22868.5243 | 32560.5148 | -1478.8952 | 53768.2996 | 18480.2832 | 188579.473 | -6753.0946
232.12 | 11.2166 | 6.4721 |  | 27397.3637 | -187296.251 | 355073.585 | 5916980.98 | 1655026.95 | -46346.6307 | 99045.599 | -24527.0691 | 217090.965 | 337336.612 | 1382311.79 | -28514.8791 | 30282.9949 | -3930.8371 | 53848.11 | 27893.1941 | 158535.968 | -9273.3583
232.32 | 11.2174 | 6.3714 |  | -6516.1777 | -210043.692 | 370927.664 | 6330740.59 | 1000801.35 | -46666.2512 | 99321.3064 | -33381.6278 | 218503.757 | 414764.059 | 1404298.1 | -35393.6052 | 32196.8474 | -4639.5005 | 53524.455 | 30863.8577 | 174256.556 | -13401.7272
232.52 | 11.2094 | 6.2606 |  | -23959.2873 | -216230.797 | 390671.691 | 6168838.69 | 524361.062 | -52570.5257 | 93622.2708 | -37229.2528 | 221341.523 | 463711.404 | 1242232.34 | -33751.5003 | 26684.7322 | -5881.5184 | 53772.3001 | 38306.3576 | 157174.594 | -13006.1327
232.72 | 11.2079 | 6.1267 |  | -45374.0193 | -224899.326 | 428757.279 | 6009866.07 | 1394.0386 | -38685.3395 | 77352.1598 | -38469.0359 | 230808.646 | 443570.341 | 1053868.71 | -20071.8361 | 26192.5319 | -5171.4849 | 55134.7244 | 34571.638 | 163325.188 | -7159.4163
232.92 | 11.2113 | 6.0065 |  | -51846.4397 | -235131.215 | 462190.082 | 6113260.43 | -155234.275 | -40283.7587 | 73995.9652 | -39412.4396 | 240097.778 | 461052.417 | 985560.169 | -23635.1105 | 23388.0495 | -5438.6979 | 57255.668 | 35632.3691 | 141483.695 | -8292.3195
233.12 | 11.2019 | 5.8853 |  | -59826.3062 | -231615.321 | 499629.113 | 6270875.03 | -241129.534 | -32908.9873 | 81601.7979 | -42789.6819 | 249830.253 | 511094.667 | 1110608.88 | -17931.3408 | 25660.8188 | -6414.612 | 59001.893 | 39630.6057 | 143307.537 | -5985.6002
233.32 | 11.2218 | 5.7483 |  | -41027.4919 | -258587.967 | 535581.539 | 7184873.61 | 244759.744 | -49920.2658 | 98541.3591 | -45092.2028 | 258275.433 | 547406.138 | 1342545.92 | -29009.7284 | 29279.0935 | -6664.407 | 60975.4909 | 40632.2004 | 148702.579 | -11647.2827
233.52 | 11.2366 | 5.6988 |  | -18307.8435 | -274979.508 | 567448.82 | 7558567.41 | 794446.219 | -65196.2147 | 101273.111 | -39691.5706 | 263685.802 | 513645.181 | 1424033.75 | -33725.1528 | 33402.0722 | -6746.2601 | 61553.5732 | 42231.9586 | 173828.149 | -10534.7414
233.72 | 11.2238 | 5.6303 |  | -29315.2073 | -215282.196 | 590313.456 | 6477738.17 | 588329.027 | -43596.0823 | 96988.2707 | -36819.0194 | 266689.594 | 485044.817 | 1644324.02 | -31449.9915 | 45446.5437 | -5930.4661 | 62470.5779 | 37504.5349 | 244152.304 | -13252.6074
233.92 | 11.2439 | 5.4935 |  | 23813.3465 | -222546.802 | 618519.947 | 6499939.43 | 1539681.73 | -51908.9931 | 95814.6203 | -26706.3467 | 272715.273 | 408806.516 | 1472155.91 | -25318.6734 | 39645.6814 | -6326.036 | 62523.4357 | 45691.5997 | 234508.461 | -7248.0927
234.12 | 11.2546 | 5.4347 |  | 41496.5937 | -212530.445 | 642404.266 | 6401649.62 | 2080273.26 | -43881.9019 | 102275.123 | -18180.4518 | 278960.439 | 247582.389 | 1526169.23 | -24481.8414 | 39507.7363 | -1870.9377 | 63603.1537 | 23490.6336 | 224326.975 | -6774.1502
234.32 | 11.2224 | 5.3407 |  | 73380.1 | -190298.903 | 646468.849 | 6223358.11 | 2737551.29 | -50431.6785 | 110817.092 | -12800.6887 | 282588.123 | 238781.892 | 1696109.02 | -30094.0945 | 42757.4009 | -2684.8365 | 65738.5498 | 28111.3454 | 237410.512 | -8742.8897
234.52 | 11.2301 | 5.1089 |  | 99384.4122 | -159863.383 | 645025.9 | 5860586.78 | 3107103.59 | -41795.9749 | 113463.756 | -10868.6481 | 278708.958 | 250262.313 | 1794171.8 | -26654.3336 | 44556.1284 | -2916.2211 | 64046.9175 | 28421.5582 | 239896.449 | -10221.2733
234.72 | 11.2532 | 5.003 |  | 133859.35 | -146378.126 | 639459.465 | 5724621.83 | 3919928.81 | -32524.941 | 119101.621 | -1184.6194 | 276851.29 | 133806.266 | 1819228.85 | -20850.2271 | 45514.6229 | -1393.7954 | 63762.7699 | 23277.8926 | 254788.913 | -5435.2384
234.92 | 11.2316 | 4.9215 |  | 163083.66 | -131454.911 | 616151.466 | 5554174.36 | 4649959.51 | -38844.9759 | 123658.875 | 8611.4454 | 270640.005 | 2218.2231 | 1955333.35 | -29590.9356 | 50640.5092 | 1456.8808 | 62550.3212 | 11485.5012 | 287692.125 | -9923.6233
235.12 | 11.2433 | 4.7107 |  | 197283.758 | -106510.709 | 596542.402 | 5033104.79 | 5317446.08 | -40556.3506 | 122563.359 | 18367.3046 | 265810.07 | -50020.4346 | 1928963.25 | -29786.5283 | 49228.6989 | 725.8315 | 61684.3203 | 18098.3973 | 274838.346 | -10381.9447
235.32 | 11.2642 | 4.5989 |  | 208989.084 | -96446.3338 | 570269.205 | 4492665.78 | 5474834.1 | -48535.9852 | 111450.342 | 25976.6184 | 260089.419 | -217412.999 | 1708980.21 | -29693.0979 | 43754.0271 | 5603.0028 | 60215.8832 | -9594.0912 | 244525.262 | -9782.5579
235.52 | 11.2628 | 4.5295 |  | 217543.605 | -63684.6851 | 542459.986 | 3476076.04 | 5475032.61 | -41153.1037 | 94568.1232 | 33585.954 | 256406.868 | -291798.595 | 1465207.5 | -20168.0182 | 39338.3831 | 5816.8122 | 60072.9716 | -7797.6096 | 238080.196 | -6055.1749
235.72 | 11.2569 | 4.3977 |  | 204890.581 | -47979.8628 | 505573.819 | 3179005.8 | 5218076.09 | -40248.4265 | 94780.1268 | 32085.9263 | 249954.607 | -310042.515 | 1411133.1 | -22485.1797 | 34233.1147 | 7378.9762 | 59085.4597 | -18239.1246 | 197651.173 | -5941.5366
235.92 | 11.2679 | 4.2367 |  | 216834.77 | -54960.2433 | 473586.128 | 3178722.44 | 5238167.36 | -47959.0281 | 87074.069 | 30623 | 243412.587 | -240470.143 | 1311415.48 | -23908.5713 | 34839.987 | 4412.2681 | 58505.6874 | -3194.7999 | 201633.007 | -6959.7774
236.12 | 11.2866 | 4.1435 |  | 199539.263 | -63591.0157 | 437511.972 | 3335367.92 | 5096375.19 | -50438.1178 | 93725.9702 | 30476.0612 | 232429.735 | -294287.716 | 1308036.02 | -29413.2757 | 29364.6973 | 7098.3434 | 55081.934 | -17619.4148 | 165200.868 | -8310.6124
236.32 | 11.266 | 4.0596 |  | 174919.999 | -46383.9465 | 402871.317 | 3018446.58 | 4656870.64 | -31612.7235 | 88979.4295 | 26858.8582 | 228234.284 | -224832.42 | 1466866.58 | -18487.8591 | 40613.9552 | 4748.9868 | 56533.7851 | -10079.5879 | 206851.572 | -6347.6853
236.52 | 11.2618 | 3.8676 |  | 169006.834 | -75536.6116 | 381242.783 | 3800410.81 | 4553889.56 | -52459.3545 | 96868.1599 | 19073.3299 | 221647.35 | -117169.479 | 1567235.03 | -32954.1556 | 40568.6796 | 3107.8027 | 54414.2306 | -343.9076 | 223384.378 | -11085.7285
236.72 | 11.2913 | 3.7167 |  | 144482.369 | -106911.748 | 362677.599 | 4377820.87 | 4185511.39 | -57429.4139 | 101214.21 | 12981.9783 | 216916.72 | -64641.2867 | 1597659.31 | -34536.1686 | 39585.7162 | 2630.4651 | 53597.163 | 34.6769 | 202189.423 | -11126.3924
236.92 | 11.2718 | 3.6512 |  | 98756.6161 | -103837.941 | 342713.525 | 4583405.62 | 3442951.28 | -33388.9633 | 105461.527 | 3645.5957 | 213405.231 | 21189.2458 | 1684972.69 | -26231.7711 | 42766.6631 | 1348.0024 | 53260.069 | 6703.5171 | 240183.949 | -8728.4951
237.12 | 11.2471 | 3.4593 |  | 75732.1502 | -146966.401 | 349982.268 | 5492274.73 | 2799189.74 | -38546.9984 | 107716.404 | -11701.8372 | 216734.733 | 215307.541 | 1699768.19 | -25532.3443 | 43094.0593 | -2320.1648 | 54265.4034 | 23494.1267 | 249480.112 | -9053.4275
237.32 | 11.2922 | 3.2498 |  | 67093.905 | -214641.61 | 348759.909 | 7150114.98 | 2726441.75 | -50109.7005 | 123511.122 | -23421.5042 | 215788.413 | 333759.907 | 1660533.98 | -30849.329 | 37424.7432 | -4396.8033 | 53313.1052 | 33482.0336 | 210552.781 | -8433.0041
237.52 | 11.3114 | 3.2398 |  | 16524.2907 | -223771.696 | 360067.631 | 7275698.23 | 1859747 | -41662.3804 | 120420.578 | -30639.0218 | 217143.205 | 376475.051 | 1818023.89 | -26493.5321 | 45696.379 | -3880.5292 | 53797.624 | 26613.1662 | 245150.323 | -8974.4474
237.72 | 11.2919 | 3.1617 |  | -7664.6472 | -215265.617 | 381492.683 | 7340502.39 | 1383931.14 | -35471.141 | 126043.824 | -39340.4408 | 221987.276 | 570220.772 | 2043072.54 | -27506.455 | 52028.2953 | -9182.5757 | 55582.1662 | 53264.8062 | 274950.562 | -9815.3909
237.92 | 11.3402 | 3.01 |  | -13048.9658 | -269661.594 | 412435.268 | 8409893.59 | 1284628.11 | -54564.8809 | 128948.329 | -45490.3932 | 228673.758 | 604386.578 | 1986215.47 | -33887.4807 | 50173.4206 | -8962.8985 | 55830.6741 | 54808.8105 | 284631.404 | -9317.139
238.12 | 11.3619 | 3.0233 |  | -28778.1441 | -270121.77 | 442848.214 | 8447857.81 | 1088246.34 | -52201.355 | 132207.982 | -47161.7902 | 234795.666 | 614922.031 | 2041344.17 | -33065.0641 | 52320.682 | -8947.3258 | 56726.5285 | 54375.8237 | 294477.045 | -10472.9103
238.32 | 11.3441 | 2.9754 |  | -35711.051 | -286796.818 | 479339.492 | 8800422.64 | 874442.74 | -47838.6527 | 129226.341 | -51651.7783 | 246173.136 | 648115.913 | 2016529.34 | -24430.9618 | 55666.4521 | -9838.643 | 59292.5636 | 55892.215 | 311811.2 | -7241.9801
238.52 | 11.379 | 2.8396 |  | -23467.0345 | -308654.972 | 523239.201 | 9408854.72 | 1025676.61 | -56007.7247 | 140499.151 | -56766.6917 | 256327.871 | 707247.904 | 1995905.43 | -30667.0072 | 49007.6249 | -10412.5409 | 60701.2634 | 63883.1229 | 287559.867 | -10405.2976
238.72 | 11.4016 | 2.8324 |  | -22835.0558 | -314139.155 | 555217.433 | 9569527.22 | 1159198.63 | -55265.4149 | 147692.518 | -55545.2223 | 263179.95 | 670422.056 | 2037346.78 | -29917.1947 | 47074.2864 | -9123.7293 | 61792.175 | 56144.7645 | 261512.028 | -8778.1945
238.92 | 11.3975 | 2.7904 |  | -8212.7183 | -290707.069 | 586032.196 | 9089727.11 | 1287655.49 | -50007.9675 | 142328.088 | -53308.7177 | 269610.191 | 670821.912 | 2114730.61 | -26269.3399 | 51830.6288 | -9010.7747 | 63594.7598 | 54162.7224 | 290787.682 | -9252.2405
239.12 | 11.4389 | 2.6986 |  | 23941.4812 | -281733.13 | 616158.86 | 8990756.01 | 2015665.41 | -45071.5136 | 146488.137 | -44335.0335 | 274247.727 | 607020.074 | 2153073.21 | -24081.7619 | 51955.1198 | -8873.0277 | 63188.1788 | 55318.3472 | 287890.676 | -7089.92
239.32 | 11.4684 | 2.724 |  | 52175.9072 | -264815.672 | 636032.005 | 8791593.73 | 2804261.82 | -41451.4606 | 153202.478 | -32950.347 | 279599.54 | 466512.698 | 2317486.28 | -26622.5441 | 57183.4186 | -6087.2964 | 64913.6652 | 42620.0171 | 315116.229 | -7408.4678
239.52 | 11.4773 | 2.7129 |  | 84553.2489 | -244733.129 | 653292.894 | 8596901.37 | 3492235.22 | -47400.1139 | 160639.5 | -25659.5652 | 284569.216 | 417757.935 | 2495671.68 | -36761.01 | 61862.7532 | -5803.0229 | 66506.5031 | 43262.0549 | 330603.081 | -11390.033
239.72 | 11.5207 | 2.6575 |  | 111994.242 | -214964.401 | 660767.036 | 7834636.63 | 3895752.86 | -50390.4342 | 149822.2 | -16033.5199 | 285739.529 | 344279.473 | 2336024 | -40223.7495 | 59767.6506 | -5678.5159 | 65877.6732 | 49633.2847 | 339851.634 | -13201.9641
239.92 | 11.5495 | 2.6956 |  | 126135.033 | -164068.787 | 662909.12 | 6355043.21 | 3884910.91 | -28299.0059 | 127312.658 | -6088.263 | 287210.769 | 221046.354 | 2064979.52 | -18295.2648 | 54391.2334 | -3640.0956 | 66009.8703 | 37750.2057 | 311582.509 | -3925.4794
240.12 | 11.5762 | 2.6912 |  | 141216.033 | -118732.587 | 656358.5 | 5374112.59 | 4098929.19 | -21369.1414 | 118174.994 | 1772.2325 | 284923.431 | 155262.657 | 2084002.9 | -15122.8395 | 58094.8981 | -3179.2089 | 65776.3839 | 31342.4169 | 322870.616 | -4023.2608
240.32 | 11.6142 | 2.6899 |  | 198108.343 | -135133.166 | 635727.913 | 5867509.3 | 5445059.07 | -40209.0697 | 132801.832 | 14189.9931 | 281415.346 | -3330.1984 | 2088319.55 | -29710.3659 | 54708.4494 | -203.423 | 64963.9442 | 21626.5452 | 301280.535 | -7622.6277
240.52 | 11.6407 | 2.7301 |  | 228975.777 | -133672.228 | 614486.92 | 5807746.58 | 6254472.76 | -36453.9177 | 140820.883 | 24371.3511 | 278826.241 | -213749.096 | 2035295.11 | -31402.2263 | 50056.749 | 5928.6641 | 64494.4016 | -10282.0432 | 274002.776 | -9542.6709
240.72 | 11.6634 | 2.7465 |  | 242696.073 | -113825.794 | 586209.856 | 5190246.92 | 6449631.75 | -43831.2118 | 131641.804 | 31662.7535 | 276697.328 | -287727.774 | 1899904.97 | -32982.4312 | 46451.7924 | 6852.7123 | 65277.1038 | -12639.0631 | 266062.508 | -11033.1378
240.92 | 11.6977 | 2.7594 |  | 230327.405 | -77174.0727 | 551051.647 | 4350868.54 | 6001283.21 | -28522.2507 | 121254.167 | 29936.489 | 270732.751 | -239907.637 | 1816012.49 | -20613.8098 | 44940.885 | 5210.8213 | 64414.2734 | -5722.8689 | 252706.644 | -6251.3018
241.12 | 11.7114 | 2.8102 |  | 221264.658 | -87626.6456 | 523255.868 | 4331890.78 | 5592041.15 | -45295.7897 | 110377.006 | 26320.614 | 265113.379 | -204094.778 | 1685443.94 | -26332.1054 | 43508.4763 | 4644.6331 | 63558.9142 | -4019.9661 | 247233.483 | -7781.7723
241.32 | 11.7134 | 2.8023 |  | 215411.063 | -87685.3626 | 478182.518 | 4260495.04 | 5449133.29 | -49507.8618 | 109776.984 | 24977.6589 | 252639.662 | -175566.307 | 1578739.75 | -31381.1282 | 35671.209 | 4090.492 | 60539.8937 | -383.6872 | 204029.471 | -9660.9528
241.52 | 11.7185 | 2.7534 |  | 191235.434 | -74608.9654 | 445161.74 | 3837046.22 | 5027621.26 | -37288.9047 | 101131.33 | 24350.2146 | 244420.868 | -187936.102 | 1601096.11 | -21351.7191 | 41399.4755 | 4531.6772 | 59235.9067 | -6496.9786 | 231790.477 | -6787.7662
241.72 | 11.7327 | 2.7282 |  | 178933.757 | -90367.8194 | 420218.708 | 4208143.73 | 4997823.62 | -42886.1265 | 106972.414 | 23180.9138 | 239868.84 | -184685.853 | 1682035.11 | -26166.8288 | 43447.6139 | 4608.8429 | 58491.6768 | -4951.5997 | 251804.085 | -8581.0712
241.92 | 11.7383 | 2.717 |  | 160966.376 | -129065.202 | 405481.966 | 5158492.66 | 4788728.21 | -49241.2541 | 117960.777 | 15409.4118 | 240511.107 | -118022.663 | 1751360.04 | -32747.3104 | 42058.7565 | 4098.119 | 59469.4518 | -4024.0819 | 231067.09 | -9280.6218
242.12 | 11.7538 | 2.6759 |  | 121448.618 | -142305.436 | 390399.276 | 5674930.66 | 4002217.21 | -48705.6282 | 119311.128 | 2000.1364 | 237470.404 | 79397.8866 | 1896478.79 | -36856.8787 | 49949.1593 | -337.482 | 59523.4475 | 16483.0606 | 279831.622 | -12661.5707
242.32 | 11.7669 | 2.661 |  | 80322.6919 | -165106.806 | 388830.477 | 6118877.05 | 3018191.38 | -40394.9955 | 116537.521 | -13387.9325 | 236887.303 | 237267.631 | 1813134.61 | -29574.3138 | 47776.1406 | -2750.1255 | 59021.1416 | 29021.0392 | 283846.192 | -9152.5029
242.52 | 11.798 | 2.6631 |  | 51270.6236 | -186968.047 | 393620.181 | 6552966.96 | 2337520.48 | -43003.4544 | 112653.384 | -23807.302 | 235460.678 | 376822.165 | 1814225.94 | -28389.3876 | 49315.7785 | -5635.1898 | 57829.1638 | 41096.7505 | 291078.775 | -10033.2976
242.72 | 11.8098 | 2.7104 |  | 16148.3206 | -207441.459 | 405709.072 | 6941722.11 | 1845252.1 | -51360.2978 | 117832.953 | -29153.1902 | 238215.075 | 403857.043 | 1869115.01 | -35920.2818 | 46867.8671 | -4716.2122 | 58537.1858 | 33005.5675 | 257491.525 | -10498.3056
242.92 | 11.797 | 2.7009 |  | -8972.7274 | -209606.301 | 430067.21 | 6794719.95 | 1265700.91 | -45831.0747 | 108963.53 | -33594.4905 | 244041.9 | 480538.877 | 1847352.81 | -28089.3795 | 50708.8804 | -7097.696 | 59901.712 | 46880.0762 | 294413.85 | -9375.0783
243.12 | 11.7895 | 2.6328 |  | -30669.9186 | -233912.875 | 462103.305 | 7330919.96 | 855470.6 | -53582.7597 | 113422.92 | -40939.6621 | 252560.652 | 544650.121 | 1827550.98 | -32750.5655 | 47302.9036 | -7500.2114 | 61188.5716 | 49059.3939 | 273034.605 | -10185.7014
243.32 | 11.8008 | 2.5702 |  | -34529.0893 | -264708.881 | 500082.684 | 8035261.49 | 721176.859 | -53015.1503 | 120629.701 | -48579.9786 | 262963.562 | 619055.592 | 1761202.94 | -28504.1525 | 42062.8267 | -8514.5348 | 63407.55 | 51866.168 | 236379.2 | -8926.2164
243.52 | 11.7777 | 2.5284 |  | -45131.9975 | -282757.13 | 532784.665 | 8610500.47 | 518056.418 | -52116.1143 | 129648.532 | -55915.316 | 270433.329 | 660966.492 | 1777003.64 | -29934.9248 | 40680.273 | -8208.3985 | 64650.2153 | 47951.8248 | 218709.533 | -9582.4
243.72 | 11.7659 | 2.4412 |  | -42389.0876 | -282361.367 | 566430.919 | 8752161.05 | 525387.331 | -46648.7305 | 133994.18 | -59136.3743 | 276533.4 | 711726.728 | 1808948.98 | -27871.8403 | 41037.0085 | -9525.6477 | 65604.6084 | 56492.4809 | 229674.534 | -10467.6281
243.92 | 11.7705 | 2.3672 |  | -34727.4376 | -272929.404 | 598214.575 | 8505820.92 | 724899.66 | -48063.7608 | 131071.258 | -53552.7801 | 280492.142 | 672706.75 | 1863913.39 | -28687.4132 | 44392.2902 | -9266.6536 | 65764.2557 | 54989.5182 | 236053.452 | -10278.2976
244.12 | 11.7563 | 2.3008 |  | -8793.4185 | -252498.025 | 631206.292 | 7954568.07 | 1183491.5 | -46272.6976 | 125766.169 | -44499.4066 | 286673.665 | 585014.669 | 1894882.28 | -26191.2957 | 47762.5057 | -8011.8893 | 66852.3538 | 50550.4918 | 265470.679 | -8954.7555
244.32 | 11.7412 | 2.1939 |  | 13066.9084 | -227225.485 | 658762.101 | 7536543.65 | 1798481.51 | -42249.0338 | 129259.39 | -34037.9929 | 292019.64 | 484384.558 | 2042426.55 | -27941.7232 | 55066.4134 | -7045.7504 | 67657.7887 | 43862.5456 | 281800.011 | -8312.9733
244.52 | 11.7254 | 2.0732 |  | 52004.5064 | -227013.441 | 672365.237 | 7579191.73 | 2603820.84 | -61495.2753 | 135030.022 | -25405.9524 | 296139.591 | 371846.61 | 2030523.67 | -43314.6191 | 51870.8636 | -4051.7598 | 68396.6792 | 37421.3918 | 304103.026 | -14347.4077
244.72 | 11.6919 | 1.9343 |  | 67833.9426 | -177042.05 | 687303.464 | 6405834.69 | 2660987.39 | -42408.8826 | 121815.514 | -18825.6347 | 299546.372 | 349360.849 | 1931117.91 | -27365.04 | 49335.4721 | -5245.5051 | 69165.3841 | 44076.9339 | 275358.628 | -8279.0289
244.92 | 11.686 | 1.7668 |  | 91269.7085 | -158614.016 | 682270.192 | 5842696.81 | 2941927.63 | -39801.5106 | 112561.629 | -12299.3709 | 296205.879 | 254688.644 | 1756001.91 | -25233.7489 | 44766.3489 | -3032.4123 | 67805.9802 | 33546.3657 | 263158.892 | -9128.3984
245.12 | 11.6646 | 1.6553 |  | 127662.583 | -143596.204 | 674127.401 | 5467808.29 | 3665471.28 | -30452.3229 | 113849.287 | -1832.8334 | 294550.692 | 113667.032 | 1650631.94 | -18256.7888 | 39539.2468 | -444.3448 | 67411.9032 | 20363.7901 | 226748.697 | -4319.6372
245.32 | 11.6391 | 1.5225 |  | 169327.704 | -133479.752 | 655274.863 | 5493849.89 | 4651153.11 | -33885.4811 | 124975.294 | 7490.1093 | 290134.273 | -3576.9596 | 1762238.4 | -22399.1607 | 40793.9261 | 2009.3412 | 66879.6259 | 7831.8866 | 223955.571 | -6164.3089
245.52 | 11.6416 | 1.3815 |  | 210394.222 | -133829.388 | 631334.961 | 5786008.19 | 5678586.74 | -42565.5414 | 139417.424 | 15841.6951 | 285640.468 | -100592.188 | 1889673.85 | -31536.7417 | 40181.1551 | 4069.716 | 66466.1181 | -2665.9812 | 200187.794 | -9732.8568
245.72 | 11.6557 | 1.278 |  | 226424.562 | -121342.343 | 603622.376 | 5508141.77 | 6001453.89 | -38081.9086 | 137758.74 | 20787.2963 | 279976.868 | -166930.04 | 1935394.68 | -28448.9639 | 42734.8092 | 5536.2762 | 65628.4093 | -9840.7513 | 224099.949 | -10489.2167
245.92 | 11.6506 | 1.1973 |  | 229113.304 | -104660.08 | 568337.294 | 5234904.91 | 5988109.03 | -31510.395 | 136396.526 | 20701.8688 | 273326.545 | -183749.482 | 1894909.5 | -26194.0276 | 41483.0285 | 6307.1687 | 64784.191 | -12486.4505 | 229817.635 | -9992.9882
246.12 | 11.6536 | 1.1015 |  | 235683.618 | -103627.376 | 532829.615 | 5025772.69 | 5979113.32 | -41404.8416 | 126853.451 | 23092.6162 | 265325.798 | -156337.126 | 1770048.29 | -28327.9439 | 41202.7864 | 3572.0459 | 63389.5259 | 2431.7182 | 230083.038 | -7870.0404
246.32 | 11.6386 | 1.0476 |  | 210715.919 | -72093.7038 | 492553.27 | 4113817.84 | 5404342.87 | -37151.9861 | 108783.586 | 24746.2872 | 252496.777 | -161156.601 | 1787808.39 | -25374.0598 | 49707.3411 | 3024.1928 | 60347.017 | 5060.7729 | 283958.567 | -7965.1477
246.52 | 11.6198 | 1.0417 |  | 200097.417 | -60026.4275 | 452328.919 | 3782144.7 | 5259793.43 | -35151.9161 | 106414.265 | 25731.9976 | 243037.397 | -155882.684 | 1781719.81 | -24075.5775 | 50303.5311 | 2219.6946 | 58547.7738 | 14690.7284 | 310470.569 | -6415.6562
246.72 | 11.6116 | 1.0468 |  | 185985.603 | -78027.9741 | 422950.958 | 4227188.35 | 5120327.7 | -39110.4904 | 111822.087 | 21888.5705 | 236188.29 | -138009.985 | 1876114.36 | -26877.559 | 51392.7786 | 3045.3431 | 57154.6334 | 7105.2005 | 308395.982 | -8118.0279
246.92 | 11.5955 | 1.0737 |  | 174857.993 | -117618.236 | 397915.354 | 5249810.03 | 5085157.64 | -45067.7269 | 123657.039 | 15396.9692 | 233085.005 | -79217.9299 | 1942423 | -31843.4775 | 48795.7028 | 2669.3288 | 57483.0165 | 6503.819 | 288162.933 | -9300.8711
247.12 | 11.5769 | 1.1108 |  | 135742.006 | -135126.791 | 379113.356 | 5836515.17 | 4351520.65 | -39800.4965 | 130470.645 | 2050.3864 | 229130.373 | 85513.8831 | 2119613.25 | -32019.4032 | 52098.851 | 67.5011 | 57611.6882 | 10848.1386 | 263189.046 | -10600.6869
247.32 | 11.5859 | 1.1551 |  | 111415.976 | -170703.754 | 369158.688 | 6527606.99 | 3690731.29 | -49391.3093 | 123461.538 | -9920.645 | 227061.806 | 253803.393 | 2017506.29 | -31305.5289 | 56901.9276 | -4999.4806 | 57134.517 | 41277.9609 | 333201.741 | -8587.7535
247.52 | 11.6092 | 1.1974 |  | 60161.7823 | -169760.238 | 367767.424 | 6534819.56 | 2668123.91 | -39163.0594 | 120983.808 | -21085.4011 | 222529.048 | 370727.745 | 2095196.54 | -29183.1278 | 60097.0045 | -6479.7164 | 54886.3763 | 48326.9145 | 348243.707 | -9370.5038
247.72 | 11.6298 | 1.2103 |  | 35232.5871 | -192305.644 | 375019.12 | 6962746.89 | 2293368.05 | -40433.6067 | 123523.828 | -26017.1122 | 225111.388 | 423494.128 | 2043921.68 | -31143.5878 | 56745.4227 | -7576.1961 | 55682.9908 | 55263.4542 | 335969.98 | -8594.3922
247.92 | 11.6349 | 1.2141 |  | 4720.4042 | -207426.893 | 399870.118 | 7070144.88 | 1696902.37 | -45061.9965 | 119733.856 | -31632.5855 | 230980.489 | 455659.754 | 2021486.11 | -31509.6422 | 55905.8873 | -6777.623 | 56413.4427 | 46238.1689 | 321320.935 | -9812.3698
248.12 | 11.6233 | 1.2193 |  | -25023.9341 | -215918.587 | 427622.169 | 7060794.65 | 1033302.25 | -50423.5682 | 116298.443 | -38330.4365 | 240216.222 | 512911.608 | 1902073.23 | -36954.1112 | 50665.4875 | -6917.7428 | 58877.7801 | 46471.8578 | 296769.383 | -11674.3628
248.32 | 11.6248 | 1.2263 |  | -46022.5995 | -216472.277 | 460039.264 | 6771644.59 | 347243.01 | -47056.3894 | 99609.603 | -43050.8146 | 247428.062 | 600955.311 | 1714811.48 | -29048.5142 | 50641.0426 | -10064.3812 | 59705.117 | 65686.5944 | 311291.97 | -8981.7146
248.52 | 11.6219 | 1.2338 |  | -67879.4783 | -220436.634 | 492158.922 | 6895083.12 | -101960.192 | -36023.8311 | 96125.9182 | -48058.7171 | 254192.737 | 639605.412 | 1642765.93 | -25427.1091 | 48955.4714 | -10306.5694 | 60503.5884 | 65035.5738 | 298401.642 | -8127.2355
248.72 | 11.5965 | 1.2402 |  | -63540.8284 | -239188.658 | 531556.287 | 7175932.04 | -123312.661 | -50605.0067 | 98659.5216 | -50927.8257 | 263692.778 | 654274.428 | 1587936.61 | -32907.0419 | 44350.4981 | -9548.5932 | 62661.775 | 59175.3666 | 264723.389 | -10320.0233
248.92 | 11.57 | 1.2377 |  | -70154.5768 | -209475.298 | 560615.773 | 6596613.22 | -237424.654 | -35953.9033 | 99442.1105 | -48980.9674 | 267497.2 | 645582.74 | 1582986.58 | -29026.6274 | 42253.4898 | -9764.1087 | 62594.8255 | 60678.0718 | 244939.905 | -9718.7346
249.12 | 11.5677 | 1.2317 |  | -53569.775 | -197987.717 | 592415.337 | 6254318.76 | 43143.1557 | -28515.5249 | 96776.4997 | -43961.4178 | 274060.163 | 574562.397 | 1534082.74 | -19555.8923 | 40998.782 | -8302.4276 | 63687.4729 | 55232.3445 | 251117.556 | -6649.3005
249.32 | 11.5569 | 1.2249 |  | -21610.932 | -204401.277 | 625945.178 | 6478411.93 | 864864.682 | -34880.6773 | 107452.241 | -35614.0108 | 282229.143 | 486875.692 | 1637182.19 | -20966.4981 | 39575.6662 | -6635.5838 | 65072.8357 | 49074.1344 | 248003.452 | -4861.7759
249.52 | 11.5246 | 1.219 |  | 5750.3503 | -203242.466 | 648865.261 | 6780926.27 | 1507950.57 | -57428.955 | 116477.787 | -31031.1973 | 287785.767 | 434379.294 | 1886486.02 | -41821.161 | 48139.4768 | -4740.0404 | 66846.1302 | 36350.8896 | 267366.703 | -15617.5357
249.72 | 11.4879 | 1.2139 |  | 39940.7653 | -186540.307 | 660919.972 | 6433231.63 | 2018038.92 | -51409.738 | 112729.002 | -24905.2952 | 289006.865 | 425818.217 | 1858317.61 | -34041.2097 | 49276.2585 | -6724.3234 | 66810.4357 | 49785.9724 | 281955.798 | -10902.0511
249.92 | 11.4689 | 1.2084 |  | 56002.5847 | -154778.958 | 668413.605 | 5695055.65 | 2199879.21 | -40712.4267 | 101632.675 | -18167.7786 | 287462.616 | 360897.201 | 1843239.31 | -25116.8442 | 54308.8937 | -6409.1311 | 65891.1831 | 49748.1437 | 311684.411 | -8350.0491
250.12 | 11.4447 | 1.2021 |  | 99581.7156 | -148157.802 | 658137.325 | 5696708.84 | 3169631.86 | -34428.6364 | 112282.217 | -8582.4445 | 284325.383 | 228645.685 | 1787398.01 | -22060.2182 | 48455.6101 | -3770.274 | 64809.2964 | 40007.565 | 288876.356 | -6202.9782
250.32 | 11.4096 | 1.1963 |  | 139262.579 | -147935.881 | 653381.893 | 5820708.24 | 4101709.18 | -35406.3122 | 123321.972 | 532.4319 | 283893.331 | 97959.6314 | 1858681.12 | -23039.1763 | 45331.7122 | -314.6172 | 65193.5717 | 17792.7709 | 246255.328 | -5811.7435
250.52 | 11.3757 | 1.1914 |  | 170997.129 | -115317.017 | 624491.757 | 5588001.25 | 4873216.99 | -25246.4317 | 132090.562 | 7657.418 | 276751.16 | 85764.5388 | 2192671.4 | -24260.082 | 59908.1204 | -2296.9141 | 65292.0495 | 24221.0524 | 296550.001 | -6508.7639
250.72 | 11.3655 | 1.1864 |  | 201591.78 | -112510.432 | 596206.414 | 5709882.58 | 5547918.99 | -40773.9768 | 140613.164 | 12999.8084 | 267188.996 | 7630.5626 | 2279546.57 | -35624.9879 | 61255.5227 | -10.7611 | 62393.0571 | 22402.251 | 342634.86 | -12893.741
250.92 | 11.3269 | 1.1802 |  | 219924.146 | -117879.905 | 568497.873 | 5688594.21 | 5878401.79 | -32858.0612 | 140975.681 | 16482.2779 | 262825.523 | -45860.5529 | 2185546.03 | -25779.1442 | 55047.0155 | 1177.699 | 61805.8235 | 14737.957 | 309639.186 | -6731.5439
251.12 | 11.2859 | 1.1748 |  | 220959.313 | -103124.345 | 526930.489 | 5431407.72 | 5806455.6 | -34150.867 | 139475.892 | 15571.886 | 252873.933 | -37667.9305 | 2174711 | -26513.5003 | 53782.8067 | 1445.1549 | 60296.1028 | 11906.3136 | 298370.27 | -8066.8118
251.32 | 11.2488 | 1.17 |  | 222824.343 | -104485.643 | 488544.953 | 5314374.29 | 5736925.47 | -27458.6773 | 131889.308 | 15788.1163 | 242264.449 | -20599.8896 | 2082208.52 | -19146.7517 | 53274.0877 | 110.2567 | 57710.4774 | 20602.408 | 305751.945 | -5973.7831
251.52 | 11.2063 | 1.1657 |  | 214396.396 | -117113.089 | 445964.954 | 5622990.71 | 5657441.23 | -24774.9194 | 133437.224 | 14953.3084 | 231595.116 | -44070.2835 | 2090019.45 | -18929.8226 | 52790.677 | 1166.7203 | 55881.5531 | 12361.1671 | 296102.678 | -5248.2558
251.72 | 11.1693 | 1.1617 |  | 220498.109 | -134915.681 | 411715.913 | 6214751.14 | 5907643.63 | -26711.3552 | 147168.754 | 11496.4932 | 223485.23 | 2713.1956 | 2215149.68 | -23621.6288 | 52422.6576 | 459.7991 | 54815.1233 | 13016.9433 | 278751.095 | -6484.2661
251.92 | 11.133 | 1.1578 |  | 208988.027 | -164829.735 | 378127.393 | 6928158.39 | 5904966.48 | -34424.7249 | 153216.339 | 9456.8818 | 214935.334 | -26904.353 | 2247587.07 | -31638.7405 | 54729.5454 | 1867.2182 | 52959.5312 | 6906.6342 | 300697.869 | -8911.1043
252.12 | 11.0778 | 1.1544 |  | 174104.048 | -135877.968 | 347204.875 | 6328023.62 | 5177056.99 | -30725.7727 | 144996.367 | 4901.0991 | 207139.752 | 91311.3545 | 2318089.84 | -31186.26 | 60788.6198 | -2218.3757 | 52207.3299 | 27500.6534 | 332459.25 | -9386.0922
252.32 | 11.0432 | 1.1518 |  | 126438.652 | -125420.164 | 328343.043 | 5901696.29 | 4014471.75 | -31394.9007 | 129557.339 | -5625.6568 | 199970.485 | 221972.13 | 2234844.29 | -29292.795 | 61479.1779 | -4389.5931 | 50016.09 | 36960.7127 | 347152.138 | -10236.4809
252.52 | 10.9906 | 1.1486 |  | 96217.5354 | -156703.3 | 317326.41 | 6079526.31 | 3205941.79 | -40189.0135 | 113755.913 | -12514.673 | 199045.086 | 270055.566 | 1858928.21 | -28573.9949 | 53522.5357 | -5597.4223 | 49753.1919 | 46355.002 | 320371.469 | -7874.6046
252.72 | 10.9295 | 1.146 |  | 51978.7433 | -148368.348 | 309418.849 | 5558043.16 | 2134669.44 | -26712.9676 | 97419.9813 | -19299.761 | 195171.853 | 360700.435 | 1669767.92 | -16300.8015 | 49735.8545 | -8047.2585 | 48503.088 | 56934.7014 | 294076.498 | -3017.9221
252.92 | 10.8891 | 1.1441 |  | 18664.3495 | -169131.683 | 315344.543 | 5812557.21 | 1435414.41 | -30480.943 | 91812.1014 | -27282.1589 | 194393.967 | 398481.523 | 1622699.02 | -21630.3007 | 49375.1074 | -6564.8748 | 47799.4038 | 45697.2864 | 301835.785 | -7235.7387
253.12 | 10.8387 | 1.1417 |  | 2027.1404 | -191252.995 | 322574.569 | 6244633.07 | 1306157.07 | -42516.7379 | 101203.782 | -29988.0447 | 196093.161 | 412546.628 | 1579867.31 | -30498.8406 | 42400.7823 | -6162.2817 | 48194.289 | 43251.8064 | 253829.151 | -9737.9106
253.32 | 10.764 | 1.1396 |  | -31903.9505 | -197137.853 | 344552.745 | 6170174.2 | 547705.254 | -39194.4796 | 93149.7095 | -37203.9402 | 201879.625 | 471959.46 | 1521046.76 | -25674.4986 | 42644.1417 | -6509.5019 | 49466.0621 | 41556.1399 | 257108.086 | -8723.964
253.52 | 10.7118 | 1.1383 |  | -62641.7364 | -190913.929 | 363561.406 | 6064668.23 | -190765.264 | -29541.6802 | 87707.3219 | -45447.8322 | 205497.373 | 588567.277 | 1467328.02 | -22028.5342 | 42338.5681 | -9331.7887 | 50166.778 | 58350.1508 | 265124.684 | -8656.8534
253.72 | 10.6647 | 1.1368 |  | -70954.3808 | -223718.169 | 392846.971 | 6627429.91 | -455848.92 | -33318.3487 | 87598.5074 | -51637.1447 | 210760.056 | 660382.12 | 1389021.69 | -21192.1222 | 37427.5241 | -10315.7446 | 50482.75 | 61973.7112 | 237460.141 | -7761.3533
253.92 | 10.5967 | 1.1355 |  | -84437.8348 | -222747.582 | 421010.053 | 6876613.25 | -630853.009 | -20953.5763 | 101319.054 | -58070.8597 | 216132.005 | 717947.182 | 1522096.32 | -16721.6261 | 33004.4286 | -9696.2365 | 51811.5472 | 53658.1446 | 191130.003 | -5601.8066
254.12 | 10.5582 | 1.1346 |  | -70913.1069 | -234642.428 | 442871.492 | 7166994.79 | -277444.65 | -41343.322 | 103334.897 | -54534.053 | 217364.179 | 702840.387 | 1544901.04 | -29605.8269 | 37291.4579 | -10730.5368 | 51225.5452 | 61581.1928 | 219643.422 | -11593.9257
254.32 | 10.4875 | 1.1331 |  | -76165.7711 | -209503.564 | 476702.491 | 6524205.37 | -379152.177 | -30464.1062 | 96682.7538 | -49934.5358 | 223991.946 | 623283.495 | 1540418.04 | -22777.1493 | 40690.3979 | -9017.1983 | 52549.3484 | 53238.2983 | 232101.99 | -7471.1371
254.52 | 10.4067 | 1.1326 |  | -72897.5222 | -183491.875 | 497162.625 | 5852076.31 | -442357.217 | -20281.1601 | 84395.3706 | -46075.0143 | 227227.912 | 632044.272 | 1598568.29 | -16482.667 | 47315.3378 | -10519.3725 | 53161.0747 | 61231.105 | 273276.193 | -6194.9272
254.72 | 10.3691 | 1.1326 |  | -45766.908 | -184611.634 | 523249.679 | 6174390.03 | 134823.114 | -23987.7914 | 98094.9655 | -44793.6914 | 232093.567 | 654594.809 | 1750755.88 | -19028.0947 | 48933.1062 | -11638.9973 | 54168.4178 | 66934.9185 | 267509.185 | -6089.0883
254.92 | 10.3557 | 1.1314 |  | -38672.928 | -200123.218 | 543876.595 | 6802509.37 | 546419.613 | -31733.2245 | 118222.062 | -39958.6897 | 234482.041 | 511465.675 | 1909828 | -24902.1051 | 47226.6997 | -7531.6884 | 53071.5738 | 56238.3598 | 259163.209 | -6498.6268
255.12 | 10.2285 | 1.1303 |  | 15112.5924 | -200099.669 | 549897.561 | 6932418.98 | 1509761.08 | -36668.4455 | 121085.439 | -35897.4482 | 236918.302 | 546682.966 | 1903815.86 | -26761.3038 | 48231.5143 | -9748.591 | 55438.9378 | 62403.1961 | 270243.093 | -8265.2228
255.32 | 10.1994 | 1.1312 |  | 47368.6059 | -178153.029 | 555247.674 | 6519405.49 | 2035189.45 | -33978.3062 | 118077.055 | -30097.6847 | 232466.139 | 488589.72 | 1881109.88 | -25663.843 | 48248.9977 | -8617.369 | 52712.804 | 56857.1453 | 270385.493 | -7995.4195
255.52 | 10.1683 | 1.1304 |  | 66421.74 | -149274.451 | 551716.255 | 5629544.05 | 2527294.95 | -28597.658 | 106789.263 | -14342.9927 | 229988.175 | 269866.857 | 1771344.5 | -21507.6724 | 49885.3336 | -4626.3371 | 52024.6062 | 40412.0665 | 291637.019 | -7398.7562
255.72 | 10.0885 | 1.1296 |  | 96536.0111 | -115048.599 | 548463.028 | 4772381.3 | 3045947.1 | -23771.2373 | 101862.101 | -3747.5788 | 231001.861 | 160118.397 | 1661995.4 | -15351.3386 | 45712.5638 | -3273.2097 | 52809.5456 | 34825.9303 | 263290.615 | -4379.4169
255.92 | 10.067 | 1.1303 |  | 130611.497 | -109738.401 | 538041.096 | 4816452.12 | 3650090.42 | -20457.7846 | 110755.432 | -2131.626 | 229392.85 | 122411.125 | 1633547.69 | -10903.52 | 39879.3613 | -1608.6226 | 52486.978 | 24796.0117 | 229581.161 | -2519.0935
256.12 | 10.0528 | 1.1298 |  | 161538.855 | -121415.641 | 514256.504 | 5291784.28 | 4379713.67 | -30120.4618 | 120939.522 | 3230.8266 | 223241.985 | 35106.5171 | 1740466.46 | -21062.7587 | 40563.1132 | 1048.08 | 51498.1776 | 9185.4112 | 222739.801 | -6115.08
256.32 | 9.9678 | 1.1292 |  | 182779.42 | -106576.765 | 487295.498 | 5077797.68 | 4877771.87 | -32219.8216 | 123892.763 | 9709.9932 | 215316.57 | 8811.775 | 1886881.77 | -23755.2593 | 45257.4209 | 478.7846 | 50296.6093 | 11243.3195 | 238116.044 | -7276.1199
256.52 | 9.9231 | 1.1306 |  | 191213.654 | -79685.9862 | 452165.791 | 4603720.07 | 4999889.21 | -25411.7064 | 120373.015 | 12852.6637 | 205535.316 | -1194.1508 | 1944972.4 | -20485.3448 | 49888.2896 | -268.4248 | 48537.9737 | 16867.5477 | 273816.254 | -5827.1799
256.72 | 9.9072 | 1.1346 |  | 204602.726 | -65242.5433 | 418683.714 | 4312498.78 | 5262435.88 | -22759.4395 | 116881.764 | 17568.4623 | 195377.388 | -10949.7116 | 1976337.54 | -16629.2677 | 54338.3763 | -2004.0116 | 46027.6505 | 30131.9948 | 308087.027 | -5201.0231
256.92 | 9.8551 | 1.1395 |  | 213715.845 | -102380.337 | 392057.225 | 4941797.02 | 5505025.31 | -32758.3526 | 122600.128 | 18103.7443 | 190860.511 | -123372.399 | 1848816.86 | -19631.2181 | 45944.5271 | 2953.0707 | 45309.5764 | 2198.531 | 258153.703 | -4659.6637
257.12 | 9.7832 | 1.1437 |  | 213777.854 | -86738.122 | 350331.682 | 4755523.58 | 5467325.27 | -24876.8658 | 122476.07 | 16694.6076 | 181505.423 | -42850.9141 | 1894388.25 | -19983.8799 | 48652.2849 | -596.4923 | 44321.9783 | 16999.5599 | 263700.338 | -4149.6905
257.32 | 9.7687 | 1.1472 |  | 194799.039 | -79552.8141 | 316285.932 | 4557937.16 | 5071417.38 | -26012.4073 | 113053.697 | 15688.0446 | 168947.797 | -34977.4354 | 1907726.86 | -20239.2674 | 53447.8083 | -703.9204 | 40855.0209 | 21295.0677 | 305757.552 | -7603.0511
257.52 | 9.7311 | 1.1502 |  | 192605.119 | -99157.605 | 287848.077 | 4847259.38 | 5100907.39 | -22892.4118 | 116256.225 | 15445.9518 | 164551.036 | -39522.3788 | 1787541.84 | -14404.4488 | 45925.8558 | -905.2686 | 40610.2038 | 23305.3871 | 254565.38 | -1772.7947
257.72 | 9.7058 | 1.153 |  | 167365.003 | -96104.4432 | 260711.822 | 4980877.98 | 4620021.83 | -20968.3656 | 120644.047 | 7122.9435 | 156589.428 | 7618.268 | 1884781.49 | -18007.1587 | 47084.7476 | 451.9229 | 38876.4096 | 8812.4363 | 256602.159 | -5775.4647
257.92 | 9.6953 | 1.1561 |  | 160144.08 | -127163.94 | 237892.101 | 5559546.1 | 4554753.01 | -22997.6181 | 124003.206 | 3363.174 | 152353.379 | 36337.1316 | 1822177.88 | -18937.6855 | 44909.0381 | -381.3277 | 38493.1656 | 14251.5535 | 249561.934 | -5293.1257
258.12 | 9.6764 | 1.159 |  | 127611.388 | -126410.213 | 218601.331 | 5504658.17 | 3971651.75 | -22802.3389 | 120980.758 | -1628.8025 | 146573.442 | 81307.4411 | 1846258.05 | -19819.8001 | 45911.5494 | -664.413 | 37081.453 | 15436.0318 | 254792.615 | -6754.1727
258.32 | 9.6268 | 1.1611 |  | 89287.1689 | -118158.627 | 207530.431 | 5121738.9 | 3066128.63 | -22049.498 | 105561.816 | -7741.945 | 144076.324 | 179466.826 | 1787596.72 | -22438.2068 | 50870.6907 | -3398.9809 | 37075.466 | 29384.5831 | 297362.739 | -8404.951
258.52 | 9.6096 | 1.1631 |  | 61309.184 | -123150.861 | 203121.235 | 4899004.16 | 2304163.58 | -25532.8584 | 90922.7238 | -13337.2498 | 141593.745 | 286634.3 | 1605939.29 | -18716.5038 | 47995.5787 | -6744.2598 | 35894.9644 | 48900.2679 | 282887.459 | -6607.3151
258.72 | 9.5973 | 1.1651 |  | 28950.1288 | -142236.717 | 205572.382 | 4975772.01 | 1591070.16 | -26646.2184 | 83381.454 | -19463.2616 | 142466.42 | 289884.173 | 1362116 | -17317.3414 | 38814.001 | -4983.2362 | 35881.3223 | 36610.3708 | 231359.947 | -5108.2789
258.92 | 9.5474 | 1.1665 |  | -5577.1608 | -136326.741 | 215027.532 | 4655539.11 | 861777.219 | -18371.7696 | 77298.5763 | -24748.9926 | 145019.339 | 339080.832 | 1250307.79 | -15596.9386 | 34219.4731 | -5413.1266 | 36499.5405 | 36025.5887 | 201493.654 | -4504.7514
259.12 | 9.4917 | 1.1676 |  | -33530.3634 | -146150.557 | 223402.26 | 4687012.97 | 182778.512 | -21943.801 | 68279.8493 | -31556.6202 | 146530.576 | 408090.038 | 1139694.8 | -17777.1577 | 31816.3896 | -6136.7245 | 36642.6112 | 38331.2724 | 197932.632 | -6973.0277
259.32 | 9.4679 | 1.1685 |  | -49172.7089 | -169997.973 | 246863.872 | 4833897.11 | -276576.312 | -24194.5968 | 60419.3616 | -36106.643 | 151339.877 | 465399.78 | 966494.791 | -16587.5096 | 27463.0264 | -7444.1537 | 37319.0708 | 43181.0638 | 169157.146 | -6181.3567
259.52 | 9.4269 | 1.1689 |  | -73774.1984 | -181758.543 | 265441.066 | 4990525.45 | -731787.791 | -18299.9874 | 56823.8917 | -39362.3418 | 154888.277 | 460801.29 | 879410.839 | -13991.9646 | 24764.7513 | -6419.6887 | 37555.1776 | 37353.9565 | 156065.868 | -5940.232
259.72 | 9.3909 | 1.1694 |  | -82871.4499 | -192992.476 | 292570.447 | 5151183.9 | -998444.7 | -22228.8056 | 54151.1551 | -43257.729 | 161819.571 | 518295.629 | 845939.956 | -12251.2268 | 24662.7594 | -7863.504 | 39302.9764 | 44187.6421 | 154911.667 | -5213.0667
259.92 | 9.3798 | 1.1701 |  | -91240.0555 | -187675.424 | 316614.353 | 5281996.52 | -1053959.64 | -8950.8359 | 62375.2639 | -46095.7143 | 165891.443 | 575254.229 | 987430.805 | -12467.3443 | 27492.5328 | -9371.9711 | 39595.7927 | 50797.8608 | 156483.504 | -4813.3016
260.12 | 9.3608 | 1.1704 |  | -89581.0122 | -196274.678 | 344694.468 | 5679355.57 | -865810.861 | -16783.2454 | 73628.5818 | -47853.1769 | 171911.763 | 566246.256 | 1120866.99 | -18124.6265 | 29552.8969 | -7951.0426 | 40703.8999 | 43767.7302 | 169471.622 | -8086.1349
260.32 | 9.3336 | 1.1709 |  | -75558.178 | -200565.544 | 376167.734 | 5866169.77 | -535895.949 | -17587.1694 | 81485.1729 | -46368.0576 | 179199.851 | 566008.823 | 1165788.64 | -15605.8257 | 27429.4186 | -8267.8652 | 42007.5565 | 47117.2881 | 156448.399 | -5977.7039
260.52 | 9.3251 | 1.1723 |  | -75988.7106 | -187039.45 | 400467.407 | 5661881.72 | -555025.168 | -15897.0795 | 79146.1951 | -45687.6279 | 183854.655 | 576954.147 | 1302841.92 | -13958.6586 | 33968.9763 | -8573.9535 | 42905.4689 | 47573.36 | 190788.534 | -6545.8116
260.72 | 9.313 | 1.1728 |  | -48846.0128 | -207653.276 | 426881.319 | 6253366.96 | 74882.7476 | -26030.5805 | 91824.9523 | -42698.9439 | 190035.53 | 527256.042 | 1313317.35 | -18384.3492 | 31274.8599 | -7594.5559 | 43817.8616 | 43667.7958 | 168364.274 | -6092.8261
260.92 | 9.2741 | 1.1729 |  | -31389.8334 | -205688.202 | 445127.227 | 6261991.39 | 438875.573 | -33640.2919 | 94340.6459 | -39117.6696 | 193463.045 | 498678.208 | 1384257.04 | -20458.9331 | 34281.1628 | -7451.2654 | 44634.5051 | 45448.9856 | 195692.059 | -6775.4594
261.12 | 9.2465 | 1.1728 |  | -12373.0875 | -186289.276 | 462541.804 | 5890259.93 | 708396.092 | -29230.0624 | 89794.7337 | -34737.9218 | 196022.84 | 465996.219 | 1431261.25 | -18568.1309 | 38300.0673 | -7084.3954 | 44970.8036 | 43332.2166 | 215977.782 | -7386.2438
261.32 | 9.2146 | 1.1728 |  | 10483.371 | -171795.426 | 473918.503 | 5612933.99 | 1166261.12 | -29674.6507 | 91971.8317 | -28468.2943 | 197408.762 | 404241.753 | 1419557.18 | -18167.0577 | 37618.1481 | -6570.8893 | 44847.0042 | 43422.6644 | 215173.578 | -6219.2284
261.52 | 9.182 | 1.1728 |  | 30248.918 | -149332.39 | 480838.805 | 5152549.22 | 1543764.19 | -21403.4514 | 91851.5904 | -22132.5415 | 198337.114 | 317725.159 | 1432933.24 | -15166.4058 | 37239.7691 | -4616.7313 | 45101.3445 | 34927.4682 | 215706.922 | -5339.3322
261.72 | 9.1447 | 1.1728 |  | 63241.3977 | -131858.817 | 480435.603 | 4784628.15 | 2183282.22 | -25298.1533 | 90597.3064 | -12810.8996 | 197412.247 | 245860.893 | 1421085.17 | -15814.6276 | 36467.0983 | -4051.1083 | 44818.6673 | 32224.3657 | 203922.41 | -4832.8608
261.92 | 9.1185 | 1.1728 |  | 82499.5011 | -106048.108 | 478355.532 | 4256161.91 | 2559486.63 | -22829.6321 | 87242.5899 | -5341.4372 | 195885.744 | 172459.322 | 1488831.3 | -13976.8037 | 39835.0821 | -2732.0998 | 44389.9537 | 23407.55 | 216459.139 | -4995.6328
262.12 | 9.1027 | 1.1734 |  | 117187.483 | -100004.277 | 467757.044 | 4280541.12 | 3330088.67 | -26286.1395 | 95325.6696 | 1824.1297 | 193566.342 | 82286.453 | 1518991.12 | -15760.5515 | 37766.938 | -680.1899 | 44124.0834 | 12960.9579 | 201245.322 | -4734.5507
262.32 | 9.0945 | 1.1768 |  | 145760.709 | -100748.253 | 456833.901 | 4436318.76 | 3998748.27 | -30477.4974 | 103280.644 | 7826.5509 | 191237.502 | 2424.4601 | 1573155.43 | -17664.8716 | 39178.9705 | 379.5203 | 43720.801 | 10593.502 | 212601.014 | -5153.2335
262.52 | 9.0958 | 1.1814 |  | 171068.845 | -90618.0526 | 434226.134 | 4367605.66 | 4557722.4 | -26892.6865 | 109238.121 | 13331.2381 | 185939.036 | -64225.1374 | 1635662.25 | -19824.8334 | 39760.52 | 1586.4587 | 42855.9402 | 6358.4616 | 214069.799 | -5755.152
262.72 | 9.0932 | 1.1867 |  | 187278.173 | -75076.8354 | 415488.522 | 3971369.07 | 4849848.13 | -28038.6717 | 104606.197 | 19338.0975 | 181542.447 | -118333.266 | 1608832.67 | -19007.7789 | 41891.7034 | 1651.7658 | 41978.3864 | 8469.1746 | 234549.009 | -5219.2028
262.92 | 9.1101 | 1.1919 |  | 193552.226 | -44810.6902 | 387142.443 | 3386273.15 | 4970484.57 | -28344.0298 | 102198.902 | 23248.9849 | 174521.261 | -144274.563 | 1640339.53 | -19469.0124 | 42751.8785 | 2006.1643 | 40675.206 | 7796.0081 | 244877.424 | -5763.3235
263.12 | 9.1199 | 1.1964 |  | 198077.199 | -33216.8718 | 359559.903 | 2972509.46 | 5050986.49 | -36583.4643 | 95206.6958 | 28590.9431 | 168249.747 | -203829.577 | 1589958.47 | -21790.7163 | 42378.6532 | 2926.8832 | 39546.6404 | 3249.0559 | 237217.801 | -6320.8843
263.32 | 9.1166 | 1.2008 |  | 195035.59 | -17399.9272 | 334225.711 | 2305978.95 | 4866518.31 | -42144.823 | 80498.3673 | 32715.8809 | 163203.622 | -262326.211 | 1379567.61 | -19941.3721 | 38771.3474 | 3806.1158 | 38755.1788 | -467.0113 | 225395.604 | -5177.9237
263.52 | 9.1167 | 1.2062 |  | 186152.09 | -1069.2364 | 303609.288 | 1630154.98 | 4496271.37 | -39484.0317 | 65894.0899 | 33604.6444 | 156739.783 | -272225.623 | 1165385.68 | -16922.8268 | 33508.2163 | 3826.7529 | 37563.9888 | -1012.8742 | 199776.952 | -3696.3522
263.72 | 9.1377 | 1.2119 |  | 177957.935 | 1699.4889 | 279198.734 | 1393551.68 | 4289074.64 | -37894.7189 | 62766.448 | 32956.5503 | 151120.89 | -299790.395 | 1034006.13 | -13901.5156 | 26079.7598 | 5677.9137 | 36322.3021 | -14091.5486 | 152679.675 | -2588.8837
263.92 | 9.12 | 1.2174 |  | 169101.733 | -11849.3663 | 252621.214 | 1707749.21 | 4200879 | -36823.9039 | 64263.4042 | 30898.4975 | 146571.96 | -283966.471 | 1095770.91 | -13919.8528 | 28287.4922 | 5590.6888 | 36203.7532 | -15585.716 | 156473.3 | -2092.6125
264.12 | 9.1373 | 1.2237 |  | 166878.535 | -36548.6411 | 229944.135 | 2493183.24 | 4274567 | -47094.5792 | 74819.7253 | 25535.2184 | 140628.305 | -208478.667 | 1240193.47 | -25302.0235 | 33711.6189 | 3762.685 | 34798.5023 | -6014.0414 | 190019.142 | -8374.6105
264.32 | 9.1696 | 1.2291 |  | 156136.724 | -68868.9596 | 208136.976 | 3278590.63 | 4264050.63 | -42868.0628 | 87197.8267 | 21322.0828 | 135671.066 | -200571.23 | 1266561.58 | -23985.6672 | 30243.4196 | 4414.9985 | 33658.7162 | -9345.2126 | 171120.028 | -6445.5975
264.52 | 9.1927 | 1.234 |  | 127842.302 | -73584.3805 | 191544.227 | 3384471.09 | 3729139.86 | -37584.8946 | 83668.2339 | 15677.0726 | 133231.162 | -142718.564 | 1269430.97 | -23694.9589 | 31901.3521 | 3576.8309 | 33831.5344 | -6965.3757 | 179369.061 | -7621.5073
264.72 | 9.2389 | 1.2386 |  | 97354.5605 | -69838.2539 | 186138.136 | 3101872.32 | 2952773.93 | -29579.7308 | 71453.9953 | 9211.4672 | 132403.031 | -39963.4318 | 1188621.65 | -17134.1905 | 32525.1423 | 945.2853 | 33641.6974 | 6752.1942 | 192716.42 | -6101.0034
264.92 | 9.2815 | 1.2424 |  | 60523.7924 | -81940.9579 | 185128.623 | 3268226.03 | 2163138.01 | -16137.354 | 66366.7666 | 27.3506 | 133715.536 | 54216.3183 | 1163349.59 | -10640.8473 | 33672.4417 | -656.1774 | 33877.0778 | 14698.9984 | 204379.159 | -3229.8096
265.12 | 9.3431 | 1.2457 |  | 43921.5728 | -110238.383 | 187328.341 | 3946989.61 | 1865336.83 | -26143.7545 | 71201.3776 | -7869.9089 | 134690.306 | 166097.486 | 1194722.66 | -17032.0656 | 33209.3372 | -2906.3916 | 34176.5109 | 25106.9812 | 196330.525 | -5665.2206
265.32 | 9.3882 | 1.2484 |  | 19170.748 | -137663.763 | 198075.274 | 4454747.91 | 1466992.15 | -33719.1542 | 73725.8666 | -13704.2004 | 137097.936 | 206972.453 | 1219880.58 | -20599.4587 | 33647.0866 | -2848.7896 | 34354.6834 | 23272.1893 | 197793.991 | -7206.8766
265.52 | 9.4388 | 1.2514 |  | -6134.3548 | -144718.483 | 212012.025 | 4497937.57 | 942386.919 | -28472.4345 | 69260.9301 | -18436.9457 | 142191.149 | 254755.949 | 1160430.44 | -17719.0949 | 32752.2804 | -3688.7284 | 35921.6319 | 26919.0728 | 193096.209 | -6391.8519
265.72 | 9.4956 | 1.2551 |  | -28944.8518 | -152064.149 | 238807.378 | 4504423.9 | 413454.801 | -25580.2461 | 65303.9621 | -24204.9631 | 149363.323 | 318909.795 | 1104967.37 | -19075.4039 | 31808.8678 | -4647.045 | 36853.4193 | 30808.4652 | 186959.131 | -7044.5481
265.92 | 9.5415 | 1.2594 |  | -46554.1209 | -168418.288 | 264618.546 | 4774928.82 | 12688.2822 | -24497.7838 | 65910.3969 | -30310.8262 | 157564.883 | 367540.383 | 1043029.21 | -17230.3755 | 28350.4368 | -4985.3666 | 38781.8537 | 32435.6248 | 172323.49 | -5909.4499
266.12 | 9.5876 | 1.2639 |  | -54820.4898 | -186063.322 | 293255.249 | 5278778.39 | -139376.038 | -22476.275 | 72437.5169 | -36804.2441 | 165375.462 | 446041.187 | 1057081.86 | -16922.7612 | 27045.1562 | -6324.2653 | 40023.4785 | 38463.6575 | 164851.629 | -7039.2779
266.32 | 9.6434 | 1.2682 |  | -62878.9113 | -209427.789 | 327107.024 | 5832162.95 | -240103.768 | -27978.7852 | 78758.4267 | -40888.8625 | 174205.991 | 482916.561 | 1116547.27 | -18075.2851 | 24471.3747 | -6104.8335 | 41806.361 | 36200.7394 | 144082.296 | -6456.7501
266.52 | 9.6909 | 1.2715 |  | -65589.6572 | -213152.432 | 357130.884 | 6088848.46 | -235007.575 | -20859.8754 | 83226.1509 | -42559.0946 | 181974.999 | 514276.167 | 1209643.09 | -15134.2338 | 28888.6646 | -7167.7069 | 43316.4098 | 43122.8693 | 172285.916 | -6135.3062
266.72 | 9.7614 | 1.2744 |  | -56424.6293 | -232053.604 | 394170.964 | 6642691.62 | 58388.6647 | -28091.6323 | 91607.3736 | -42897.1955 | 191367.874 | 527179.77 | 1358070.74 | -14702.9534 | 32920.896 | -7417.7883 | 45201.11 | 43068.4659 | 180643.661 | -6861.437
266.92 | 9.821 | 1.2767 |  | -39787.0366 | -242074.243 | 427262.771 | 7240621.91 | 553805.316 | -33352.0907 | 109316.645 | -43506.1288 | 200652.574 | 520468.839 | 1527816.96 | -20679.5836 | 33554.7889 | -6528.3128 | 47198.2387 | 39347.4186 | 182950.695 | -7055.1566
267.12 | 9.8957 | 1.2784 |  | -18972.8777 | -249993.306 | 461188.506 | 7702183.24 | 1067962.8 | -27596.2295 | 123492.025 | -43533.3787 | 210061.694 | 521509.523 | 1681950.39 | -17418.3314 | 37104.1473 | -6616.2172 | 49190.967 | 40862.7011 | 202005.749 | -6131.0486
267.32 | 9.972 | 1.279 |  | -1634.6068 | -247324.294 | 492514.4 | 7822131.37 | 1434451.21 | -37531.0823 | 127125.77 | -40482.0162 | 217859.015 | 522142.798 | 1867650.46 | -23393.4725 | 45713.8552 | -7404.2211 | 50939.8608 | 43518.1322 | 238545.469 | -8362.4747
267.52 | 10.0413 | 1.279 |  | 20037.8842 | -229587.402 | 513876.572 | 7451846.65 | 1838524.75 | -38209.5295 | 121793.686 | -32490.9459 | 221801.09 | 503129.38 | 1963355.15 | -22579.7462 | 53206.1328 | -9503.6382 | 51628.0318 | 58187.8509 | 290400.831 | -6999.8951
267.72 | 10.1021 | 1.2796 |  | 44444.582 | -217687.558 | 537627.099 | 7006461.75 | 2167459.43 | -42783.8688 | 110652.484 | -24602.7239 | 227231.545 | 378191.759 | 1815547.17 | -26366.608 | 52711.198 | -6432.1674 | 51760.3194 | 51386.659 | 319671.817 | -9887.0613
267.92 | 10.1781 | 1.2805 |  | 79379.9038 | -193015.567 | 551069.547 | 6246015.16 | 2825334.16 | -37966.6227 | 105332.769 | -11241.7852 | 232115.762 | 245383.077 | 1591024.57 | -21848.6756 | 42567.5698 | -4918.0244 | 52479.1617 | 44420.1685 | 251638.304 | -6071.9691
268.12 | 10.2327 | 1.2812 |  | 88892.2623 | -144209.244 | 559774.936 | 4964946.3 | 2928036.73 | -33730.0711 | 95090.953 | -1596.4559 | 235968.446 | 61443.4609 | 1431124.15 | -18241.3847 | 36298.0995 | 662.8881 | 53694.6756 | 11678.7554 | 206737.939 | -4926.0629
268.32 | 10.2836 | 1.2825 |  | 124801.07 | -125669.81 | 565270.507 | 4342818.57 | 3511248.73 | -40543.4498 | 86149.3943 | 9735.1666 | 240088.831 | -55134.9017 | 1228629.36 | -19156.4982 | 30876.8088 | 2176.9885 | 54608.5756 | 6173.1854 | 186106.434 | -5279.1481
268.52 | 10.3389 | 1.2839 |  | 143086.538 | -96829.476 | 559354.477 | 3582233.36 | 3796325.35 | -44915.2905 | 77592.4106 | 17984.9011 | 240557.642 | -135834.282 | 1160730.21 | -22081.847 | 29634.0445 | 3526.9723 | 55072.0182 | -1093.949 | 173601.067 | -5429.5192
268.72 | 10.3903 | 1.2847 |  | 151390.237 | -41537.0353 | 542247.566 | 2514899.02 | 3928103.07 | -35733.5462 | 73707.108 | 24109.2333 | 236731.17 | -179574.441 | 1243721.74 | -19267.2321 | 34160.4866 | 3750.56 | 54357.5204 | -223.1001 | 200194.679 | -6322.6378
268.92 | 10.4299 | 1.2859 |  | 182691.244 | -42828.6116 | 523679.939 | 2639027.11 | 4593203.11 | -43411.0347 | 78076.6899 | 30034.0228 | 234223.333 | -242502.985 | 1295618 | -21041.2806 | 34991.8486 | 4621.7497 | 54198.6976 | -6600.6137 | 188199.259 | -5549.1953
269.12 | 10.5027 | 1.2873 |  | 209006.682 | -31200.3454 | 500310.583 | 2589984.13 | 5244196.49 | -48960.6044 | 87747.585 | 35744.1232 | 228971.471 | -297754.801 | 1386062.81 | -27888.8811 | 36349.5079 | 5469.9563 | 53203.9358 | -8483.2772 | 204910.635 | -7649.9049
269.32 | 10.5588 | 1.2875 |  | 211768.507 | -18024.2405 | 467989.879 | 2387260.58 | 5484603.63 | -47226.7517 | 89786.5084 | 41176.8526 | 223183.348 | -389821.127 | 1469699.83 | -25907.2418 | 39981.4746 | 7669.4267 | 52364.4477 | -18496.902 | 229328.465 | -7291.173
269.52 | 10.5961 | 1.2878 |  | 217136.621 | -18230.9158 | 445818.851 | 2392014.07 | 5503515.13 | -45620.5185 | 88782.194 | 40029.8087 | 221827.097 | -372525.532 | 1442050.57 | -23442.7412 | 38979.5896 | 7261.1108 | 52948.7313 | -16077.5153 | 231690.379 | -6870.2207
269.72 | 10.6774 | 1.2889 |  | 219129.808 | -33468.9691 | 416284.528 | 2881986.05 | 5544763.61 | -38334.3412 | 97320.7391 | 35008.9491 | 216558.167 | -295619.138 | 1473890.68 | -22299.3375 | 36535.2277 | 5468.3843 | 51988.2743 | -8767.4239 | 203650.496 | -5896.1634
269.92 | 10.7391 | 1.2888 |  | 202787.364 | -45950.2338 | 383838.139 | 3412376.98 | 5388875.2 | -34919.6102 | 106796.25 | 29642.5926 | 209808.099 | -255471.026 | 1635459.68 | -24178.4867 | 40140.9136 | 5531.2215 | 51113.1566 | -10512.5538 | 220831.612 | -6861.0746
270.12 | 10.7704 | 1.2891 |  | 193349.928 | -68106.9593 | 359193.724 | 3909496.23 | 5213797.6 | -42329.1304 | 107071.133 | 25134.35 | 204519.7 | -190084.612 | 1690517.53 | -27370.4434 | 43660.7475 | 3927.1139 | 50319.7553 | -869.6623 | 251752.134 | -8433.8691
270.32 | 10.8037 | 1.2896 |  | 169357.581 | -78266.8295 | 338138.807 | 4155216.55 | 4748920.97 | -39672.2005 | 108596.23 | 17974.0868 | 199980.569 | -106684.686 | 1727303.72 | -27721.4928 | 44999.9258 | 2355.388 | 49323.8028 | 5625.7584 | 257871.479 | -8176.0885
270.52 | 10.8657 | 1.2895 |  | 144248.009 | -91034.9564 | 319142.258 | 4385950.61 | 4331381.24 | -37448.9176 | 109727.042 | 12671.2364 | 195740.492 | -48460.0386 | 1726365.53 | -28006.6739 | 43984.1222 | 1459.5838 | 48461.5152 | 9325.2549 | 253141.297 | -8700.4436
270.72 | 10.8937 | 1.2886 |  | 108880.918 | -109217.433 | 315724.297 | 4485677.57 | 3560919.87 | -41201.4885 | 100961.341 | 5730.43 | 197106.333 | -1168.45 | 1651627.75 | -25905.3791 | 43061.4428 | 1584.9569 | 49161.3123 | 6133.7143 | 248367.004 | -8157.5327
270.92 | 10.9321 | 1.2883 |  | 72038.4691 | -118532.88 | 313860.144 | 4592641.41 | 2707143.77 | -35617.9272 | 90900.7176 | -3817.6272 | 198576.683 | 141356.64 | 1571433.83 | -23788.449 | 45087.7688 | -2278.1916 | 49686.402 | 26001.0061 | 266772.448 | -7313.8375
271.12 | 11.0056 | 1.2881 |  | 44640.6743 | -150880.128 | 324588.902 | 5159678.09 | 2083905.38 | -37646.7539 | 90046.7129 | -13892.9644 | 201155.748 | 243700.552 | 1501490.49 | -23952.1772 | 42091.2125 | -3615.2869 | 49591.8951 | 31776.6527 | 255079.032 | -7576.8062
271.32 | 11.0445 | 1.287 |  | 19011.5899 | -188448.146 | 341857.495 | 5982581.62 | 1734199.63 | -41943.441 | 101134.994 | -21989.9231 | 207066.991 | 289792.965 | 1521763.63 | -27737.8821 | 37509.3399 | -2847.6307 | 50886.9241 | 24010.0653 | 219957.514 | -8111.6109
271.52 | 11.0908 | 1.2868 |  | 37.6112 | -209509.656 | 364319.957 | 6603732.57 | 1449003.34 | -39120.8699 | 110076.299 | -30047.3368 | 214033.287 | 396859.332 | 1644935.16 | -25766.3118 | 37680.2405 | -4610.5594 | 52879.7337 | 32470.3772 | 211118.278 | -9255.1843
271.72 | 11.1708 | 1.2865 |  | -8558.8435 | -249587.991 | 399263.746 | 7499927.95 | 1318313.68 | -47858.4196 | 118758.141 | -37354.3487 | 224119.438 | 456155.52 | 1653327.25 | -30767.9295 | 38114.5536 | -5393.3598 | 54556.4984 | 37201.6055 | 220565.233 | -10671.2558
271.92 | 11.2075 | 1.2857 |  | -42165.3852 | -234072.918 | 430867.662 | 7124867.79 | 607329.081 | -45965.0463 | 108549.551 | -41108.645 | 231759.028 | 529802.938 | 1724931.03 | -32168.2567 | 45884.1672 | -7351.9725 | 56239.1013 | 48180.5691 | 268659.69 | -11607.41
272.12 | 11.2298 | 1.286 |  | -65996.0694 | -212641.947 | 464573.231 | 6704859.01 | -54375.9167 | -25541.8051 | 100818.156 | -48247.0642 | 239313.841 | 659593.84 | 1781205.81 | -16194.5862 | 48286.7207 | -10340.4602 | 57563.4463 | 62349.103 | 282523.69 | -6864.1029
272.32 | 11.3011 | 1.2865 |  | -43025.5537 | -267518.911 | 507798.636 | 7918285.8 | 438273.656 | -48035.5905 | 109785.085 | -49489.8611 | 249404.297 | 647166.351 | 1691194.17 | -23070.0822 | 45186.9105 | -10081.1089 | 58651.3346 | 62366.4542 | 270747.598 | -7848.4887
272.52 | 11.3444 | 1.2842 |  | -21439.8735 | -306566.501 | 547953.517 | 9047525.5 | 1189458.25 | -51377.0631 | 133868.783 | -47233.4026 | 261177.028 | 555430.158 | 1849901.19 | -28035.2495 | 43451.9002 | -6704.9097 | 61123.6488 | 43265.3115 | 240348.429 | -8647.3433
272.72 | 11.3736 | 1.2811 |  | 1657.0838 | -296324.539 | 578473.482 | 9257880.95 | 1805405.42 | -60126.8308 | 149793.449 | -45689.4467 | 268713.356 | 597344.176 | 2166882.04 | -35730.7911 | 49851.598 | -7845.1837 | 63643.8971 | 50468.5688 | 266980.052 | -13441.5061
272.92 | 11.4496 | 1.2779 |  | 15614.1357 | -267033.792 | 608608.16 | 8999208.31 | 2110695.46 | -40956.559 | 160294.905 | -45468.2457 | 274482.341 | 612733.138 | 2399046.73 | -27428.1881 | 57225.5975 | -8162.9047 | 64518.1356 | 51326.6638 | 310272.406 | -9386.5216
273.12 | 11.5056 | 1.2727 |  | 43676.6344 | -266604.138 | 637930.521 | 9057180.65 | 2637391.46 | -50018.7535 | 158144.086 | -38789.7062 | 281265.182 | 572904.291 | 2475317.25 | -29914.3788 | 64651.857 | -9362.6268 | 65640.7794 | 62456.5031 | 366826.935 | -9259.9022
273.32 | 11.546 | 1.2679 |  | 79402.1541 | -262480.949 | 655683.286 | 9050395.62 | 3292709.7 | -48145.5691 | 163235.541 | -32891.9834 | 286125.799 | 494602.506 | 2402649.72 | -32789.9083 | 57642.7014 | -7133.508 | 66132.226 | 53184.0903 | 322415.631 | -10233.8456
273.52 | 11.6043 | 1.2637 |  | 111828.65 | -230657.079 | 664153.992 | 8221969.9 | 3798586.64 | -44182.6412 | 155507.826 | -22425.2202 | 287973.429 | 368016.706 | 2274626.1 | -30937.9348 | 54134.8737 | -4643.9778 | 66484.4458 | 39322.2141 | 299638.17 | -9394.3114
273.72 | 11.6459 | 1.2587 |  | 135274.437 | -193765.67 | 670188.409 | 6936585.38 | 4222626.88 | -36679.1141 | 136074.803 | -4655.8684 | 289453.427 | 149504.008 | 2043742.76 | -22764.2423 | 51318.0387 | -1349.7198 | 65849.3104 | 27873.4831 | 299381.645 | -6975.5413
273.92 | 11.6729 | 1.2545 |  | 167286.114 | -161925.193 | 661241.754 | 6087120.18 | 4770294.1 | -37989.9705 | 126971.144 | 7726.9886 | 291313.299 | 1462.3216 | 1897861.97 | -23065.429 | 47786.3758 | 1339.8437 | 67367.5551 | 15417.9539 | 281821.136 | -5770.1862
274.12 | 11.7141 | 1.2508 |  | 196017.267 | -130894.638 | 651119.984 | 5386204.37 | 5312478.61 | -39208.3665 | 125202.089 | 17459.6234 | 290329.629 | -111649.097 | 1794521.99 | -27159.2833 | 42638.0172 | 3639.1842 | 66696.5958 | 5827.9322 | 256214.603 | -7909.1142
274.32 | 11.736 | 1.2471 |  | 213239.159 | -114445.127 | 630396.968 | 5046564.74 | 5643016.11 | -34619.0799 | 127224.244 | 21296.8813 | 288791.173 | -163766.032 | 1839355.44 | -20873.5062 | 43856.7932 | 4724.0958 | 67578.7536 | -6318.7617 | 235332.243 | -5942.8617
274.52 | 11.7893 | 1.2435 |  | 238142.119 | -108993.141 | 598119.509 | 5345646.83 | 6225382.7 | -34206.5439 | 142009.26 | 22475.7264 | 283270.419 | -170359.557 | 1942502.76 | -29188.0483 | 41884.9608 | 4996.4235 | 67004.5341 | -5449.9058 | 227427.088 | -7422.2877
274.72 | 11.8342 | 1.2384 |  | 247433.152 | -104669.115 | 566740.663 | 5116748.22 | 6417961.84 | -45415.0412 | 133195.897 | 28711.6323 | 274747.093 | -226446.934 | 1917708.78 | -36915.0209 | 46171.5897 | 5398.4491 | 64983.457 | -6024.0761 | 255418.478 | -11771.3989
274.92 | 11.8586 | 1.233 |  | 228576.002 | -65436.7186 | 527959.605 | 4175804.54 | 6023294.48 | -26082.8352 | 123016.553 | 30318.8179 | 266919.16 | -250802.646 | 1905941.29 | -19693.4629 | 48542.6046 | 5616.0629 | 63814.3697 | -7236.1161 | 274911.966 | -6338.1664
275.12 | 11.9052 | 1.2283 |  | 226886.153 | -70034.8586 | 497374.82 | 4241157.71 | 5957034.37 | -34863.341 | 121712.399 | 29101.6249 | 262147.112 | -209410.071 | 1894279.59 | -24758.9977 | 47868.2068 | 4191.2187 | 63386.6031 | 1133.8125 | 275033.14 | -6808.6628
275.32 | 11.9203 | 1.2228 |  | 207337.724 | -78076.29 | 471543.471 | 4378402.44 | 5641465.82 | -38009.1693 | 121862.773 | 26017.0038 | 256452.223 | -176951.236 | 1944340.59 | -30441.8897 | 51760.8832 | 3575.9492 | 61868.1273 | 5248.3211 | 305134.666 | -8376.0301
275.52 | 11.9143 | 1.2197 |  | 171763.807 | -78085.9075 | 437136.697 | 4356628.65 | 4893541.73 | -45894.242 | 114141.788 | 18168.4904 | 249164.695 | -88264.2945 | 1963076.39 | -34178.3024 | 55491.638 | 2326.1231 | 61398.9763 | 8711.6571 | 324557.961 | -12036.894
275.72 | 11.9347 | 1.2183 |  | 146293.391 | -100097.584 | 421329.549 | 4635569.48 | 4277736.25 | -39431.8939 | 109538.054 | 10035.1093 | 245395.435 | 17660.5416 | 1818230.87 | -25426.0991 | 49293.0348 | -155.2314 | 59839.231 | 22793.6398 | 301202.287 | -8010.9994
275.92 | 11.955 | 1.2154 |  | 112879.653 | -124416.287 | 405871.827 | 5232297.7 | 3717000.69 | -42956.1291 | 115015.886 | 693.3376 | 242715.353 | 98780.4789 | 1855078.95 | -29631.5366 | 46861.2426 | -614.3408 | 60152.1473 | 19276.827 | 268934.549 | -7972.5311
276.12 | 11.9407 | 1.212 |  | 78335.9715 | -155855.952 | 403799.953 | 5830318.83 | 3017386.27 | -37689.1426 | 115797.783 | -10841.1299 | 243206.348 | 194106.107 | 1856816.42 | -26698.5869 | 46657.998 | -913.9651 | 60259.4149 | 18708.2098 | 271403.711 | -8932.6967
276.32 | 11.9695 | 1.209 |  | 61629.2791 | -199177.762 | 408298.256 | 6838881.53 | 2729027.73 | -52168.4305 | 119934.772 | -19354.5887 | 244971.491 | 339315.036 | 1876936.46 | -30485.4344 | 49314.72 | -5549.859 | 60902.3973 | 42673.815 | 282223.26 | -8217.3181
276.52 | 11.9995 | 1.2034 |  | 23569.3226 | -227095.09 | 428594.494 | 7396249.01 | 2027312.63 | -50117.0343 | 124010.49 | -29758.3838 | 248894.254 | 382792.006 | 1871174.74 | -35534.9358 | 48135.3997 | -4068.0923 | 60663.5994 | 34344.3543 | 286943.864 | -12022.7194
276.72 | 12.0047 | 1.1979 |  | -4093.3484 | -244699.348 | 456215.45 | 7508136.46 | 1410020.89 | -52484.0035 | 113195.475 | -34303.9559 | 256890.691 | 481797.034 | 1814094.03 | -31472.2756 | 49748.0649 | -7296.2722 | 62746.2548 | 52000.59 | 301652.345 | -10208.9507
276.92 | 12.0246 | 1.1933 |  | -32345.7067 | -253128.235 | 485709.004 | 7730580.37 | 777490.947 | -47125.1854 | 113441.311 | -43718.3501 | 263754.856 | 573620.059 | 1815333.36 | -29913.3825 | 48908.2794 | -8194.2871 | 63593.5294 | 55583.2258 | 297299.083 | -9673.7261
277.12 | 12.0327 | 1.1887 |  | -36246.9556 | -282022.93 | 521341.518 | 8341725.87 | 681937.977 | -59178.953 | 120499.541 | -49069.8253 | 272198.307 | 636964.583 | 1811539.9 | -32495.4043 | 44004.2887 | -8855.5816 | 65182.0174 | 57135.2727 | 263926.349 | -10213.7917
277.32 | 12.0281 | 1.1854 |  | -39266.4116 | -302665.379 | 561614.373 | 8829387.9 | 687690.653 | -53059.7618 | 127449.883 | -51797.0396 | 282019.403 | 634469.153 | 1758130.97 | -29295.1879 | 39079.4524 | -8084.7051 | 66918.1296 | 52526.2613 | 228220.077 | -9089.4504
277.52 | 12.0133 | 1.1837 |  | -38050.2737 | -297726.964 | 594431.452 | 8780017.53 | 618399.886 | -52809.7797 | 123342.781 | -52783.2683 | 288286.241 | 672146.655 | 1855563.52 | -25514.3528 | 47329.3501 | -9636.5616 | 68171.3054 | 60110.841 | 272232.032 | -10249.0601
277.72 | 12.01 | 1.1833 |  | -19818.5062 | -305915.124 | 632609.053 | 9219007.57 | 1089344.42 | -56498.0682 | 138590.922 | -52570.4032 | 296559.68 | 667440.725 | 1993875.29 | -28704.8543 | 45534.73 | -8801.5048 | 69745.7437 | 56310.1086 | 254902.445 | -7599.827
277.92 | 11.9963 | 1.1845 |  | 7275.4282 | -288488.33 | 656194.242 | 9287465.69 | 1754850.2 | -49584.0347 | 157039.117 | -50548.651 | 299474.322 | 656003.288 | 2216166.32 | -31040.2587 | 48882.7499 | -8356.2785 | 69949.1987 | 53863.6883 | 266836.284 | -10101.909
278.12 | 12.0137 | 1.186 |  | 34757.9232 | -284037.95 | 677878.679 | 9561240.9 | 2511378.88 | -45313.7701 | 171461.449 | -46051.7885 | 302925.989 | 570257.767 | 2393074.95 | -29079.9615 | 54240.9422 | -6428.9579 | 70112.4966 | 45459.0496 | 299016.632 | -10275.3499
278.32 | 12.0328 | 1.1851 |  | 81848.3774 | -294929.436 | 701169.115 | 9916001.09 | 3452561.09 | -50215.0958 | 175360.705 | -37048.1368 | 311426.929 | 505098.41 | 2457398.53 | -30885.1111 | 59543.8041 | -7085.7982 | 73139.5809 | 49711.2672 | 320876.588 | -8985.5271
278.52 | 12.0453 | 1.1839 |  | 103879.428 | -257308.031 | 705415.938 | 9201561.04 | 3842832.21 | -55600.7233 | 171381.99 | -28380.2068 | 308135.78 | 459510.365 | 2592170.9 | -40011.301 | 64301.6215 | -6500.0144 | 71633.3053 | 51022.7323 | 354242.912 | -13102.7204
278.72 | 12.0422 | 1.1819 |  | 123873.797 | -203309.163 | 703360.081 | 7642755.4 | 4069112 | -48213.2336 | 146601.657 | -12515.0149 | 305532.36 | 339487.263 | 2410498.58 | -39009.8003 | 65752.8439 | -6744.2481 | 70425.8898 | 59069.3631 | 383854.664 | -11604.3673
278.92 | 12.0231 | 1.1808 |  | 145774.579 | -151992.267 | 695989.753 | 6186898.98 | 4257928.64 | -30774.2096 | 129318.761 | -1592.3998 | 303701.208 | 157649.908 | 2098278.22 | -25022.3977 | 59257.6838 | -2681.4162 | 69010.1469 | 40634.448 | 367778.727 | -7347.3486
279.12 | 11.9998 | 1.1809 |  | 177057.358 | -120807.334 | 679302.554 | 5231953.16 | 4825980.9 | -39307.0075 | 123625.258 | 11229.6597 | 301878.87 | 12701.7606 | 1905822.09 | -28108.5873 | 50050.5943 | 57.8546 | 69454.6271 | 25570.5881 | 304994.033 | -6010.4231
279.32 | 11.9669 | 1.1808 |  | 191038.979 | -80960.8546 | 646184.725 | 4240813.12 | 5067495.16 | -38558.5638 | 111266.225 | 21615.2559 | 293832.448 | -125411.789 | 1838470.14 | -25433.8515 | 50297.2488 | 3032.6022 | 67903.5469 | 8362.7788 | 301265.352 | -7137.8698
279.52 | 11.9355 | 1.1792 |  | 218174.754 | -77931.364 | 619465.309 | 4039667.67 | 5530983.57 | -45263.5252 | 105892.691 | 28374.3294 | 290180.101 | -189896.744 | 1705515.99 | -24389.3149 | 47444.0987 | 3354.3563 | 67736.5506 | 9238.4455 | 291282.993 | -6155.5575
279.72 | 11.9121 | 1.1762 |  | 223913.479 | -80466.943 | 576630.714 | 4383146.87 | 5773328.32 | -36542.707 | 123508.052 | 25511.3101 | 281041.755 | -210177.049 | 1784884.61 | -27139.6107 | 39081.9542 | 6305.5296 | 66027.9831 | -9741.9928 | 233864.633 | -8465.5038
279.92 | 11.9011 | 1.1728 |  | 237327.274 | -95390.2686 | 538482.937 | 4776557.44 | 6059344.29 | -47817.1337 | 127608.654 | 25828.4555 | 273260.213 | -194706.092 | 1798675.84 | -33486.28 | 40473.6356 | 5044.0633 | 65450.4206 | -5422.845 | 225061.285 | -9855.2427
280.12 | 11.8817 | 1.1715 |  | 210903.575 | -70030.4357 | 494133.529 | 4289603.04 | 5580867.14 | -35244.4871 | 120297.608 | 24414.8768 | 260029.899 | -172207.515 | 1864458.92 | -27619.2139 | 49619.3671 | 3532.1158 | 62538.9712 | 2855.2828 | 279628.608 | -9302.0588
280.32 | 11.8494 | 1.1729 |  | 189588.499 | -77256.2575 | 458075.043 | 4331335.69 | 5156044.09 | -42444.8745 | 116401.512 | 20311.6491 | 252131.643 | -121210.984 | 1888963.75 | -30602.1059 | 50013.3885 | 3090.8736 | 61523.367 | 6380.8857 | 300535.305 | -9375.739
280.52 | 11.8278 | 1.1756 |  | 168298.706 | -73231.6097 | 427629.758 | 4276373.71 | 4719679.35 | -40013.1529 | 113361.298 | 15537.5465 | 243417.802 | -7133.4062 | 1947587.48 | -25795.4114 | 53626.7061 | -844.9745 | 59602.5123 | 28657.6786 | 319288.352 | -7096.5246
280.72 | 11.7818 | 1.179 |  | 137301.859 | -116622.453 | 409565.27 | 5195523.24 | 4162759.01 | -45688.7492 | 117211.04 | 4872.4838 | 239657.922 | 29594.5026 | 1925511.82 | -34624.3081 | 52739.4685 | 994.0336 | 58953.0069 | 12667.8509 | 303392.518 | -10326.5135
280.92 | 11.7231 | 1.1852 |  | 108627.25 | -131646.975 | 387192.07 | 5546145.58 | 3572389.22 | -43908.8864 | 117132.257 | -4701.0781 | 234364.446 | 200190.729 | 1923019.27 | -30190.8995 | 52300.9888 | -4034.3287 | 58579.1564 | 38005.6683 | 301176.529 | -8449.5062
281.12 | 11.6833 | 1.1943 |  | 61207.7033 | -148849.135 | 377611.975 | 5906736.53 | 2507337.59 | -40848.2461 | 111562.112 | -19008.3187 | 228706.298 | 319080.81 | 1942758.58 | -30768.704 | 55513.2719 | -4482.6505 | 56565.2209 | 36691.0604 | 325533.466 | -10955.316
281.32 | 11.6426 | 1.1998 |  | 43688.7191 | -187290.649 | 380617.154 | 6598669.33 | 2228231.88 | -37892.6989 | 115716.408 | -25151.6693 | 229292.595 | 422058.668 | 1869855.89 | -24272.9627 | 50044.9447 | -7641.4329 | 56679.2029 | 54156.7007 | 294441.87 | -6170.8418
281.52 | 11.621 | 1.1989 |  | 7359.9959 | -197140.811 | 383817.751 | 7077832.84 | 1658942.99 | -33840.3063 | 128381.835 | -36242.6104 | 227743.86 | 482397.253 | 2003242.84 | -29344.6217 | 51692.2707 | -6459.7912 | 56165.1752 | 42252.6944 | 290806.04 | -9122.5867
281.72 | 11.5834 | 1.1965 |  | -6354.7369 | -237237.752 | 410350.123 | 7627150.31 | 1392045.08 | -54610.3402 | 119436.239 | -38182.4882 | 234651.567 | 527166.894 | 1920061.02 | -36126.5491 | 53569.1489 | -8159.7418 | 57509.3629 | 55284.2547 | 322089.649 | -10717.6815
281.92 | 11.5705 | 1.195 |  | -33400.7636 | -237904.418 | 435422.145 | 7468327.22 | 752613.827 | -48688.6153 | 112826.724 | -43835.2568 | 239980.759 | 596071.53 | 1835832.4 | -32003.0658 | 49926.1106 | -9086.5425 | 58464.6965 | 58733.6522 | 300126.565 | -10386.1692
282.12 | 11.522 | 1.1936 |  | -57876.0224 | -248700.993 | 466601.061 | 7530196.3 | 87303.5215 | -43646.9706 | 104629.14 | -51469.858 | 247092.959 | 659225.826 | 1729812.64 | -26729.8484 | 47658.1731 | -9496.3706 | 59467.1437 | 57063.7208 | 287573.037 | -9500.967
282.32 | 11.4667 | 1.1933 |  | -64906.1969 | -248151.998 | 504514.447 | 7390028.81 | -269245.633 | -40539.5815 | 101218.502 | -56059.0811 | 255035.061 | 738044.141 | 1647996.56 | -24533.595 | 44140.8116 | -11587.6722 | 61139.0745 | 68059.0397 | 261270.294 | -8077.4381
282.52 | 11.4165 | 1.1936 |  | -71619.6651 | -243382.257 | 530321.002 | 7363755.08 | -337084.298 | -36840.5134 | 100968.947 | -55783.5371 | 256679.073 | 724470.803 | 1664305.83 | -22868.4607 | 46722.0375 | -11330.4087 | 60081.4848 | 65440.796 | 265934.823 | -8149.3086
282.72 | 11.3605 | 1.1936 |  | -48968.1672 | -255067.176 | 560059.629 | 7644008.01 | 220897.94 | -44289.3235 | 107489.51 | -50389.5771 | 262528.522 | 661701.241 | 1727814.34 | -24531.5806 | 45696.6434 | -9901.1593 | 61539.6534 | 59058.4449 | 259244.809 | -8351.6123
282.92 | 11.3084 | 1.1937 |  | -25242.2513 | -261312.567 | 589338.996 | 7909482.77 | 881477.719 | -50072.2079 | 121106.735 | -44744.8289 | 268077.445 | 568801.336 | 1748677.49 | -27714.2667 | 40675.7398 | -7437.4892 | 61882.5735 | 50217.6022 | 237811.104 | -8489.1527
283.12 | 11.2746 | 1.1939 |  | 2032.0306 | -252103.213 | 609265.272 | 7872985.85 | 1412927.36 | -43408.5356 | 123087.453 | -39663.116 | 273108.977 | 516460.956 | 1794433.82 | -24301.6479 | 44791.2453 | -7109.2183 | 63618.3751 | 46841.6668 | 247568.407 | -8129.3965
283.32 | 11.2496 | 1.1935 |  | 24452.5455 | -229866.912 | 629925.268 | 7674187 | 1889310.93 | -39946.7284 | 131484.129 | -36040.0562 | 276137.939 | 491747.016 | 1938346.69 | -27974.6955 | 47897.8679 | -6752.21 | 63717.2106 | 46226.096 | 267811.804 | -9769.7417
283.52 | 11.1983 | 1.1925 |  | 55153.236 | -211337.956 | 635131.532 | 7209792.91 | 2408089.61 | -49400.9421 | 125419.817 | -26628.6441 | 275015.06 | 419165.109 | 1906303.1 | -34053.245 | 47963.0281 | -6108.1217 | 63266.2472 | 46592.427 | 278479.744 | -11631.5002
283.72 | 11.1535 | 1.1924 |  | 77425.265 | -171239.044 | 639450.756 | 5945451.57 | 2636502.43 | -44247.9191 | 107498.906 | -14660.7886 | 274280.373 | 284397.829 | 1667723.16 | -27923.44 | 42275.7568 | -4025.1098 | 62759.7775 | 38445.5653 | 246387.973 | -8214.3877
283.92 | 11.1264 | 1.1927 |  | 89871.0303 | -102228.069 | 630647.946 | 4158324.95 | 2723033.32 | -31398.7564 | 85044.3423 | -913.9586 | 269458.743 | 139340.791 | 1520360.83 | -19898.4252 | 42700.0874 | -1906.3459 | 61248.6417 | 27114.6644 | 249319.135 | -6902.6521
284.12 | 11.066 | 1.1925 |  | 121161.623 | -79387.1444 | 617014.606 | 3515354.9 | 3349395.68 | -33304.9234 | 80333.8167 | 11280.6668 | 267665.418 | -31434.3291 | 1376552.61 | -18022.2104 | 38355.1508 | 1544.3759 | 61254.026 | 9104.2952 | 225450.75 | -3586.4286
284.32 | 11.0111 | 1.1929 |  | 157581.233 | -73041.2462 | 599647.909 | 3489865.3 | 4097794.27 | -46662.3751 | 84714.3239 | 18934.6615 | 264194.942 | -104307.044 | 1399208.93 | -27473.9696 | 38108.8692 | 2436.1168 | 60884.8575 | 5650.4736 | 212414.937 | -7691.7385
284.52 | 10.9721 | 1.1936 |  | 180477.441 | -72466.7473 | 568127.634 | 3615448.35 | 4601290.1 | -46529.2741 | 95673.1546 | 21412.1219 | 257126.166 | -176625.489 | 1390147.98 | -30703.0612 | 33901.5107 | 4853.1562 | 59558.9124 | -6122.9176 | 197726.429 | -8802.2819
284.72 | 10.9184 | 1.1937 |  | 190607.609 | -44637.8974 | 533627.538 | 3002754.84 | 4673943.07 | -50187.285 | 87213.8001 | 25019.5337 | 248093.643 | -173357.035 | 1373172.6 | -27355.3151 | 35715.4809 | 3614.0572 | 58178.5663 | 113.5123 | 201832.273 | -8546.1849
284.92 | 10.8821 | 1.1938 |  | 188663.9 | -26172.898 | 491260.447 | 2457986.41 | 4569509.06 | -46205.5622 | 78832.2551 | 27670.7156 | 235423.836 | -206170.462 | 1337348.6 | -22456.9002 | 37453.2231 | 4054.5816 | 55085.5166 | 190.4688 | 228878.343 | -7818.2937
285.12 | 10.8505 | 1.1935 |  | 200535.443 | -27034.5829 | 453595.404 | 2432499.39 | 4880747.38 | -49771.0583 | 80675.2949 | 32179.3972 | 226765.287 | -264247.245 | 1264698.57 | -26277.1918 | 32598.426 | 5044.8099 | 53809.8326 | -4731.9161 | 196041.406 | -6225.7192
285.32 | 10.802 | 1.1932 |  | 189087.939 | -15421.5113 | 415621.31 | 2084872.81 | 4728788.54 | -52002.4142 | 75200.8127 | 34364.403 | 216844.141 | -308227.387 | 1256647.41 | -27612.5064 | 34869.967 | 6222.0443 | 51698.2133 | -12191.7093 | 209932.583 | -7436.8469
285.52 | 10.7516 | 1.1936 |  | 176249.075 | -21674.992 | 382628.302 | 2178803.69 | 4456265.82 | -51031.4082 | 70815.0096 | 31139.78 | 210765.336 | -267157.759 | 1266838.84 | -25799.061 | 37263.5065 | 5276.1725 | 51327.0293 | -7324.9977 | 229671.087 | -7545.325
285.72 | 10.7171 | 1.194 |  | 160993.98 | -40000.4458 | 350646.434 | 2780572.81 | 4195342.24 | -44315.7908 | 79312.4566 | 22878.3958 | 202609.642 | -165914.778 | 1307033.72 | -25975.7424 | 34899.9575 | 3431.6053 | 49455.2385 | -98.4565 | 209722.377 | -8668.6219
285.92 | 10.67 | 1.1938 |  | 143340.606 | -87741.2173 | 326730.065 | 3876823.83 | 3911321.73 | -44008.8418 | 92396.3241 | 11813.8979 | 197478.275 | -83390.75 | 1320878.8 | -26664.041 | 31413.5589 | 2957.2559 | 48863.2737 | -1346.1177 | 179799.204 | -7412.6327
286.12 | 10.6185 | 1.1943 |  | 111862.644 | -89884.1795 | 299311.473 | 4142513.55 | 3311977.15 | -38192.0068 | 96907.6043 | 1534.626 | 188660.843 | 69016.0994 | 1438333.28 | -29161.8891 | 34628.199 | -457.2812 | 47167.48 | 14637.2496 | 195735.316 | -9142.7902
286.32 | 10.5895 | 1.1955 |  | 70542.0231 | -92217.2191 | 286217.797 | 4014416.4 | 2418027.9 | -31326.8232 | 83144.7489 | -5437.2341 | 182342.408 | 157614.031 | 1495721.21 | -21945.6591 | 43297.1068 | -2405.5661 | 45517.4661 | 23698.0351 | 248008.784 | -7993.1073
286.52 | 10.5479 | 1.1966 |  | 48246.1882 | -112138.606 | 278877.464 | 4370380.13 | 2068798.81 | -35138.5212 | 83385.306 | -9926.1331 | 179379.655 | 211156.151 | 1460734.7 | -25804.8012 | 42341.0211 | -3518.188 | 44562.5098 | 30859.1832 | 254191.291 | -8746.6796
286.72 | 10.5082 | 1.1978 |  | 21689.9617 | -137622.528 | 286494.009 | 4765387.39 | 1531460.89 | -31284.3599 | 84165.1843 | -17948.3924 | 182069.395 | 255227.789 | 1363429.16 | -21178.2504 | 38080.5023 | -3211.4299 | 45287.2925 | 27664.8639 | 233176.659 | -6681.9438
286.92 | 10.4976 | 1.1989 |  | -266.6283 | -165025.603 | 296691.764 | 5415110.45 | 1146959.39 | -27962.1717 | 92077.2078 | -26835.9549 | 184931.224 | 339992.266 | 1338874.35 | -20681.4568 | 34160.825 | -4562.0057 | 45583.4791 | 35405.7903 | 215926.696 | -7375.6675
287.12 | 10.4682 | 1.1994 |  | -27484.9277 | -196413.363 | 316617.071 | 5996982.46 | 535225.247 | -33059.0626 | 91240.8313 | -36358.706 | 190881.61 | 443476.036 | 1337210.42 | -20952.3123 | 32229.117 | -5722.6046 | 47206.0849 | 37631.3759 | 199259.464 | -7085.1386
287.32 | 10.426 | 1.2006 |  | -53915.175 | -201745.03 | 336274.556 | 6259846.36 | -62837.8481 | -25927.0521 | 91480.4148 | -46284.8151 | 193404.011 | 598894.729 | 1455347.11 | -22563.8233 | 37953.8163 | -9220.1401 | 47439.4997 | 53530.4267 | 222028.19 | -8525.6978
287.52 | 10.4117 | 1.2019 |  | -60754.1986 | -227824.152 | 358976.661 | 6771792.36 | -196601.871 | -38102.7517 | 92251.2455 | -50124.5025 | 195878.826 | 642423.439 | 1443170.99 | -24295.4116 | 38132.3656 | -10034.6934 | 47342.351 | 57043.5114 | 218906.936 | -8663.7731
287.72 | 10.3807 | 1.2021 |  | -72931.0279 | -213147.618 | 385043.818 | 6461068.77 | -317468.715 | -29842.0823 | 92777.848 | -48231.1655 | 199936.155 | 621891.886 | 1515217.91 | -22224.2862 | 39940.492 | -9589.0404 | 47914.3536 | 54244.6254 | 219521.585 | -7855.7166
287.92 | 10.3285 | 1.2028 |  | -79588.8447 | -207498.215 | 417114.033 | 6320486.8 | -432248.907 | -23246.2625 | 88534.3472 | -47615.069 | 207579.055 | 598454.404 | 1517988.28 | -18178.7746 | 43152.3027 | -9018.0683 | 49466.7533 | 51873.4141 | 244704.597 | -6814.67
288.12 | 10.3025 | 1.204 |  | -66222.6237 | -210211.677 | 449026.607 | 6556943.58 | -160596.789 | -31429.9377 | 98935.5478 | -48438.8119 | 215277.18 | 639182.194 | 1538544.78 | -23382.899 | 38929.0589 | -10200.1297 | 50759.5788 | 60680.5786 | 226644.207 | -7389.7454
288.32 | 10.2778 | 1.2039 |  | -53423.3607 | -234401.788 | 482199.631 | 6982452.76 | 23905.354 | -36987.3452 | 100405.364 | -49234.6984 | 222342.13 | 597170.863 | 1464981.07 | -20154.9853 | 36530.5327 | -8189.4297 | 51631.6095 | 49186.6488 | 216264.86 | -7151.3357
288.52 | 10.2376 | 1.2035 |  | -41680.7358 | -223487.869 | 504750.596 | 6935195.83 | 285714.669 | -31960.9489 | 107371.323 | -47414.3899 | 227182.295 | 587151.03 | 1508602.32 | -21670.6384 | 34515.7968 | -8119.9164 | 52841.8788 | 49758.6964 | 201300.893 | -7359.9652
288.72 | 10.2106 | 1.2036 |  | -23028.0989 | -192741.124 | 522558.927 | 6344673.42 | 558919.357 | -29911.9696 | 100595.194 | -41907.0541 | 227585.975 | 573567.369 | 1611868.59 | -19000.0319 | 41991.5444 | -8873.4441 | 52417.0755 | 54250.1625 | 243985.177 | -7496.3887
288.92 | 10.1917 | 1.2029 |  | 6730.6944 | -186437.094 | 540471.524 | 6168793.56 | 1285138.06 | -35220.19 | 103744.161 | -31032.442 | 229964.923 | 442505.768 | 1647469.61 | -21508.2902 | 42248.1403 | -6351.7598 | 52456.8434 | 41684.9652 | 233023.96 | -7081.5887
289.12 | 10.1527 | 1.2019 |  | 42975.7685 | -170976.582 | 548810.538 | 5878901.77 | 2056192.5 | -38644.7566 | 107975.456 | -21045.1844 | 232494.674 | 320507.492 | 1649478.63 | -23886.9037 | 40127.7268 | -3938.6804 | 53202.0869 | 31121.712 | 224478.428 | -7547.6144
289.32 | 10.1268 | 1.2016 |  | 68223.0936 | -147533.31 | 557603.682 | 5245445.74 | 2470725.53 | -39534.1209 | 100055.916 | -11628.2117 | 234394.017 | 213285.533 | 1547087.45 | -24876.412 | 38336.6542 | -2197.8878 | 53504.0809 | 24436.4202 | 217545.511 | -8816.242
289.52 | 10.0883 | 1.2014 |  | 82151.9792 | -111700.199 | 554062.524 | 4261784.08 | 2561957.28 | -35002.7557 | 85357.7896 | -3630.4965 | 233648.583 | 121059.73 | 1360684.48 | -21520.1706 | 35454.2587 | -869.2532 | 53261.0154 | 18658.5939 | 202408.374 | -7592.3252
289.72 | 10.0487 | 1.201 |  | 99690.8373 | -81269.3698 | 544289.634 | 3338421.82 | 2666525.08 | -30505.4619 | 70703.9448 | 3640.4186 | 230831.708 | 45252.1402 | 1148199.35 | -17855.6132 | 30918.2562 | 30.6001 | 52578.8167 | 14727.5017 | 184650.067 | -5008.417
289.92 | 10.0152 | 1.2006 |  | 124378.951 | -52150.3035 | 525807.427 | 2618420.57 | 3073762.25 | -36035.0657 | 64722.3209 | 12234.4547 | 224569.015 | -35865.4916 | 1076405.19 | -18769.2803 | 29860.54 | 843.0803 | 51105.2536 | 10434.148 | 168432.162 | -4816.2313
290.12 | 9.9792 | 1.2003 |  | 142222.549 | -26132.0046 | 501696.952 | 2048350.02 | 3550673.18 | -42930.4511 | 64980.7376 | 22007.7449 | 217526.109 | -173195.513 | 1084617.07 | -23650.2074 | 30155.627 | 3982.9157 | 49547.5009 | -3667.512 | 180822.588 | -7074.2983
290.32 | 9.937 | 1.2 |  | 166039.803 | -11451.7569 | 474923.37 | 1737617.83 | 4112490.28 | -46585.2075 | 66560.3366 | 30566.0165 | 212180.423 | -276070.164 | 1064268.47 | -22735.0703 | 28653.3037 | 5686.9515 | 48982.5463 | -10685.4572 | 170541.176 | -6311.8267
290.52 | 9.8983 | 1.1995 |  | 181254.743 | -11252.5755 | 446760.14 | 1726342.32 | 4382210.02 | -50057.8444 | 65096.4404 | 33350.2629 | 206579.101 | -306763.253 | 1057774.7 | -22568.7783 | 28208.7981 | 6233.5596 | 48141.7842 | -13827.1845 | 169487.717 | -6699.152
290.72 | 9.8734 | 1.1987 |  | 187873.569 | -12614.767 | 413611.325 | 1831117.26 | 4479154.81 | -50231.7581 | 68192.8201 | 32482.7339 | 199025.082 | -281421.979 | 1095427.07 | -21798.9441 | 27525.4567 | 5439.8593 | 46961.6492 | -10196.478 | 158421.65 | -6153.2765
290.92 | 9.8325 | 1.1978 |  | 184681.749 | -13629.832 | 373622.478 | 2022371.23 | 4449551.99 | -46937.0993 | 73731.5169 | 29584.5414 | 188279.537 | -253724.583 | 1154640.23 | -23520.7945 | 28493.2971 | 5035.11 | 44708.5505 | -8797.474 | 166222.693 | -7352.5281
291.12 | 9.7892 | 1.1971 |  | 184551.48 | -21634.6352 | 339899.942 | 2269140 | 4487080.54 | -41654.0054 | 78251.3527 | 27597.633 | 179385.532 | -231053.011 | 1165374.65 | -22357.7643 | 28578.7918 | 4408.4902 | 43220.5349 | -5598.8543 | 164791.832 | -6183.6951
291.32 | 9.7564 | 1.1964 |  | 175255.049 | -28805.1465 | 302559.972 | 2594299.59 | 4456930.93 | -39237.7941 | 85701.134 | 24654.2024 | 168855.461 | -214862.519 | 1291939.52 | -21298.8265 | 31912.0675 | 4480.5552 | 40830.9211 | -7272.8476 | 180162.839 | -7390.9542
291.52 | 9.723 | 1.1952 |  | 177359.802 | -69285.4318 | 278454.412 | 3433901.84 | 4554447.98 | -45859.9143 | 89345.2451 | 21856.8478 | 164328.453 | -211115.585 | 1242730.38 | -22270.8729 | 29402.0043 | 4799.9699 | 40507.6599 | -8831.3795 | 176123.614 | -5787.149
291.72 | 9.6845 | 1.194 |  | 146447.893 | -60524.7074 | 250323.67 | 3422068.75 | 4024708.9 | -29219.0836 | 91992.9186 | 15308.8452 | 157140.67 | -106732.063 | 1386682.8 | -22857.706 | 34226.2886 | 2373.0588 | 39268.9822 | -83.2698 | 180375.108 | -6459.9218
291.92 | 9.6448 | 1.1926 |  | 112740.392 | -62046.5689 | 228183.76 | 3517622.51 | 3300731.86 | -22085.2265 | 87137.4644 | 5923.9945 | 151392.175 | 38312.9444 | 1502132.36 | -16545.5568 | 41787.8312 | -1202.586 | 38636.8729 | 16670.3517 | 235008.282 | -4634.8899
292.12 | 9.6151 | 1.191 |  | 90902.0558 | -83551.2621 | 213482.591 | 4160454.16 | 2891945.89 | -24139.6818 | 92674.2101 | -3937.4801 | 145442.158 | 186618.251 | 1646664.33 | -19077.8713 | 48208.6158 | -4934.0978 | 37022.0093 | 38685.4536 | 280707.973 | -5772.4447
292.32 | 9.5732 | 1.1894 |  | 67485.8635 | -123077.18 | 202183.271 | 5116096.07 | 2600926.62 | -31571.0689 | 102170.28 | -11784.0025 | 141528.53 | 239710.698 | 1695686.9 | -24966.5002 | 47080.7414 | -5017.3154 | 36069.3497 | 39481.368 | 269591.937 | -7524.7399
292.52 | 9.5433 | 1.1883 |  | 47380.6475 | -140172.606 | 198619.926 | 5444430.45 | 2162722.42 | -29011.1037 | 106177.773 | -20458.5659 | 140290.971 | 311670.323 | 1594868.41 | -23267.1837 | 38432.2915 | -4970.4072 | 35704.6316 | 35327.6267 | 217352.789 | -7865.9404
292.72 | 9.515 | 1.1867 |  | 13442.5069 | -147217.703 | 206212.169 | 5336886.59 | 1376325.26 | -14478.174 | 96422.8631 | -27511.7765 | 142503.76 | 362845.829 | 1443103.17 | -12343.5566 | 34801.4097 | -5109.4155 | 36020.2073 | 31263.5816 | 195778.554 | -3112.5285
292.92 | 9.4861 | 1.1844 |  | -15889.0422 | -154917.001 | 217406.598 | 5260184.09 | 700164.112 | -18614.5764 | 84732.8393 | -32178.3059 | 143974.639 | 442699.255 | 1412924.58 | -13642.0956 | 37987.582 | -7249.746 | 36184.7754 | 42901.4815 | 219490.332 | -5779.3676
293.12 | 9.4487 | 1.1821 |  | -36887.3382 | -174154.115 | 229779.146 | 5634678.99 | 310586.009 | -20209.434 | 86384.5958 | -38092.8641 | 146665.566 | 482480.61 | 1341166.9 | -16101.3956 | 33916.1471 | -7196.0768 | 36531.1707 | 42464.943 | 200633.369 | -5067.126
293.32 | 9.4124 | 1.1802 |  | -56438.3898 | -179880.429 | 247345.064 | 5822424.54 | -66048.9634 | -20196.9749 | 91255.2906 | -44401.5353 | 150122.114 | 539760.571 | 1352215.06 | -19906.431 | 32322.2287 | -7673.1202 | 37179.2075 | 43449.0946 | 188576.683 | -7482.3467
293.52 | 9.3836 | 1.1782 |  | -67755.5022 | -190534.046 | 271675.606 | 5903249.11 | -331183.409 | -20251.3903 | 86689.2514 | -46544.579 | 155218.482 | 573492.94 | 1285796.26 | -17708.2398 | 31896.7299 | -8758.4495 | 37962.129 | 49254.7601 | 185500.414 | -5971.6239
293.72 | 9.36 | 1.1756 |  | -80364.0451 | -190055.489 | 299979.565 | 5710518.2 | -638459.788 | -21366.9869 | 77402.4107 | -46765.8454 | 160403.758 | 578422.102 | 1256737.82 | -17149.0656 | 34125.4921 | -8850.6133 | 38557.5951 | 49525.1965 | 201144.268 | -7197.8825
293.92 | 9.3141 | 1.1733 |  | -87576.0503 | -189386.637 | 326536.481 | 5618610.17 | -799702.087 | -17088.9218 | 75964.4445 | -47186.7274 | 167239.162 | 583896.446 | 1191778.01 | -15456.6553 | 31013.02 | -9076.3687 | 39991.6958 | 52997.1833 | 187153.032 | -5415.7137
294.12 | 9.2772 | 1.1728 |  | -92544.1053 | -181811.618 | 356675.836 | 5420813.59 | -1034769.8 | -14064.8853 | 68089.8327 | -49124.613 | 173344.457 | 638139.943 | 1219781.04 | -12752.6124 | 37195.42 | -10929.2411 | 41034.0285 | 59239.5873 | 212049.75 | -5647.6647
294.32 | 9.2495 | 1.1728 |  | -84859.7099 | -187281.555 | 383079.024 | 5536095.17 | -888894.209 | -22685.4808 | 72041.9456 | -48303.2982 | 177736.808 | 617458.015 | 1225013.48 | -19308.6925 | 35949.5323 | -10056.0619 | 41467.6385 | 57629.6811 | 215748.649 | -7212.5645
294.52 | 9.1898 | 1.1728 |  | -73509.1485 | -181489.155 | 406465.571 | 5395220.1 | -628407.226 | -26133.7006 | 73284.1212 | -44122.537 | 181851.515 | 559065.334 | 1177149.31 | -19464.925 | 32046.8147 | -8640.7673 | 41868.8387 | 50551.6799 | 192502.995 | -7479.1563
294.72 | 9.1412 | 1.1728 |  | -60850.5654 | -162679.077 | 426844.791 | 4884510.88 | -454948.247 | -16058.0874 | 68659.5736 | -39309.9457 | 185973.348 | 504794.373 | 1102070.36 | -12418.2123 | 28921.5875 | -7567.2977 | 42717.3547 | 46397.5811 | 178888.612 | -5013.1482
294.92 | 9.1106 | 1.1728 |  | -45029.4784 | -140794.355 | 446247.126 | 4435557.55 | -152529.492 | -13370.5189 | 66424.8323 | -32881.5926 | 189333.907 | 452897.823 | 1136246.71 | -11821.7202 | 30831.7164 | -7151.055 | 43124.895 | 43414.2746 | 172719.174 | -5130.721
295.12 | 9.0746 | 1.1728 |  | -13971.3242 | -143714.849 | 463634.27 | 4535773.13 | 495829.417 | -26329.8895 | 70534.2934 | -26434.1689 | 193171.73 | 364239.75 | 1129639.11 | -15273.5028 | 28608.8914 | -5127.2914 | 43844.5727 | 32550.8116 | 155118.116 | -4980.3035
295.32 | 9.038 | 1.1728 |  | 11427.9555 | -132352.061 | 470941.179 | 4416463.1 | 1041827.57 | -26449.9352 | 74704.1298 | -20300.6076 | 194203.5 | 293970.396 | 1161270.97 | -18254.6033 | 28950.9659 | -3901.7498 | 43988.1806 | 27812.972 | 155777.942 | -6398.6472
295.52 | 9.0187 | 1.1728 |  | 32574.6512 | -101254.478 | 476771.592 | 3701054 | 1384742.93 | -30844.3443 | 68387.8091 | -12309.0069 | 194316.853 | 218719.707 | 1138170.45 | -19950.4857 | 30284.1274 | -2991.1392 | 43916.6497 | 25561.9199 | 171914.003 | -6929.0141
295.72 | 8.9906 | 1.1728 |  | 49962.2571 | -68485.2362 | 473620.04 | 2861751.71 | 1674628.45 | -21261.3039 | 59293.4825 | -2942.0136 | 193104.957 | 125418.229 | 1084390.21 | -11912.1341 | 32082.0951 | -2207.3901 | 43505.8678 | 24355.6832 | 190176.215 | -2962.4371
295.92 | 8.9732 | 1.1728 |  | 76639.1073 | -49989.4683 | 469421.716 | 2570410.78 | 2225172.53 | -23671.1294 | 60910.2688 | 4299.9902 | 191941.257 | 54244.4885 | 1143128.43 | -11975.3982 | 34019.731 | -1205.8475 | 43366.1524 | 20879.8611 | 201935.343 | -3453.0524
296.12 | 8.9648 | 1.1728 |  | 115867.432 | -61360.2933 | 458431.717 | 3050719.46 | 3165411.33 | -37510.8116 | 77449.8011 | 10088.5694 | 189126.923 | -38045.4639 | 1222516.94 | -23108.9678 | 30410.7437 | 1554.9757 | 42585.1513 | 5635.9809 | 173465.714 | -6895.7937
296.32 | 8.941 | 1.1728 |  | 142830.617 | -61284.8426 | 441982.393 | 2961982.38 | 3702882.94 | -44836.3102 | 78733.4551 | 16803.7613 | 185955.538 | -132096.115 | 1157757.96 | -21827.4887 | 27613.0477 | 3501.6388 | 42375.9766 | -3473.0704 | 160954.88 | -5725.2425
296.52 | 8.9178 | 1.1728 |  | 149684.001 | -28784.0043 | 418766.212 | 2252058.67 | 3744538.77 | -35586.2622 | 71152.9409 | 21024.3714 | 180273.225 | -157317.985 | 1163461.95 | -17171.5958 | 30979.1096 | 3204.5468 | 41336.8742 | -1634.8708 | 177435.326 | -5663.9774
296.72 | 8.8931 | 1.1728 |  | 164578.171 | -26104.6931 | 396606.932 | 2132948.55 | 3946876.8 | -37627.821 | 68551.4227 | 23662.167 | 175206.623 | -180036.101 | 1098483.54 | -16944.4596 | 28721.876 | 3216.2185 | 40526.351 | -2548.5368 | 159724.425 | -3993.2458
296.92 | 8.8841 | 1.1728 |  | 180565.522 | -27151.4726 | 368213.613 | 2162341.14 | 4301263.4 | -43811.9241 | 73142.7061 | 26889.9418 | 166906.551 | -231096.701 | 1064502.42 | -20117.4602 | 24481.7376 | 4566.0707 | 38517.2479 | -8254.4102 | 138322.854 | -5938.6059
297.12 | 8.8682 | 1.1728 |  | 188835.937 | -23242.5259 | 335810.915 | 2140452.31 | 4590514.53 | -42016.4678 | 77289.5723 | 30598.4441 | 159677.631 | -306665.152 | 1090709.34 | -18749.6778 | 23188.7002 | 6746.3024 | 37463.6419 | -20243.4376 | 124502.824 | -4410.6748
297.32 | 8.8707 | 1.1731 |  | 202831.701 | -25880.5097 | 308068.697 | 2271079.8 | 4930594.45 | -41834.5911 | 77946.0502 | 33634.5473 | 153604.327 | -334394.512 | 1108093.56 | -15426.1161 | 26204.9706 | 6543.6696 | 36397.9778 | -16940.3923 | 152994.826 | -4592.6328
297.52 | 8.8791 | 1.1738 |  | 195539.932 | -35482.3224 | 282420.388 | 2685898.04 | 4950603.05 | -37092.9665 | 86987.1882 | 31051.159 | 149207.718 | -312073.517 | 1318188.47 | -16233.1997 | 32557.0756 | 6503.9006 | 36117.5253 | -19659.7437 | 174179.618 | -5147.4964
297.72 | 8.89 | 1.1748 |  | 195222.32 | -49197.8843 | 255436.877 | 3337629.28 | 4985952.39 | -28848.8841 | 98597.4817 | 24078.1076 | 143901.334 | -195375.414 | 1492815.62 | -15985.3349 | 36974.3461 | 3407.3907 | 35713.7001 | -4088.994 | 199469.175 | -4745.4438
297.92 | 8.9059 | 1.176 |  | 183303.166 | -73424.3302 | 228752.024 | 4069193.31 | 4808769.46 | -28110.1931 | 105219.955 | 17062.4007 | 136148.322 | -110892.072 | 1579966.28 | -20594.3474 | 38617.5945 | 2019.6369 | 33657.27 | 4550.5311 | 217482.33 | -6510.6352
298.12 | 8.9216 | 1.177 |  | 164100.499 | -81926.3289 | 200980.519 | 4198916.82 | 4448975.49 | -28624.8907 | 103293.907 | 13192.6401 | 128853.962 | -75308.1911 | 1553520.49 | -18255.6544 | 39176.5805 | 1134.3175 | 32388.5147 | 9203.7053 | 224106.136 | -5592
298.32 | 8.927 | 1.1779 |  | 139413.657 | -77136.1999 | 182656.033 | 3940887.64 | 3920659.36 | -25184.8259 | 94142.144 | 10601.8807 | 123852.31 | -39899.4968 | 1521080.42 | -15438.6749 | 40577.1299 | 348.5702 | 31292.4785 | 11941.6866 | 232552.117 | -4810.2333
298.52 | 8.9324 | 1.1794 |  | 120721.733 | -90359.3101 | 170779.693 | 4021178.06 | 3511347.57 | -23131.3809 | 89283.9215 | 6460.3425 | 122243.431 | 9265.8991 | 1443765.5 | -12224.3467 | 38326.3903 | -533.1152 | 31272.8468 | 15608.4845 | 218379.574 | -3039.9509
298.72 | 8.9456 | 1.1806 |  | 94804.4284 | -103890.575 | 159936.619 | 4343672.72 | 3074982.4 | -23070.0219 | 91402.1621 | 202.2579 | 119791.553 | 75894.3443 | 1476026.87 | -13745.593 | 38582.9273 | -1354.5355 | 30522.8531 | 18039.0904 | 222889.712 | -3989.4753
298.92 | 8.9298 | 1.1818 |  | 70394.8066 | -132483.708 | 156772.06 | 4932196.25 | 2620311.71 | -32050.4337 | 93823.6938 | -7446.1225 | 120034.444 | 150428.552 | 1482498.2 | -19018.9586 | 38094.4204 | -2394.9868 | 31179.8094 | 21938.0766 | 215338.663 | -5765.5493
299.12 | 8.9191 | 1.1843 |  | 48106.3875 | -149343.003 | 157054.642 | 5363207.05 | 2054849.89 | -25832.3594 | 95629.6795 | -18912.8971 | 120374.509 | 292934.046 | 1466662.2 | -15145.857 | 37852.0955 | -5389.8891 | 31122.1605 | 36113.1638 | 217897.43 | -4375.59
299.32 | 8.9411 | 1.1867 |  | 22706.2572 | -168037.323 | 161592.381 | 5861724.24 | 1563643.56 | -20286.8811 | 98545.3014 | -27983.2852 | 120313.959 | 387911.374 | 1549705.3 | -13445.1416 | 39655.1669 | -6398.6609 | 30892.9301 | 37367.0054 | 219518.385 | -4452.3808
299.52 | 8.9487 | 1.1879 |  | 3374.543 | -190892.433 | 172361.782 | 6477030.61 | 1371402.79 | -26518.9595 | 107241.194 | -33256.8235 | 122464.319 | 453806.411 | 1677175.63 | -17287.0024 | 41697.1867 | -7390.1743 | 31280.3535 | 42383.0177 | 228047.569 | -6099.2865
299.72 | 8.9571 | 1.189 |  | -11666.0582 | -206094.982 | 187860.947 | 6763890.07 | 1098320.75 | -28028.8191 | 108239.402 | -37737.4306 | 126819.109 | 492809.084 | 1665902.06 | -19944.8905 | 42932.595 | -8257.0733 | 32407.4412 | 49492.3994 | 242553.888 | -6539.2647
299.92 | 8.9924 | 1.1897 |  | -37496.9233 | -185375 | 208858.549 | 6225406.63 | 503380.653 | -17150.2465 | 96671.6295 | -40252.4365 | 130813.206 | 584512.055 | 1708448.08 | -11420.7338 | 48396.468 | -11546.0423 | 32998.1916 | 63950.2679 | 265935.974 | -3919.5377
300.12 | 9.0285 | 1.1896 |  | -57901.1993 | -196800.016 | 236814.642 | 6439188.23 | 102665.332 | -17112.377 | 96888.9318 | -45254.6545 | 138269.712 | 621378.187 | 1724436.08 | -15819.1321 | 48808.4064 | -11396.3652 | 34146.9672 | 66297.5796 | 280671.009 | -5759.7358
300.32 | 9.0503 | 1.1892 |  | -53666.1618 | -229394.969 | 270869.686 | 7054131.35 | 166393.376 | -31472.0161 | 105822.67 | -49480.2462 | 147941.477 | 638899.049 | 1632458.8 | -19157.8007 | 39402.7484 | -10144.0666 | 36078.9837 | 56686.632 | 219915.099 | -5972.4135
300.52 | 9.0592 | 1.1894 |  | -65002.5761 | -229563.267 | 297223.072 | 7094525.87 | -56520.6922 | -23641.648 | 105097.897 | -52607.0683 | 155023.314 | 666048.034 | 1625150.06 | -11583.7532 | 40352.6543 | -10490.2387 | 37632.1952 | 53009.1832 | 209181.895 | -3850.6755
300.72 | 9.0952 | 1.1899 |  | -70786.962 | -219788.336 | 329935.304 | 6780688.97 | -294386.001 | -24771.1933 | 94269.1267 | -51987.6457 | 162164.652 | 691150.23 | 1596358.91 | -18632.9649 | 45669.8109 | -12409.1944 | 38967.9177 | 67399.6178 | 257124.494 | -6197.5096
300.92 | 9.1109 | 1.1896 |  | -72354.4144 | -202310.347 | 357557.935 | 6195580 | -365497.881 | -31089.6869 | 83775.7203 | -46286.7975 | 166387.695 | 635645.612 | 1517808.98 | -20650.0681 | 45561.8486 | -11621.7865 | 38748.324 | 67418.4222 | 266229.243 | -7403.6844
301.12 | 9.1043 | 1.1896 |  | -65359.4837 | -184330.591 | 390960.092 | 5571914.59 | -336866.283 | -20172.4322 | 76377.9237 | -41853.9693 | 176244.972 | 553127.435 | 1323351.25 | -17059.6498 | 38914.8506 | -9336.6521 | 41039.1893 | 55963.8888 | 232183.622 | -5276.2744
301.32 | 9.1267 | 1.1901 |  | -56203.0498 | -161385.395 | 418276.823 | 4913852.63 | -222184.315 | -16922.4162 | 73114.9006 | -36409.5905 | 182497.573 | 477727.577 | 1183552.19 | -12872.2175 | 31330.7334 | -7434.271 | 41784.6356 | 46015.0485 | 185755.523 | -4057.2806
301.52 | 9.1359 | 1.1901 |  | -43515.6716 | -147672.879 | 441466.039 | 4537568.59 | 14310.5928 | -15623.7061 | 69183.1168 | -30439.2811 | 189076.958 | 389365.823 | 1109473.57 | -13161.1445 | 27873.7585 | -5089.2359 | 43183.7418 | 33202.3068 | 163762.973 | -4235.0528
301.72 | 9.1394 | 1.1902 |  | -14416.8536 | -141259.684 | 463464.299 | 4339941.65 | 499672.545 | -26705.8678 | 65961.2908 | -24194.5749 | 194788.536 | 338292.221 | 1033244.88 | -17677.3421 | 26997.7861 | -4923.3918 | 44313.6868 | 34268.3474 | 161324.549 | -4934.8619
301.92 | 9.1598 | 1.1905 |  | -1043.541 | -116013.817 | 476453.878 | 3785133.41 | 732871.715 | -22053.0377 | 63437.9138 | -18260.4569 | 197054.806 | 268028.391 | 1034072.52 | -15631.7637 | 28488.9992 | -3678.1943 | 44474.6809 | 27903.076 | 161699.541 | -5563.4321
302.12 | 9.1996 | 1.1905 |  | 36008.9861 | -109962.263 | 485345.761 | 3601787.41 | 1476581.75 | -34153.2392 | 61945.8564 | -8157.0107 | 199401.244 | 159759.827 | 972719.107 | -19796.9688 | 27626.8756 | -2131.5568 | 44937.1323 | 23364.8009 | 167961.619 | -5897.9471
302.32 | 9.2205 | 1.1899 |  | 54152.5204 | -73767.7789 | 490012.136 | 2836059.35 | 1854165.31 | -32834.5803 | 59024.5559 | 1259.7577 | 200760.06 | 45440.5724 | 1025985.79 | -19052.9289 | 29703.2036 | 227.5765 | 45141.3774 | 11976.8566 | 174689.837 | -6108.8688
302.52 | 9.2251 | 1.1896 |  | 81109.175 | -64514.8397 | 489336.742 | 2587870.36 | 2380294.78 | -40465.2959 | 58181.7911 | 8619.1696 | 202180.764 | -25192.1137 | 1031532.28 | -19883.6342 | 30867.979 | 1052.0704 | 45762.5671 | 9784.5839 | 188422.269 | -5951.8143
302.72 | 9.2348 | 1.1902 |  | 113546.209 | -63283.6799 | 478968.426 | 2767268.83 | 3000449.62 | -40167.6416 | 68466.8001 | 11624.8332 | 200630.04 | -62709.5024 | 1049795.25 | -18975.8329 | 26497.4067 | 1898.4695 | 45568.787 | 5852.8516 | 159722.261 | -5437.6549
302.92 | 9.2265 | 1.1908 |  | 144519.088 | -83953.4586 | 466260.086 | 3380823.87 | 3668975.42 | -43727.1644 | 81551.7852 | 13613.7827 | 198123.18 | -121027.565 | 1055133.71 | -21176.3892 | 22435.3978 | 3742.671 | 45036.8671 | -4911.4077 | 125003.343 | -5427.6042
303.12 | 9.2159 | 1.1912 |  | 167142.059 | -77176.4663 | 443060.955 | 3450435.69 | 4115823.89 | -42110.355 | 85363.8813 | 16427.6261 | 192444.425 | -120349.438 | 1179742.94 | -21692.452 | 26867.5307 | 2956.8908 | 44410.2906 | -173.1819 | 151614.564 | -6426.6711
303.32 | 9.2303 | 1.1916 |  | 176990.462 | -52813.5946 | 418864.274 | 3094904.22 | 4406351.58 | -30694.676 | 86652.8174 | 21416.7549 | 184867.92 | -162038.127 | 1331104.44 | -16531.8103 | 33551.8367 | 3333.0761 | 42624.256 | -2411.1288 | 183126.231 | -4941.109
303.52 | 9.2232 | 1.1917 |  | 193669.532 | -50709.9176 | 390383.917 | 3263743.38 | 4923679.03 | -27456.5771 | 96301.946 | 25383.1853 | 178869.77 | -216326.44 | 1474725.9 | -16195.8593 | 35534.4414 | 4931.5613 | 41835.2266 | -11603.4431 | 191057.686 | -4697.3602
303.72 | 9.228 | 1.1925 |  | 213481.083 | -62445.562 | 366563.741 | 3725811.99 | 5425970.06 | -30623.8193 | 105275.851 | 27033.8439 | 174191.147 | -210580.12 | 1594818.8 | -17144.0735 | 39297.7573 | 3863.0123 | 41271.7502 | -5904.7068 | 209822.069 | -4758.6322
303.92 | 9.2684 | 1.1926 |  | 215561.807 | -63639.7467 | 333444.551 | 4197439.54 | 5660520.28 | -19441.5844 | 118568.006 | 24635.036 | 166742.338 | -176729.019 | 1838854.15 | -16566.5685 | 47367.3253 | 2658.3898 | 40384.6437 | -1105.4486 | 244215.673 | -4992.8443
304.12 | 9.3096 | 1.1912 |  | 221875.875 | -88124.8838 | 307447.361 | 4906555.46 | 5861381.61 | -25925.073 | 124777.448 | 22433.5037 | 161891.368 | -130524.667 | 1946687.84 | -20977.2504 | 50867.3939 | 1162.9142 | 39772.2936 | 10519.6525 | 278590.54 | -5825.2566
304.32 | 9.3359 | 1.1894 |  | 203128.672 | -79652.9188 | 279173.833 | 4768638.85 | 5410902.12 | -22396.8713 | 121703.956 | 17319.354 | 154538.525 | -30232.2804 | 2007757.66 | -20177.6663 | 54642.8785 | -1852.5741 | 38381.4578 | 27952.32 | 301589.162 | -6487.6807
304.52 | 9.3641 | 1.188 |  | 175836.869 | -74549.4035 | 251682.763 | 4506869.54 | 4706314.57 | -10817.1451 | 113390.119 | 10322.6809 | 147408.663 | 8784.3623 | 1866170.63 | -12987.6274 | 51605.7001 | -1738.1373 | 36712.3892 | 25737.0641 | 289747.184 | -4704.037
304.72 | 9.3721 | 1.1867 |  | 166715.868 | -92872.0812 | 231242.081 | 4496454.32 | 4469938.49 | -28020.875 | 105239.803 | 10843.5998 | 142517.712 | -2617.3989 | 1642897.2 | -18817.841 | 44323.4977 | -1526.4853 | 35262.867 | 25365.563 | 256016.874 | -4270.6723
304.92 | 9.3424 | 1.1861 |  | 136910.356 | -86000.3845 | 207143.234 | 3925080.17 | 3877632.56 | -35574.9717 | 90191.9727 | 12488.6925 | 135983.452 | -56803.4549 | 1497822.25 | -21261.519 | 40534.6685 | 850.1211 | 33946.6401 | 12230.3872 | 237979.372 | -6023.245
305.12 | 9.3235 | 1.1864 |  | 112269.58 | -68577.4504 | 195169.2 | 3287214.06 | 3293769.29 | -21451.2646 | 78676.146 | 10176.5204 | 134936.599 | -9777.0738 | 1407493.71 | -12204.6753 | 40097.3437 | -695.141 | 34317.9704 | 18045.1915 | 235019.141 | -2951.7172
305.32 | 9.3181 | 1.1863 |  | 83258.8339 | -90269.9334 | 190704.257 | 3674770.42 | 2722405.86 | -29493.4641 | 78832.871 | 1837.8401 | 134294.41 | 59104.2378 | 1437076.65 | -15622.5473 | 40503.3837 | -769.9223 | 33863.0516 | 15097.0108 | 237660.629 | -5069.0769
305.52 | 9.2969 | 1.186 |  | 65186.6104 | -125699.444 | 185400.604 | 4730815.44 | 2454841.87 | -31355.3022 | 92376.8327 | -9413.5091 | 135234.267 | 189128.418 | 1503321 | -18040.526 | 38833.4523 | -3101.4147 | 35053.1046 | 24341.8841 | 214896.45 | -4908.0291
305.72 | 9.279 | 1.1863 |  | 36717.543 | -156455.236 | 186566.268 | 5650891.85 | 1881645.46 | -24646.0028 | 100786.051 | -23826.1236 | 134474.493 | 350078.767 | 1604877.15 | -17444.7962 | 40908.0121 | -5633.294 | 34408.86 | 34789.647 | 225544.882 | -5751.6284
305.92 | 9.2964 | 1.1863 |  | 15579.5949 | -188576.923 | 190862.085 | 6522140.61 | 1572652.04 | -27218.241 | 109600.386 | -32584.6818 | 134380.597 | 480842.681 | 1723987.47 | -16772.3201 | 41951.9977 | -8377.8846 | 34575.1508 | 46568.9846 | 221242.868 | -4967.0221
306.12 | 9.3319 | 1.1855 |  | -4842.9169 | -200547.392 | 201354.514 | 6955895.19 | 1291623.21 | -22897.7321 | 115967.585 | -39286.5473 | 134731.611 | 524129.83 | 1838317.13 | -19091.247 | 46587.4047 | -8233.3368 | 34073.7627 | 47414.428 | 260937.465 | -7392.4037
306.32 | 9.3717 | 1.1839 |  | -21963.1861 | -196588.943 | 222170.501 | 6895780.06 | 1091019.57 | -17368.8829 | 119109.68 | -40816.2319 | 140435.468 | 540059.326 | 1887433.2 | -17448.3202 | 49092.6591 | -8734.1786 | 35474.3127 | 48811.008 | 266271.603 | -6347.3449
306.52 | 9.4145 | 1.1822 |  | -40862.6736 | -203096.535 | 251307.1 | 6896124.01 | 694785.324 | -19669.0014 | 113695.619 | -43930.1635 | 148566.391 | 569761.187 | 1858814.12 | -14254.3581 | 49806.2086 | -9127.1546 | 36783.6148 | 55178.3058 | 290798.106 | -6015.4404
306.72 | 9.4342 | 1.1799 |  | -51682.23 | -224935.542 | 286828.235 | 7238604.79 | 376408.823 | -31675.8385 | 112492.422 | -48524.3422 | 159816.967 | 627271.091 | 1790656.58 | -22618.7553 | 45151.975 | -9775.7741 | 39425.4538 | 55915.4177 | 251971.629 | -7972.4333
306.92 | 9.4298 | 1.1775 |  | -63382.8767 | -233125.728 | 316430.74 | 7070086.02 | -129098.203 | -39020.2891 | 100023.03 | -52144.9468 | 166814.804 | 672423.4 | 1579254.48 | -22923.1069 | 39713.1887 | -10804.4374 | 40453.7587 | 60606.4004 | 225190.223 | -7698.659
307.12 | 9.4198 | 1.1754 |  | -84238.5749 | -201757.813 | 343475.243 | 6114913.68 | -752814.483 | -17580.6052 | 81665.543 | -51615.6983 | 171715.342 | 677178.605 | 1370681.6 | -13653.0217 | 38465.4223 | -11911.4559 | 40992.1961 | 67106.3224 | 221902.43 | -4224.5851
307.32 | 9.3993 | 1.1734 |  | -81987.3913 | -195521.678 | 375353.359 | 5700109.36 | -841018.561 | -21638.6104 | 69958.6275 | -48522.6789 | 177705.481 | 633452.513 | 1246759.92 | -14442.6132 | 38595.2788 | -11002.5328 | 41512.9427 | 62289.5391 | 228070.442 | -4919.9786
307.52 | 9.3578 | 1.1728 |  | -69711.2582 | -192373.653 | 402852.324 | 5634914.11 | -509485.925 | -21255.5155 | 77003.0386 | -44641.9702 | 183982.623 | 560335.023 | 1243989.01 | -15651.0753 | 33610.3962 | -8499.5714 | 42607.244 | 48862.3995 | 193889.404 | -5435.2211
307.72 | 9.33 | 1.1728 |  | -47014.4718 | -189338.033 | 428373.159 | 5625448.9 | -452.2566 | -30045.8188 | 83460.2561 | -39321.5274 | 189756.102 | 491890.941 | 1221177.99 | -21410.9039 | 29614.2586 | -6941.397 | 43727.1994 | 41747.3823 | 167737.449 | -7380.6718
307.92 | 9.3102 | 1.1728 |  | -44618.5724 | -159793.956 | 450063.527 | 4919959.34 | 34878.6104 | -24502.9095 | 75983.4389 | -33442.555 | 194466.597 | 424026.373 | 1169727.75 | -18762.5059 | 29064.3796 | -5660.7913 | 44449.9462 | 35388.405 | 164011.044 | -6487.6511
308.12 | 9.289 | 1.1728 |  | -33882.9453 | -128102.665 | 470139.625 | 4143213.33 | 61220.3688 | -18978.5865 | 64365.0714 | -28473.7257 | 199462.66 | 387474.906 | 1083692.58 | -14212.4122 | 29475.5574 | -5671.5757 | 45672.2595 | 36129.7453 | 172413.841 | -4283.5195
308.32 | 9.3124 | 1.1728 |  | -5960.6454 | -118933.954 | 484847.734 | 3860083.21 | 593371.495 | -22330.6776 | 60979.2801 | -20497.8165 | 201139.992 | 319373.457 | 1008274.91 | -14857.3986 | 26791.1879 | -5018.3965 | 45235.981 | 35248.583 | 158504.674 | -5471.8264
308.52 | 9.3384 | 1.1728 |  | 18037.6871 | -98360.5357 | 495860.914 | 3416931.64 | 1155287.96 | -26543.1262 | 63000.456 | -10464.8767 | 203964.603 | 157839.012 | 996456.038 | -17917.7239 | 25124.0617 | -907.922 | 45915.1814 | 14096.8663 | 138991.482 | -5895.6091
308.72 | 9.3296 | 1.1728 |  | 50030.4036 | -73033.5952 | 499557.827 | 2887570.09 | 1811662.67 | -28936.5745 | 62626.3323 | 43.9201 | 205713.013 | 55404.9778 | 994550.158 | -18484.7543 | 25432.8269 | 335.5973 | 46375.8674 | 10134.0878 | 145821.065 | -5921.4107
308.92 | 9.3437 | 1.1728 |  | 78480.3728 | -66530.1998 | 504728.189 | 2742305.54 | 2363680.07 | -32486.0966 | 63227.3299 | 6600.0476 | 208288.021 | -18287.6395 | 997479.233 | -17691.9369 | 26278.0109 | 1494.7799 | 47064.4727 | 5909.4187 | 155243.748 | -5485.7127
309.12 | 9.33 | 1.1728 |  | 104970.211 | -63908.6095 | 488639.53 | 2931534.96 | 2906355.25 | -32779.1317 | 73399.3702 | 8943.6725 | 205642.804 | -36966.6953 | 1141325.04 | -15974.9378 | 28096.7517 | 1874.6626 | 46930.2597 | 3904.5079 | 156710.995 | -4505.9251
309.32 | 9.2676 | 1.1728 |  | 132270.362 | -79432.6639 | 474894.4 | 3642009.67 | 3437081.69 | -36656.7167 | 89995.0953 | 6240.8003 | 202387.278 | -13853.7685 | 1261424.8 | -21228.6444 | 28025.2119 | 1727.0458 | 46452.913 | 4232.4712 | 162621.947 | -5727.4689
309.52 | 9.2331 | 1.1728 |  | 161408.992 | -90431.499 | 445451.314 | 4095568.37 | 4037587.85 | -36100.0391 | 100416.129 | 7717.8811 | 192910.102 | 14957.8558 | 1390516.92 | -20957.2343 | 28617.2608 | 395.3011 | 44409.212 | 11946.8493 | 146925.21 | -6250.0642
309.72 | 9.1966 | 1.1728 |  | 174957.886 | -85200.5526 | 415129.211 | 4072508.51 | 4367816.08 | -31815.8834 | 100762.519 | 11838.2774 | 183245.52 | -71056.2393 | 1446930.41 | -18291.1072 | 33277.615 | 2640.218 | 42353.4254 | -242.4947 | 180130.298 | -5553.3734
309.92 | 9.1391 | 1.1728 |  | 189902.472 | -60899.8436 | 385014.498 | 3640035.71 | 4780293.11 | -24772.2512 | 99923.7799 | 19876.0414 | 175084.739 | -111158.657 | 1553977.67 | -14603.7035 | 39057.7545 | 1622.1254 | 40907.7669 | 6745.1283 | 214841.107 | -4222.8529
310.12 | 9.1052 | 1.1728 |  | 195781.547 | -61621.798 | 355368.567 | 3691211.66 | 4984994.85 | -28331.155 | 99585.193 | 23118.7758 | 167524.981 | -150230.037 | 1643360.07 | -16252.9747 | 44849.8316 | 1932.1644 | 39531.8807 | 7355.3938 | 253531.234 | -5338.5744
310.32 | 9.1025 | 1.1728 |  | 211439.017 | -66118.7444 | 326966.244 | 4069483.71 | 5417451.59 | -25451.2432 | 113082.351 | 23078.2131 | 161611.045 | -150096.463 | 1682149.18 | -15891.2136 | 40898.7617 | 1956.9476 | 38555.1848 | 10189.0748 | 233679.685 | -3574.4989
310.52 | 9.0859 | 1.1728 |  | 206241.647 | -83033.5557 | 301010.068 | 4503347.49 | 5343473.69 | -29948.8839 | 116419.803 | 18930.2155 | 156261.071 | -129981.429 | 1790124.94 | -18579.1357 | 45011.0918 | 2648.7369 | 37989.63 | -1305.8505 | 241276.572 | -4513.9414
310.72 | 9.067 | 1.1728 |  | 189842.53 | -63581.6502 | 264882.172 | 4365281.25 | 4994116.65 | -19409.9401 | 115546.456 | 13901.9286 | 146664.082 | 11841.2866 | 1959639.55 | -17251.9109 | 53693.6667 | -2393.7141 | 36773.6939 | 24118.7197 | 286645.173 | -5831.9883
310.92 | 9.0649 | 1.1728 |  | 176812.606 | -79782.6502 | 238859.888 | 4620795.55 | 4670458.79 | -23314.4591 | 112536.138 | 9053.4728 | 138725.797 | 54483.2879 | 1902489.61 | -16217.118 | 52428.5316 | -3017.5597 | 34535.3594 | 30072.2015 | 284883.676 | -5040.8571
311.12 | 9.0528 | 1.1728 |  | 162903.197 | -81079.4429 | 212290.075 | 4599192.34 | 4394276.22 | -14092.8728 | 112809.948 | 5518.297 | 131254.56 | 76483.9912 | 1844497.71 | -13379.4676 | 48884.5655 | -2844.9618 | 32822.3681 | 26643.4919 | 266616.983 | -4745.5962
311.32 | 9.0244 | 1.1728 |  | 142859.476 | -99744.5965 | 189633.001 | 4763117.78 | 4111482.87 | -17628.2138 | 107181.306 | 6542.4423 | 126748.963 | 21756.6196 | 1730227.57 | -13893.3298 | 45740.5807 | -1238.2973 | 32130.5993 | 17951.6232 | 250056.046 | -2922.2276
311.52 | 8.9735 | 1.1728 |  | 118745.279 | -93446.8494 | 173902.08 | 4438108.19 | 3521097.33 | -18026.0472 | 98178.46 | 1476.9378 | 122935.882 | 121710.514 | 1711710.34 | -13297.8054 | 47146.7545 | -3547.1696 | 31486.1176 | 28849.9117 | 264795.059 | -4693.8627
311.72 | 8.9602 | 1.1728 |  | 93227.5574 | -117116.973 | 161127.713 | 4855929.8 | 3002862.87 | -21288.1887 | 99023.4956 | -6271.0871 | 120040.734 | 167797.667 | 1617025.73 | -14829.5461 | 41348.5051 | -2901.6875 | 31043.1973 | 23965.6972 | 228792.106 | -4186.4255
311.92 | 8.9202 | 1.1728 |  | 64790.6935 | -124937.478 | 158024.363 | 4885854.43 | 2396698.14 | -19333.7973 | 94535.499 | -12591.7523 | 119241.984 | 259311.549 | 1597114.14 | -13624.2574 | 42863.6964 | -5448.8927 | 30895.6916 | 36920.5437 | 237968.345 | -3975.6882
312.12 | 8.8777 | 1.1728 |  | 32360.4466 | -139433.105 | 149708.095 | 5280153.39 | 1751518.94 | -20738.4726 | 97610.0625 | -23090.3624 | 116373.358 | 337665.003 | 1581296.94 | -18009.8151 | 39641.4166 | -5231.1211 | 30129.5843 | 33834.581 | 226140.692 | -6055.1144
312.32 | 8.8495 | 1.1728 |  | 17621.2969 | -157679.572 | 158027.98 | 5609235.32 | 1429655.91 | -17157.3595 | 98258.437 | -29332.6945 | 117947.268 | 441691.927 | 1561061.43 | -10030.6142 | 38433.0505 | -8029.1579 | 30451.1163 | 45278.5056 | 207940.896 | -2743.9628
312.52 | 8.846 | 1.1728 |  | -1923.7508 | -180703.902 | 162195.211 | 6446116.27 | 1234787 | -12659.339 | 111489.399 | -37738.4771 | 118680.069 | 495028.299 | 1694422.62 | -12099.4489 | 41286.7111 | -7927.5301 | 30529.905 | 40783.6155 | 214375.706 | -3901.144
312.72 | 8.8209 | 1.1728 |  | -17833.3765 | -201613.757 | 177111.046 | 7038067.91 | 1015771.71 | -20555.2944 | 116734.941 | -43538.4104 | 122372.74 | 584159.113 | 1862472.67 | -15441.376 | 49023.778 | -10364.7137 | 31956.7365 | 54439.1078 | 261736.489 | -4976.163
312.92 | 8.8154 | 1.1728 |  | -31967.9397 | -223382.32 | 195141.486 | 7623693.13 | 713894.272 | -29311.1576 | 120513.963 | -51938.5745 | 125069.123 | 698412.428 | 1940173.05 | -20293.3796 | 51582.8041 | -12621.8257 | 31534.8611 | 72138.4399 | 300375.907 | -8386.4745
313.12 | 8.8131 | 1.1728 |  | -53932.4376 | -241992.097 | 217286.876 | 7938229.93 | 262307.316 | -28590.0973 | 117273.591 | -56450.5222 | 131187.455 | 738343.587 | 1903380.09 | -17084.5274 | 50050.8796 | -13116.8886 | 33143.8709 | 73621.3248 | 277518.258 | -5316.8032
313.32 | 8.7967 | 1.1728 |  | -68478.9474 | -225073.451 | 238372.015 | 7494924.26 | -234497.246 | -16627.3881 | 110627.826 | -61550.4187 | 134100.098 | 829747.07 | 1860525.86 | -11964.0762 | 51375.5313 | -15870.1555 | 33328.073 | 86091.3966 | 289744.13 | -5593.0737
313.52 | 8.7878 | 1.1728 |  | -71717.6387 | -246031.61 | 270518.858 | 7671422.36 | -281793.379 | -25736.6938 | 108723.433 | -60303.6847 | 141736.391 | 777882.398 | 1664709.43 | -16399.8478 | 42588.6679 | -13817.3725 | 34118.4058 | 75764.6458 | 242699.024 | -4638.2577
313.72 | 8.743 | 1.1728 |  | -76666.2258 | -226466.827 | 296500.672 | 6956051.9 | -471430.509 | -23910.2852 | 95843.2089 | -55421.2511 | 147138.082 | 737640.784 | 1590599.13 | -13335.0404 | 43733.0733 | -13712.2057 | 35237.4293 | 72848.0613 | 240613.797 | -3473.7237
313.92 | 8.713 | 1.1728 |  | -90257.7055 | -189285.193 | 318847.924 | 5948922.95 | -780356.12 | -17094.5692 | 80370.588 | -50108.0168 | 150112.426 | 702876.046 | 1582289.31 | -14365.0909 | 49262.0233 | -13837.6767 | 35396.5365 | 77469.7842 | 282875.468 | -5776.9212
314.12 | 8.7009 | 1.1728 |  | -70899.2181 | -195800.46 | 353043.497 | 5875411.94 | -482838.483 | -18389.4462 | 77659.7971 | -45751.2316 | 159844.402 | 633654.367 | 1406033.3 | -14562.2994 | 41999.8092 | -12142.4069 | 37297.7936 | 71147.0101 | 245994.386 | -4069.0261
314.32 | 8.6827 | 1.1728 |  | -59864.2079 | -193681.713 | 379003.686 | 5721222.98 | -278217.601 | -16400.2327 | 75933.2336 | -41522.1025 | 165837.129 | 550977.225 | 1269640.35 | -12194.7543 | 36004.7389 | -9656.3257 | 37920.4167 | 55659.7482 | 205148.104 | -3583.9603
314.52 | 8.6703 | 1.1728 |  | -48369.4878 | -188466.443 | 403086.204 | 5533272.59 | -102726.459 | -23785.3456 | 71687.4617 | -37192.7996 | 172042.695 | 485861.002 | 1201776.3 | -14736.3385 | 34891.8938 | -8045.7655 | 39292.8027 | 47511.5589 | 201471.379 | -5826.2257
314.72 | 8.6716 | 1.1728 |  | -24148.4748 | -179205.871 | 418128.287 | 5302717.41 | 328682.216 | -21574.6843 | 72349.5939 | -31116.7926 | 175206.22 | 420366.149 | 1096033.29 | -12727.4588 | 29413.8701 | -7259.594 | 39705.3914 | 46973.7514 | 174085.275 | -4119.6657
314.92 | 8.6879 | 1.1728 |  | -6800.5996 | -158621.015 | 437099.111 | 4778589.6 | 676116.874 | -22182.2983 | 69673.7295 | -23876.9968 | 179189.327 | 320968.468 | 1038563.07 | -12680.6301 | 27772.7841 | -4945.7625 | 40178.1676 | 35137.1241 | 167624.308 | -4421.3289
315.12 | 8.677 | 1.1728 |  | 19524.8578 | -136613.796 | 443879.538 | 4307536.64 | 1175470.11 | -23515.6215 | 68630.4716 | -16089.2809 | 181270.66 | 225865.888 | 1013566.63 | -13733.872 | 26523.4292 | -2938.864 | 40922.8279 | 25555.3929 | 161764.445 | -4071.9824
315.32 | 8.6921 | 1.1728 |  | 44738.8662 | -117324.079 | 454059.397 | 3849286.58 | 1661200.47 | -31092.489 | 65862.8231 | -7878.6956 | 183270.177 | 144775.268 | 1044918.85 | -14804.0432 | 28093.2864 | -1540.5584 | 41064.5001 | 17751.6227 | 162896.49 | -4919.3636
315.52 | 8.6931 | 1.1728 |  | 68990.5859 | -102295.821 | 452818.424 | 3593879.69 | 2227566.76 | -34170.303 | 68457.8323 | 782.4732 | 183751.308 | 59588.435 | 1111370.34 | -15928.7247 | 30280.508 | -622.0735 | 41365.5554 | 15401.6017 | 171058.616 | -4790.9534
315.72 | 8.6693 | 1.1728 |  | 92657.6171 | -94928.6641 | 448211.521 | 3593353.99 | 2667628.01 | -36959.8469 | 71390.3083 | 4452.2356 | 183437.932 | 17198.9014 | 1169862.34 | -16859.6354 | 33755.3932 | -95.846 | 41558.8666 | 16414.7862 | 203061.729 | -5070.5525
315.92 | 8.6668 | 1.1728 |  | 121265.561 | -90864.4767 | 436814.255 | 3734680.87 | 3216664.36 | -44073.4111 | 83566.6051 | 5978.0489 | 179936.325 | 12875.1059 | 1208008.32 | -20600.277 | 30504.0077 | -198.3539 | 40638.0773 | 16554.8062 | 181342.124 | -6558.1406
316.12 | 8.6533 | 1.1728 |  | 140381.942 | -90190.9306 | 419761.309 | 3758611.38 | 3616743.41 | -45738.4319 | 89675.3826 | 9186.3034 | 175390.913 | -70961.652 | 1187204.02 | -20676.5292 | 25539.201 | 2712.1925 | 39839.0687 | -1898.1033 | 141372.18 | -5425.9283
316.32 | 8.6289 | 1.1728 |  | 155218.535 | -57708.5223 | 400538.531 | 3074502.45 | 3863197.6 | -32279.3548 | 82429.6169 | 15263.7758 | 170521.828 | -101904.031 | 1242271.58 | -12691.4714 | 31690.9424 | 1981.5748 | 39270.7079 | 1876.9058 | 169740.832 | -3731.574
316.52 | 8.6351 | 1.1728 |  | 171765.468 | -46549.6031 | 377047.103 | 3032124.32 | 4296641.93 | -25976.8065 | 86559.6035 | 19230.4583 | 164506.616 | -122294.824 | 1414433.01 | -10960.393 | 37532.5348 | 1983.0187 | 38175.3569 | 2160.8868 | 199384.918 | -3591.4472
316.72 | 8.6573 | 1.1728 |  | 198679.421 | -60479.2253 | 354355.621 | 3640866.23 | 5050735.73 | -31040.3662 | 102660.913 | 23064.0891 | 159591.114 | -179232.54 | 1544578.71 | -14851.1739 | 37926.0444 | 3343.6266 | 37266.6831 | -2812.9079 | 205036.904 | -4160.8441
316.92 | 8.649 | 1.1728 |  | 210480.644 | -68879.622 | 327005.281 | 3981222.99 | 5445201.06 | -35929.8338 | 110431.672 | 25690.7012 | 153742.665 | -189216.323 | 1698916 | -19050.2119 | 41674.9478 | 3162.8112 | 36588.3336 | 211.9278 | 228544.985 | -5561.1519
317.12 | 8.6869 | 1.1728 |  | 211443.768 | -58600.5369 | 300460.983 | 3942494.44 | 5431780.23 | -27851.7518 | 111752.599 | 23280.174 | 147846.283 | -149665.922 | 1760076.03 | -16754.6867 | 45713.7794 | 1703.6513 | 35738.5562 | 8643.428 | 254216.923 | -5103.5381
317.32 | 8.7509 | 1.1728 |  | 206857.082 | -48140.9003 | 272207.05 | 3701760.46 | 5283913.55 | -26653.0794 | 106286.783 | 23258.0018 | 141256.063 | -101583.323 | 1763225.56 | -15878.4436 | 48257.3259 | -757.0943 | 34411.5207 | 20687.1795 | 261890.199 | -4317.7291
317.52 | 8.8004 | 1.1728 |  | 192530.004 | -51128.0813 | 250772.515 | 3595366.42 | 4936278.59 | -25952.1759 | 100176.164 | 21014.1437 | 137066.793 | -127334.34 | 1643034.6 | -13755.2389 | 45194.3468 | 1054.5908 | 33580.0915 | 10743.2646 | 252169.494 | -3801.989
317.72 | 8.8323 | 1.1728 |  | 181241.996 | -50606.9942 | 225150.812 | 3396189.16 | 4690143.52 | -23482.8663 | 95414.8099 | 20241.5536 | 132019.92 | -130937.789 | 1516344.35 | -12344.2092 | 39567.0568 | 1667.6951 | 32482.9137 | 7176.3398 | 224602.797 | -3090.2601
317.92 | 8.8598 | 1.1728 |  | 163302.418 | -58206.6733 | 203342.239 | 3330716.43 | 4296318.58 | -23723.6315 | 87366.1457 | 18889.6539 | 127432.755 | -160261.833 | 1367925.3 | -11593.937 | 36014.9541 | 3117.3255 | 31650.9523 | 526.8976 | 214537.515 | -3964.8697
318.12 | 8.8781 | 1.1728 |  | 153316.315 | -77807.3836 | 187700.499 | 3634650.74 | 4170213.56 | -25876.7584 | 92377.6662 | 15528.8338 | 125858.863 | -117457.751 | 1331912.42 | -14257.2219 | 30969.6107 | 2535.8789 | 31671.2614 | 1520.4272 | 179979.887 | -3561.6469
318.32 | 8.89 | 1.1728 |  | 124591.444 | -90496.9315 | 171422.257 | 3988069.11 | 3617857.68 | -24144.4855 | 92521.993 | 7340.0836 | 122893.792 | -61549.4158 | 1381447.25 | -14164.9499 | 33824.7625 | 2682.7126 | 31287.7327 | -5275.0446 | 187743.263 | -4754.6278
318.52 | 8.8873 | 1.1728 |  | 106584.345 | -105516.195 | 163949.666 | 4370599.07 | 3210844.69 | -26645.7188 | 91711.7892 | 290.2006 | 121707.165 | 92908.8867 | 1489771.01 | -15329.6405 | 40510.1445 | -2403.8705 | 31708.902 | 23678.6751 | 227777.239 | -5260.4839
318.72 | 8.8887 | 1.1728 |  | 79057.6738 | -127755.608 | 155640.952 | 5045869.91 | 2763562.79 | -24239.2236 | 99235.7293 | -9349.0637 | 118177.783 | 201780.79 | 1604330.91 | -16833.6477 | 42850.6392 | -4173.8282 | 30533.1694 | 31753.6084 | 238713.314 | -5335.8043
318.92 | 8.9439 | 1.1728 |  | 62870.7323 | -150562.521 | 152809.369 | 5760003.74 | 2553827.71 | -16970.5816 | 106844.78 | -16991.7982 | 117990.685 | 310035.923 | 1727299.74 | -11033.637 | 47480.3316 | -7309.3512 | 30903.6939 | 46459.6944 | 265283.042 | -2362.9976
319.12 | 8.9781 | 1.1728 |  | 41414.9852 | -184662.396 | 157375.437 | 6847517.42 | 2355322.47 | -17401.9743 | 124701.725 | -27062.0486 | 118919.338 | 365301.724 | 1942320.68 | -17468.4892 | 51080.0656 | -6388.1384 | 30772.4003 | 41438.8462 | 284233.751 | -5900.1986
319.32 | 9.0051 | 1.1728 |  | 35204.0189 | -228047.533 | 169569.436 | 7986075.84 | 2333325.79 | -27923.3997 | 137761.065 | -35829.9725 | 125253.527 | 483062.965 | 2015074.16 | -19553.7551 | 49543.0555 | -8756.6694 | 32887.5132 | 54474.3391 | 273703.538 | -4463.113
319.52 | 9.076 | 1.1728 |  | -252.7284 | -218672.111 | 185556.826 | 7841970.02 | 1537765.62 | -24561.3015 | 129771.407 | -44045.5397 | 126354.905 | 638980.182 | 2168536.11 | -20987.1468 | 59578.686 | -12733.092 | 32694.0354 | 71799.6796 | 329402.637 | -7528.4461
319.72 | 9.1324 | 1.1728 |  | -27697.5643 | -225972.103 | 209379.68 | 7840891.31 | 886085.984 | -23357.6997 | 125481.723 | -51079.5679 | 133896.75 | 722191.113 | 2066790.03 | -18516.6427 | 56637.5563 | -14534.8041 | 34440.8649 | 79948.8967 | 309361.017 | -6635.9865
319.92 | 9.1719 | 1.1728 |  | -40731.6631 | -232230.224 | 238679.063 | 7648373.46 | 389949.852 | -25044.421 | 115725.193 | -55906.5434 | 140402.164 | 790560.44 | 1901500.76 | -13118.1553 | 50848.0573 | -15431.7082 | 34652.7911 | 82487.4056 | 288824.025 | -3209.2334
320.12 | 9.2088 | 1.1728 |  | -66388.4215 | -225673.974 | 263593.557 | 7371981.81 | 32787.8476 | -21804.345 | 111982.367 | -53842.0899 | 145304.42 | 700255.331 | 1854482.63 | -16115.1558 | 49027.5214 | -11972.0179 | 35543.5619 | 66776.3229 | 269488.546 | -5181.328
320.32 | 9.2137 | 1.1728 |  | -53527.2262 | -234227.205 | 301157.385 | 7221569.62 | 237646.611 | -28059.9403 | 106714.473 | -49107.708 | 156154.175 | 643893.727 | 1714158.47 | -16473.7465 | 44785.5397 | -10863.7932 | 37544.5572 | 64301.7992 | 263818.548 | -5219.3461
320.52 | 9.2491 | 1.1728 |  | -59150.8619 | -218259.789 | 335628.193 | 6858358.2 | 175564.256 | -17468.2486 | 103363.618 | -46571.6556 | 165468.656 | 642759.916 | 1755223.6 | -10516.8586 | 48326.0631 | -11859.2766 | 39554.8194 | 67572.661 | 272260.844 | -2468.895
320.72 | 9.2967 | 1.1729 |  | -58858.6439 | -223786.931 | 368104.415 | 7230351.68 | 218478.726 | -27173.4395 | 113353.234 | -50387.4705 | 174176.775 | 667313.308 | 1913715.25 | -21115.1221 | 51088.5784 | -10849.0421 | 41381.8543 | 59576.6603 | 281808.072 | -7544.459
320.92 | 9.2814 | 1.173 |  | -42630.7759 | -246247.62 | 399202.393 | 7727594.99 | 482753.793 | -40529.457 | 119032.739 | -51110.0622 | 183400.632 | 663640.311 | 1807191.51 | -24057.112 | 45170.9758 | -10632.5695 | 43402.2671 | 61068.8267 | 253537.613 | -6892.7948
321.12 | 9.3177 | 1.1748 |  | -37000.9732 | -224122.107 | 426922.719 | 7088958.6 | 373351.549 | -32489.9246 | 105039.564 | -48639.0319 | 187928.804 | 684022.114 | 1723880.8 | -19119.2539 | 46918.0503 | -12511.6791 | 43784.5876 | 71646.5202 | 266980.016 | -6516.6864
321.32 | 9.3908 | 1.1754 |  | -23424.1149 | -187690.352 | 447690.48 | 6098695.24 | 629723.515 | -22158.2207 | 92986.706 | -36879.5363 | 190846.844 | 553972.356 | 1608699.13 | -14887.4653 | 47163.9278 | -11023.6572 | 43507.0361 | 68484.2288 | 275626.828 | -4223.0002
321.52 | 9.3989 | 1.1751 |  | -12781.1768 | -153370.37 | 473007.899 | 5181064.91 | 900337.527 | -20818.9634 | 83290.0006 | -25077.0687 | 197996.837 | 391173.144 | 1576223.38 | -13375.4445 | 47307.5489 | -7175.013 | 45025.0351 | 48429.2672 | 269328.471 | -3929.1507
321.72 | 9.4304 | 1.1763 |  | 26216.8226 | -155147.992 | 493088.355 | 5208851.93 | 1648914.73 | -27965.3739 | 87666.934 | -17726.4298 | 206445.141 | 329181.606 | 1497180.18 | -14464.2509 | 43432.8047 | -6998.9548 | 47206.6289 | 51783.6038 | 255584.574 | -2216.9495
321.92 | 9.5094 | 1.1771 |  | 56437.0779 | -153237.067 | 508048.383 | 5308371.81 | 2256675.75 | -34669.187 | 91597.3918 | -12662.6784 | 209756.107 | 257455.551 | 1528289.1 | -22541.3546 | 44851.5438 | -4892.219 | 47138.2565 | 41204.1378 | 269631.035 | -6783.5369
322.12 | 9.5408 | 1.1766 |  | 75021.2835 | -137057.842 | 510275.896 | 4999549.59 | 2703198.15 | -32909.9603 | 95983.115 | -5263.2646 | 211315.403 | 141519.144 | 1557698.48 | -22572.9034 | 42758.3293 | -1865.2412 | 47963.6696 | 25666.049 | 252373.825 | -6989.743
322.32 | 9.5467 | 1.1776 |  | 111589.092 | -134539.146 | 509264.429 | 4908132.5 | 3289290.06 | -38774.8782 | 97249.7984 | -112.8585 | 213045.114 | 89269.8192 | 1488032.67 | -18719.6734 | 38247.5696 | -1125.9253 | 48719.2291 | 22422.6802 | 222086.344 | -4711.2115
322.52 | 9.6073 | 1.1792 |  | 136715.171 | -102836.167 | 499960.939 | 4385167.1 | 3772944.93 | -28766.8106 | 99404.3863 | 6046.0005 | 210405.297 | 57180.3637 | 1552048.23 | -18274.5351 | 40429.8681 | -1509.104 | 48090.4873 | 23430.467 | 225925.474 | -4515.2316
322.72 | 9.652 | 1.1793 |  | 151967.926 | -76811.4876 | 486687.993 | 3896505.41 | 4204384.05 | -27061.5133 | 100348.415 | 14885.3409 | 206445.419 | -57154.4119 | 1691697.43 | -17522.7859 | 45885.8853 | 984.2166 | 47246.7304 | 9315.9949 | 246687.104 | -5332.3335
322.92 | 9.6314 | 1.1796 |  | 180425.056 | -76424.4762 | 468027.103 | 3954294.2 | 4806786.75 | -34820.7744 | 104639.706 | 21049.7152 | 205273.91 | -109836.829 | 1700471.59 | -21881.1268 | 44954.2034 | 1177.1221 | 47988.7112 | 11321.3334 | 241514.473 | -5560.0835
323.12 | 9.6706 | 1.1817 |  | 195881.73 | -61012.7693 | 445111.899 | 3791875.78 | 4999693.99 | -27554.7905 | 104908.107 | 20741.7628 | 199914.499 | -68164.839 | 1719151.88 | -16864.3227 | 46343.7967 | -554.7641 | 46646.2556 | 21068.0292 | 261539.441 | -4215.3787
323.32 | 9.7269 | 1.1821 |  | 206250.06 | -67675.8437 | 415078.102 | 3976294.28 | 5260871.05 | -32782.4232 | 109223.787 | 22648.5808 | 192244.38 | -136484.743 | 1727081.52 | -19723.3348 | 43898.2315 | 2176.7919 | 44949.452 | 7462.562 | 248632.274 | -5466.5063
323.52 | 9.7313 | 1.1813 |  | 222869.299 | -78364.0674 | 388473.31 | 4104873.51 | 5685854.79 | -42090.0811 | 109080.785 | 28665.8188 | 186901.34 | -226741.011 | 1632616.96 | -22849.1201 | 40781.5888 | 3964.035 | 44068.1299 | -213.3565 | 234433.32 | -6092.711
323.72 | 9.754 | 1.1816 |  | 216864.596 | -62778.9549 | 356072.385 | 3843458.98 | 5596620.24 | -24150.7767 | 108096.689 | 29076.5057 | 181461.588 | -245188.19 | 1668590.53 | -12805.9404 | 43148.1302 | 4064.7095 | 43746.8022 | -1653.4815 | 239951.41 | -2585.096
323.92 | 9.8121 | 1.1809 |  | 215343.326 | -68993.8152 | 328503.131 | 4194308.02 | 5640256.27 | -24792.2421 | 116332.251 | 24935.3809 | 175796.434 | -190893.805 | 1752836.82 | -16916.4557 | 43210.4054 | 3569.3317 | 42570.0857 | -1243.4839 | 240026.961 | -5627.8538
324.12 | 9.824 | 1.1788 |  | 204356.278 | -100896.193 | 305324.05 | 4915769.16 | 5478068.16 | -27668.376 | 125306.414 | 18077.332 | 173053.827 | -160708.929 | 1768124.52 | -19775.2942 | 40174.9272 | 4365.2101 | 42689.7754 | -6927.921 | 218026.583 | -5103.1869
324.32 | 9.8197 | 1.1779 |  | 181141.036 | -93843.8177 | 274920.542 | 4895025.02 | 4916744.02 | -22862.9643 | 122967.409 | 9689.9548 | 165450.531 | -19505.5622 | 1838586.7 | -20531.3341 | 44509.8994 | 910.6083 | 41646.8821 | 8957.537 | 240884.801 | -6500.1758
324.52 | 9.8631 | 1.1773 |  | 157009.126 | -90578.7909 | 253524.195 | 4721431.34 | 4357819.19 | -17749.9619 | 112698.55 | 5106.0926 | 157485.99 | 88144.2864 | 1868684.45 | -13445.4843 | 51722.5466 | -3051.011 | 39315.9829 | 29123.6865 | 291614.906 | -5366.6581
324.72 | 9.886 | 1.1749 |  | 137885.4 | -122803.284 | 239772.155 | 5460384.77 | 4158633.22 | -16791.6754 | 121982.093 | -195.9775 | 155686.841 | 92477.547 | 1883170.37 | -13047.8099 | 48624.5501 | -1642.137 | 39121.4749 | 20431.7735 | 269684.917 | -3003.4597
324.92 | 9.8789 | 1.173 |  | 117637.185 | -144464.6 | 225462.501 | 6227959.36 | 3930844.1 | -21031.7512 | 134084.852 | -8146.569 | 153462.827 | 191209.696 | 2047910.19 | -20480.7924 | 51304.2989 | -3374.313 | 39252.643 | 28993.5314 | 279990.604 | -6050.787
325.12 | 9.8954 | 1.1728 |  | 97037.1396 | -183374.71 | 222472.215 | 7058302.84 | 3505715.02 | -31552.6799 | 136738.475 | -18289.8472 | 153657.295 | 307764.239 | 2085499.43 | -22804.2793 | 52947.4762 | -5435.8823 | 39712.0371 | 39936.0066 | 296122.857 | -6479.0329
325.32 | 9.9374 | 1.1728 |  | 61853.9437 | -180047.949 | 219877.793 | 7126373.97 | 2817530.62 | -23594.8288 | 133871.679 | -26964.3239 | 150325.26 | 446355.407 | 2191445.53 | -20445.7971 | 60268.7308 | -9297.251 | 38307.4369 | 58175.6603 | 339672.089 | -7409.1029
325.52 | 9.9342 | 1.1728 |  | 30118.6575 | -208191.334 | 231179.813 | 7709751.37 | 2175899.83 | -29542.1919 | 139099.729 | -37672.257 | 155711.013 | 499006.729 | 2135599.22 | -21587.8573 | 55243.8042 | -8478.2372 | 40054.0459 | 54993.0709 | 313325.948 | -6339.6623
325.72 | 9.9314 | 1.1728 |  | 12916.2894 | -238890.33 | 251093.091 | 8187743.53 | 1715403.38 | -34837.2306 | 132382.596 | -44560.0539 | 159926.523 | 654257.33 | 2100917.51 | -19444.1379 | 57206.9584 | -13183.14 | 40203.7392 | 73538.9073 | 314174.691 | -4970.7946
325.92 | 9.9576 | 1.1728 |  | -20576.3549 | -249258.25 | 262382.973 | 8457186.4 | 1184034.3 | -40814.3373 | 135894.842 | -50530.3017 | 160830.554 | 654748.314 | 2163394.73 | -30464.364 | 58245.6216 | -10817.52 | 40525.4585 | 61785.1213 | 322515.3 | -10037.4059
326.12 | 9.9264 | 1.1728 |  | -31536.0492 | -243828.544 | 291056.527 | 8102630.31 | 909575.814 | -32628.9013 | 129017.602 | -50104.4091 | 167440.542 | 687278.069 | 2062927.23 | -21507.4531 | 55033.6233 | -12633.1518 | 41263.0687 | 75056.7781 | 314805.401 | -6471.9396
326.32 | 9.9219 | 1.1728 |  | -54674.6131 | -245168.78 | 321922.275 | 8037650.78 | 386481.114 | -26179.5939 | 122622.899 | -54852.2757 | 175730.152 | 711960.873 | 1982604.23 | -18664.1781 | 54597.0019 | -12534.6778 | 43012.0506 | 73084.0004 | 316851.116 | -5306.473
326.52 | 9.9448 | 1.1728 |  | -55444.6288 | -252338.13 | 359236.363 | 8155004.63 | 312334.637 | -35852.9202 | 123847.544 | -57187.1937 | 184510.918 | 764040.797 | 1978793.67 | -22719.6956 | 53229.2543 | -13639.9901 | 44634.0406 | 78598.3754 | 305000.516 | -6766.6785
326.72 | 9.9294 | 1.1728 |  | -59465.5628 | -251510.219 | 388524.934 | 8110618.12 | 245637.971 | -36954.4608 | 125308.377 | -57330.4014 | 190792.164 | 749704.768 | 2002421.5 | -23037.8085 | 52327.0959 | -12503.8091 | 45568.713 | 71379.4003 | 293377.466 | -6980.4696
326.92 | 9.9286 | 1.1728 |  | -59124.7575 | -228847.363 | 422043.362 | 7581024.76 | 167511.155 | -30116.7962 | 117474.431 | -54802.8294 | 198235.431 | 759608.494 | 1979596.5 | -23476.5825 | 54808.0553 | -13802.8506 | 46986.2266 | 78860.3461 | 312355.852 | -7255.7466
327.12 | 9.9575 | 1.1728 |  | -52819.9351 | -210613.649 | 450076.441 | 6867108.3 | 183759.972 | -30558.0369 | 101932.526 | -47246.011 | 203159.79 | 683040.207 | 1824228.37 | -21787.6079 | 53928.3166 | -13033.2859 | 47037.193 | 78269.286 | 316633.251 | -7158.5279
327.32 | 9.9594 | 1.1728 |  | -46446.5284 | -180216.544 | 478986.207 | 6049383.01 | 263315.93 | -15399.7247 | 94088.5589 | -40212.5198 | 211241.888 | 594170.747 | 1709385.47 | -11256.6248 | 50356.2346 | -11501.9384 | 48923.09 | 68942.063 | 288778.522 | -2082.4419
327.52 | 9.9546 | 1.1728 |  | -25605.8134 | -178156.626 | 504981.703 | 5968236.64 | 634991.535 | -26568.742 | 96115.8209 | -36011.8844 | 217928.431 | 518880.331 | 1669459.22 | -19128.5962 | 47735.359 | -8948.0526 | 49845.5404 | 57329.3455 | 279876.416 | -5569.3427
327.72 | 9.9543 | 1.1728 |  | 14194.8367 | -190371.59 | 523631.787 | 6206941.41 | 1401612.23 | -33708.5965 | 101480.872 | -29792.5449 | 223219.278 | 431525.878 | 1542637.78 | -22371.3019 | 41837.9136 | -7231.9141 | 51017.3472 | 51011.226 | 254317.105 | -6919.2905
327.92 | 9.9388 | 1.1728 |  | 37599.0583 | -175263.047 | 536618.327 | 5748139.65 | 1814624.22 | -37773.4139 | 97454.5243 | -21157.3988 | 225695.646 | 317606.52 | 1463469.82 | -19948.1027 | 37553.2443 | -4606.1336 | 51180.7511 | 36691.7288 | 218472.534 | -5475.7769
328.12 | 9.9148 | 1.1728 |  | 53095.2286 | -138365.622 | 539141.371 | 4995491.52 | 2033526.29 | -22611.2781 | 91621.6166 | -15149.1115 | 226584.976 | 263443.297 | 1499196.29 | -14575.0459 | 40456.5686 | -3914.4606 | 51855.536 | 31958.7698 | 228780.116 | -4911.311
328.32 | 9.9144 | 1.1728 |  | 92466.355 | -139023.07 | 537784.496 | 5094967.99 | 2839888.27 | -29121.3782 | 98116.0474 | -7518.4899 | 225300.767 | 181261.704 | 1489551.02 | -15297.9262 | 37804.8144 | -2773.2904 | 51005.1578 | 30199.0807 | 223054.606 | -3890.4999
328.52 | 9.8868 | 1.1728 |  | 126197.093 | -145400.277 | 530288.042 | 5513805.16 | 3674468.08 | -31527.0262 | 112133.114 | -2022.1774 | 224462.606 | 101180.769 | 1690277.12 | -19845.0268 | 42594.4625 | -711.0247 | 51544.5789 | 16725.723 | 227529.064 | -6577.9839
328.72 | 9.8497 | 1.1728 |  | 158491.461 | -134425.426 | 506215.558 | 5690474.25 | 4449274.58 | -31934.7976 | 126791.766 | 2359.4982 | 217246.948 | 85029.0032 | 1905632.16 | -23807.1787 | 47121.1804 | -1187.2787 | 50369.868 | 20816.6809 | 248437.026 | -7900.0521
328.92 | 9.8558 | 1.1728 |  | 181595.948 | -121247.422 | 489605.617 | 5481817.56 | 4894891.6 | -27465.7999 | 127476.455 | 7754.4934 | 212870.392 | 45467.7783 | 1945852.46 | -21779.4378 | 48996.1531 | -1334.6409 | 49636.7774 | 24668.8832 | 266448.567 | -6548.4347
329.12 | 9.8835 | 1.1728 |  | 196119.502 | -95812.689 | 461786.508 | 4941886.07 | 5214496.78 | -28253.4241 | 124605.467 | 14892.946 | 204946.635 | -19022.9678 | 1944053.37 | -21917.8863 | 50423.7576 | -906.2215 | 47749.3724 | 23683.9116 | 278567.298 | -6226.8698
329.32 | 9.8668 | 1.1728 |  | 203305.757 | -78398.0279 | 435657.815 | 4374630.73 | 5302912.01 | -25454.3718 | 114119.504 | 21179.5654 | 200085.419 | -128320.882 | 1808348.4 | -19351.4991 | 49616.724 | 1328.362 | 46958.0188 | 15789.6612 | 288337.513 | -4565.7204
329.52 | 9.8376 | 1.1728 |  | 202067.142 | -50782.7124 | 403815.358 | 3616267.35 | 5135306.65 | -29157.3523 | 100985.854 | 24466.6412 | 192033.192 | -119781.189 | 1757686.61 | -18168.1355 | 49790.573 | 469.5051 | 45186.0316 | 19325.1591 | 291449.982 | -5861.9412
329.72 | 9.8458 | 1.1728 |  | 205152.285 | -50986.9745 | 371164.92 | 3489548.5 | 5157014.32 | -29731.3786 | 97400.808 | 25934.2763 | 185602.712 | -168105.64 | 1587830.7 | -15488.4318 | 44382.9574 | 1551.8442 | 44527.7686 | 13814.0145 | 253324.817 | -2553.378
329.92 | 9.8406 | 1.1728 |  | 204070.869 | -54074.6066 | 341129.711 | 3581880.71 | 5194648.78 | -24827.3644 | 98652.0785 | 26021.4144 | 178136.167 | -185761.755 | 1590443.44 | -14193.0178 | 44416.2484 | 2215.9189 | 42479.9654 | 8209.404 | 255974.048 | -3690.8645
330.12 | 9.8128 | 1.1728 |  | 196185.436 | -79973.3106 | 308351.047 | 4241640.31 | 5194527.25 | -32441.8687 | 110820.29 | 21558.0368 | 172218.69 | -188804.126 | 1655223.21 | -22150.475 | 41287.0678 | 4268.3771 | 42227.5861 | -6059.2607 | 231442.086 | -6306.7524
330.32 | 9.7867 | 1.1728 |  | 190700.655 | -106644.431 | 281038.512 | 4822883.67 | 5072835.87 | -38678.6997 | 114355.831 | 16559.8656 | 166255.422 | -126900.978 | 1598080.22 | -25399.2723 | 37524.1917 | 2891.0379 | 41140.2138 | 922.8835 | 210888.429 | -7039.2777
330.52 | 9.7634 | 1.1728 |  | 154328.194 | -85745.9005 | 254155.191 | 4277087.05 | 4228292.66 | -29072.2793 | 102900.332 | 10098.967 | 157900.435 | -21446.0875 | 1635953.35 | -20908.5115 | 43409.6017 | 214.2135 | 39663.0258 | 12922.7035 | 240626.78 | -7549.1479
330.72 | 9.7146 | 1.1728 |  | 123498.071 | -96513.5773 | 232675.925 | 4420275.36 | 3538241.21 | -24276.5076 | 96850.5572 | 1645.1165 | 152131.048 | 55153.9937 | 1575934.71 | -15413.7805 | 44085.5423 | -865.781 | 38017.4367 | 19750.703 | 272638.998 | -5144.9817
330.92 | 9.6838 | 1.1728 |  | 109691.397 | -127122.715 | 218478.824 | 5110021.12 | 3301442.69 | -28852.839 | 103779.986 | -5639.544 | 148707.076 | 160835.588 | 1580440.92 | -16506.5956 | 41487.0468 | -3669.9526 | 37690.2218 | 34141.8201 | 242983.732 | -4680.054
331.12 | 9.6581 | 1.1728 |  | 83693.7099 | -154084.88 | 208410.001 | 5924705.65 | 2905808.61 | -21963.6933 | 114695.028 | -16562.8175 | 145498.138 | 248222.895 | 1724782.79 | -14502.0748 | 42638.0163 | -3561.5622 | 36859.1775 | 26625.1434 | 238017.477 | -4284.5918
331.32 | 9.626 | 1.1728 |  | 56848.2326 | -180846.869 | 202007.554 | 6760193.49 | 2536367.99 | -22803.1471 | 123755.749 | -25739.828 | 143508.234 | 369362.241 | 1941478.15 | -16767.3197 | 49932.8311 | -6020.7641 | 37279.0408 | 35269.6959 | 263395.159 | -6754.3654
331.52 | 9.6042 | 1.1728 |  | 43128.3671 | -223364.546 | 205572.749 | 7786938.75 | 2367256.23 | -34655.3161 | 134024.275 | -34140.1971 | 144100.943 | 476458.767 | 1991043.22 | -24769.0842 | 48463.4719 | -7893.689 | 37146.8143 | 46876.1787 | 266767.364 | -7356.9167
331.72 | 9.5786 | 1.1728 |  | 9312.5635 | -228294.423 | 213800.299 | 7821526.58 | 1628034.09 | -30605.801 | 124793.871 | -40790.4122 | 144307.398 | 581738.48 | 2021735 | -19697.0335 | 53894.1209 | -10867.3996 | 36966.8639 | 62338.7029 | 296914.47 | -5647.0095
331.92 | 9.5903 | 1.1728 |  | -21174.4339 | -214265.84 | 228772.777 | 7571733.48 | 965991.172 | -22861.2241 | 122298.979 | -48494.464 | 145064.278 | 707778.89 | 2110527.62 | -17833.7261 | 58677.8202 | -13943.7231 | 36848.5686 | 79466.4148 | 328977.028 | -6765.1098
332.12 | 9.6014 | 1.1728 |  | -28846.1956 | -257089.609 | 254338.095 | 8380389.7 | 898180.686 | -37788.756 | 129313.784 | -52533.5629 | 152737.475 | 685599.428 | 1996844 | -20394.3404 | 49730.8419 | -11401.5349 | 37901.8911 | 68277.2824 | 285271.486 | -5590.0422
332.32 | 9.5763 | 1.1728 |  | -43587.3768 | -266352.385 | 282190.993 | 8377678.92 | 573715.372 | -36932.5843 | 122226.379 | -53653.3657 | 160325.308 | 693930.279 | 1941075.77 | -18362.7825 | 52056.0948 | -12176.6237 | 39859.6766 | 70255.3709 | 293186.04 | -4897.7783
332.52 | 9.5683 | 1.1728 |  | -62248.8894 | -243374.688 | 307322.922 | 7974757.11 | 115952.355 | -27587.7761 | 115684.176 | -56799.757 | 164302.235 | 797430.569 | 2022181.42 | -19922.7008 | 59374.3734 | -15968.8432 | 39984.3733 | 90762.2337 | 343444.814 | -6860.8184
332.72 | 9.5972 | 1.1728 |  | -48890.9114 | -288706.625 | 344455.64 | 8739330.56 | 340070.344 | -45513.8879 | 121255.851 | -58322.1524 | 174481.852 | 750478.507 | 1847768.55 | -22289.2634 | 48778.4095 | -12992.5529 | 41820.1769 | 74624.4791 | 279220.385 | -5845.8164
332.92 | 9.5853 | 1.1728 |  | -47081.2537 | -282858.98 | 376068.749 | 8506283.31 | 454682.665 | -40467.1878 | 120908.217 | -54072.979 | 181302.827 | 693509.235 | 1796697.49 | -21853.5935 | 45282.9449 | -11622.0084 | 42603.5524 | 67450.5079 | 258946.341 | -6195.5264
333.12 | 9.5464 | 1.1728 |  | -57757.0796 | -253556.881 | 398632.854 | 7753191.77 | 87397.9331 | -29529.3787 | 107940.597 | -52667.937 | 186838.443 | 671644.461 | 1777005.68 | -16933.5628 | 50200.6696 | -11456.7385 | 44257.8178 | 67630.9957 | 290880.642 | -5972.3299
333.32 | 9.5631 | 1.1728 |  | -33937.1836 | -251364.831 | 433416.008 | 7619260.62 | 449842.308 | -33548.7216 | 106461.726 | -48528.0784 | 194216.033 | 690682.967 | 1683355.44 | -18505.8185 | 45940.3653 | -13377.1086 | 44919.1644 | 82092.4505 | 275269.62 | -5597.3288
333.52 | 9.5641 | 1.1728 |  | -23103.5096 | -257595.361 | 457729.388 | 7667980.35 | 758898.855 | -41947.4364 | 106436.336 | -42369.9813 | 199410.599 | 540846.132 | 1658905.99 | -19873.4318 | 46217.6079 | -8856.3028 | 45673.2737 | 56027.3072 | 267447.843 | -5392.8959
333.72 | 9.5352 | 1.1728 |  | -12543.423 | -206101.527 | 474170.085 | 6740326.44 | 1016464.3 | -24945.2009 | 108529.105 | -36252.9972 | 202729.855 | 506536.422 | 1752634.9 | -20836.2511 | 47219.1835 | -8680.7294 | 46671.755 | 56947.4625 | 276003.394 | -8234.1934
333.92 | 9.5686 | 1.1728 |  | 25953.0679 | -204286.872 | 498359.963 | 6662846.64 | 1632810.49 | -19952.3343 | 108483.937 | -32057.2674 | 210374.658 | 468475.456 | 1640322.11 | -10256.3658 | 42102.8556 | -8034.6152 | 48127.4677 | 51702.6221 | 243394.833 | -2023.9451
334.12 | 9.6413 | 1.1728 |  | 47925.4629 | -182431.288 | 510027.799 | 6337696.33 | 2197975.9 | -20745.0896 | 113342.658 | -23793.6417 | 212099.035 | 380954.743 | 1740462.94 | -12743.3565 | 45184.4298 | -6721.7405 | 48213.1071 | 45108.3641 | 246473.365 | -3642.8707
334.32 | 9.6518 | 1.1728 |  | 76791.6445 | -167641.934 | 515853.659 | 6166317.17 | 2822721.57 | -29289.3819 | 115613.345 | -15702.0678 | 214126.279 | 276482.695 | 1848786.17 | -20746.9482 | 48466.1581 | -4114.6266 | 49111.8286 | 33590.7053 | 273234.572 | -7128.8345
334.52 | 9.6625 | 1.1728 |  | 106443.896 | -153382.181 | 517815.145 | 5862076.99 | 3434790.84 | -27924.5743 | 117487.847 | -7009.4228 | 215499.553 | 205963.088 | 1823182.19 | -19965.4747 | 45622.6969 | -3741.2814 | 49193.7676 | 35043.979 | 252419.751 | -5778.694
334.72 | 9.738 | 1.1728 |  | 137445.213 | -127589.019 | 511502.139 | 5241297.85 | 3901174.88 | -28342.4273 | 113207.044 | 618.9083 | 214838.442 | 114407.184 | 1697213.74 | -20018.7218 | 42711.981 | -2463.1686 | 49172.4156 | 30500.2493 | 238749.969 | -5515.3706
334.92 | 9.7832 | 1.1728 |  | 150340.897 | -88771.4842 | 501916.952 | 4141525.91 | 4133322.55 | -24054.1015 | 100722.126 | 12427.274 | 212339.215 | -43969.8637 | 1578600.84 | -14531.542 | 41563.8061 | 784.8128 | 48146.0179 | 15419.1248 | 237343.377 | -3633.9545
335.12 | 9.7415 | 1.1728 |  | 157485.144 | -64566.0998 | 481199.53 | 3385545.11 | 4150489 | -30660.7268 | 85863.4099 | 19353.9223 | 209839.884 | -123907.704 | 1519903.58 | -15614.6738 | 44117.8148 | 2285.5752 | 48472.3146 | 8754.5697 | 267281.752 | -4946.0094
335.32 | 9.7448 | 1.1728 |  | 182207.99 | -49447.3665 | 456165.715 | 3055060.37 | 4487482.82 | -40609.6626 | 83084.9756 | 22861.3163 | 203936.133 | -91481.5873 | 1466800.02 | -21557.2405 | 40524.0343 | 86.8261 | 47384.2537 | 20672.6171 | 235208.857 | -5472.8391
335.52 | 9.7527 | 1.1728 |  | 191547.282 | -52548.9395 | 425035.448 | 3077307.43 | 4721008.09 | -40391.6169 | 86577.1881 | 25698.0951 | 195167.78 | -194341.331 | 1419154.79 | -18320.7692 | 36487.5361 | 3941.347 | 45092.0563 | -3293.6178 | 207549.276 | -4985.63
335.72 | 9.7201 | 1.1728 |  | 212538.107 | -72773.7345 | 397237.933 | 3482270.73 | 5269928.59 | -45065.9183 | 91402.2663 | 31435.1736 | 190655.904 | -292253.923 | 1329265.02 | -20500.0524 | 33542.1485 | 5547.3923 | 44880.6878 | -10123.9808 | 192889.109 | -4854.39
335.92 | 9.7201 | 1.1728 |  | 207858.534 | -56346.0789 | 361356.796 | 3459827.09 | 5292678.59 | -36685.8603 | 104101.082 | 27944.7007 | 182913.464 | -269909.401 | 1494115.19 | -19985.6024 | 35205.3218 | 5878.3065 | 43805.7459 | -14885.6934 | 189982.421 | -6029.2657
336.12 | 9.7406 | 1.1728 |  | 208922.34 | -60652.2839 | 333278.088 | 3731087.67 | 5346675.67 | -26744.69 | 107293.796 | 25103.4606 | 177129.712 | -207662.589 | 1614014.43 | -16473.2054 | 39047.8864 | 4368.9155 | 43053.2635 | -6848.3761 | 213730.002 | -4982.3022
336.32 | 9.7708 | 1.1728 |  | 195623.069 | -67475.2733 | 304377.342 | 4124304.83 | 5212595.59 | -23075.5967 | 113016.019 | 21042.6865 | 170220.357 | -131263.516 | 1791578.56 | -15613.5518 | 46329.8645 | 2074.2075 | 41920.5664 | 881.6807 | 241427.833 | -5020.992
336.52 | 9.7997 | 1.1728 |  | 183137.686 | -88763.6743 | 276489.39 | 4804049.58 | 5021747.59 | -24139.3412 | 119958.728 | 13484.5617 | 163810.673 | -37181.9495 | 1921223.03 | -16764.4177 | 50166.8279 | 106.081 | 41149.3179 | 13550.0148 | 276704.161 | -5631.1362
336.72 | 9.8652 | 1.1728 |  | 177108.899 | -107717.225 | 255535.243 | 5439569.62 | 5008428.25 | -15192.847 | 128181.873 | 8566.9703 | 158174.069 | 47154.0144 | 2018868.34 | -18232.5508 | 52514.578 | -2351.0739 | 39649.587 | 28270.306 | 294047.887 | -5434.1762
336.92 | 9.8976 | 1.1728 |  | 156552.424 | -137197.671 | 240002.701 | 6059758.39 | 4774871.14 | -24999.2351 | 131685.903 | 5299.739 | 155086.722 | 46444.7767 | 2080296.53 | -21678.9935 | 55575.6447 | -1747.5506 | 39129.0295 | 27901.7861 | 317485.172 | -5772.2908
337.12 | 9.9051 | 1.1728 |  | 126378.545 | -159594.735 | 228891.204 | 6513531.71 | 4189974.53 | -31342.616 | 135833.311 | -4807.2251 | 154954.017 | 133016.521 | 2101456.58 | -24608.4745 | 54899.5284 | -2415.6378 | 39683.912 | 28963.2907 | 313071.114 | -7090.5519
337.32 | 9.9268 | 1.1728 |  | 94466.4675 | -161631.366 | 225431.545 | 6398499.22 | 3299576.27 | -27525.0593 | 125018.443 | -15554.5266 | 153952.053 | 312381.274 | 2037592.53 | -20432.9915 | 55406.0097 | -6892.0257 | 39537.0427 | 49598.8888 | 318944.41 | -6898.8155
337.52 | 9.9371 | 1.1728 |  | 54843.0558 | -177058.223 | 225742.689 | 6609799.78 | 2388311.25 | -16536.7398 | 117929.484 | -26418.4009 | 153902.779 | 420143.97 | 1948091.97 | -14847.7712 | 52590.4391 | -8007.6748 | 38992.6532 | 52302.6616 | 302058.57 | -4909.5703
337.72 | 9.9297 | 1.1728 |  | 35135.2549 | -219852.767 | 234697.431 | 7205554.56 | 1927257.46 | -38337.7394 | 113175.09 | -32002.0762 | 156493.865 | 476142.145 | 1784364.53 | -18070.3466 | 47613.6127 | -9077.783 | 39611.903 | 57690.6332 | 273430.172 | -5087.4035
337.92 | 9.9062 | 1.1728 |  | 4426.8338 | -221166.443 | 245721.2 | 7245450.29 | 1331033.19 | -29778.6582 | 112163.874 | -38610.1988 | 157749.786 | 532088.445 | 1764149.18 | -17652.5973 | 46267.7459 | -9318.2088 | 39378.8922 | 57178.9962 | 266157.845 | -5976.0866
338.12 | 9.913 | 1.1728 |  | -14478.244 | -237913.77 | 263689.111 | 7617312.55 | 1049924.18 | -23508.197 | 118929.851 | -44908.5639 | 162989.841 | 557666.584 | 1776786.23 | -12125.7398 | 43920.1044 | -8421.6172 | 40626.9154 | 52024.6184 | 255550.751 | -3013.5945
338.32 | 9.9328 | 1.1728 |  | -20953.8701 | -262287.897 | 290929.016 | 8262224.54 | 1116104.12 | -38018.8145 | 128047.898 | -47071.9641 | 169010.386 | 600220.987 | 1907379.96 | -22401.7837 | 46557.6244 | -9262.3965 | 41642.8553 | 56527.2155 | 271514.428 | -7133.2728
338.52 | 9.9324 | 1.1728 |  | -40819.9793 | -264850.163 | 317963.569 | 8536368.47 | 868111.831 | -35415.6288 | 130231.239 | -50357.521 | 176212.997 | 659892.26 | 2124708.35 | -23105.0074 | 58804.9778 | -11541.4963 | 43622.7572 | 68864.1366 | 342623.278 | -6553.6803
338.72 | 9.9645 | 1.1728 |  | -45883.1748 | -271465.793 | 346336.596 | 8898227.36 | 714171.257 | -42367.2737 | 134344.151 | -56634.5751 | 180874.36 | 803339.186 | 2301388.95 | -27456.878 | 65689.5433 | -15577.624 | 44086.8105 | 89370.9215 | 376912.219 | -9856.2517
338.92 | 10.0225 | 1.1728 |  | -39708.4627 | -301314.25 | 383478.822 | 9615828.44 | 843998.92 | -49568.5466 | 147263.099 | -61714.6848 | 191638.535 | 812844.984 | 2226291.44 | -30840.197 | 55114.6876 | -13668.4112 | 46125.0718 | 77976.9313 | 306266.071 | -8548.1745
339.12 | 10.0507 | 1.1728 |  | -41514.7451 | -285595.211 | 418968.971 | 8906156.44 | 706072.542 | -45435.403 | 134459.934 | -56459.5728 | 199089.124 | 728402.855 | 2046718.49 | -24365.8822 | 51138.948 | -11667.7476 | 47050.593 | 68824.7876 | 288529.375 | -8208.6308
339.32 | 10.0683 | 1.1728 |  | -46775.6315 | -246713.272 | 452983.014 | 7714546.49 | 421642.424 | -25765.1759 | 115178.531 | -50431.5505 | 208082.587 | 660322.433 | 1851090.07 | -14715.0052 | 49220.5452 | -10861.2104 | 48774.8967 | 64114.7672 | 281949.362 | -4412.3502
339.52 | 10.1032 | 1.1728 |  | -31317.284 | -229088.233 | 485196.581 | 7134460.84 | 608981.873 | -24366.4421 | 107922.378 | -44061.8473 | 216558.645 | 582778.065 | 1678718.77 | -14203.9948 | 43254.1752 | -9317.3927 | 50027.9835 | 58077.4447 | 255905.622 | -4156.4596
339.72 | 10.1106 | 1.1728 |  | -9854.118 | -217278.986 | 511571.93 | 6815204.95 | 1031637.64 | -33146.7329 | 107678.362 | -36940.6541 | 223621.357 | 502077.063 | 1641009.62 | -20007.0447 | 39341.1052 | -7329.3673 | 51636.6584 | 45521.9458 | 217157.3 | -5066.522
339.92 | 10.0955 | 1.1728 |  | 7095.3012 | -193193.715 | 530425.554 | 6185219.09 | 1290282.38 | -34002.9367 | 98056.1681 | -28898.1563 | 227294.888 | 419688.943 | 1620174.06 | -20764.6648 | 43040.1541 | -6180.2316 | 52179.8364 | 40315.3208 | 238632.119 | -6832.0896
340.12 | 10.1066 | 1.1728 |  | 36720.2978 | -171796.044 | 542885.922 | 5801246.96 | 1832544.82 | -28855.7412 | 101586.065 | -22585.2251 | 230551.192 | 351334.232 | 1595464.96 | -17661.5232 | 40860.032 | -5218.4299 | 52724.6412 | 38396.29 | 228286.944 | -5684.5591
340.32 | 10.1263 | 1.1728 |  | 66667.47 | -163864.747 | 554834.708 | 5653030.6 | 2475391.61 | -27857.6818 | 103402.111 | -13991.5413 | 233742.217 | 246398.428 | 1572857.52 | -18058.7206 | 39640.555 | -3322.5462 | 53147.8413 | 30606.211 | 224945.252 | -5180.9387
340.52 | 10.1249 | 1.1728 |  | 88699.4364 | -135147.226 | 551965.371 | 5034087.32 | 2905420.42 | -31995.9589 | 99162.9268 | -4999.8471 | 232762.687 | 176439.708 | 1636217.84 | -20147.9606 | 44457.6852 | -3093.4983 | 53333.3866 | 32143.2293 | 256870.898 | -6291.4317
340.72 | 10.1499 | 1.1728 |  | 119445.608 | -102836.059 | 543920.187 | 4506533.75 | 3465456.64 | -26366.0833 | 99907.2084 | 2125.3428 | 230485.918 | 114569.002 | 1686000.66 | -16976.2301 | 45220.7688 | -2252.7117 | 52965.8231 | 27253.856 | 249566.916 | -5288.6671
340.92 | 10.2103 | 1.1728 |  | 161047.007 | -102633.102 | 535457.139 | 4507381.15 | 4420720.73 | -35300.3153 | 106656.163 | 12910.2887 | 228149.596 | -41971.0107 | 1641137.88 | -22519.3059 | 40634.7113 | 1481.8522 | 51820.5338 | 11218.6971 | 231433.651 | -7406.635
341.12 | 10.2292 | 1.1728 |  | 182120.575 | -85873.7977 | 516842.599 | 4079969.01 | 4937899.23 | -34582.2547 | 106579.212 | 22965.043 | 226953.06 | -203892.103 | 1620440.87 | -21199.18 | 39968.2959 | 5341.8405 | 52463.3678 | -8707.2634 | 226442.011 | -6331.5584
341.32 | 10.2407 | 1.1728 |  | 199465.959 | -62679.1663 | 496609.99 | 3554669.81 | 5177826.63 | -39033.6344 | 101556.317 | 27981.4392 | 224706.369 | -217134.759 | 1543362.1 | -22822.4064 | 40292.2969 | 3805.097 | 52472.8645 | 2338.8727 | 235120.545 | -6555.5315
341.52 | 10.2956 | 1.1728 |  | 205973.309 | -59031.0081 | 471054.056 | 3245593.5 | 5144101.77 | -47430.4399 | 90173.7045 | 30794.2044 | 219375.079 | -247588.125 | 1401979.26 | -23944.5 | 38100.4702 | 4170.7535 | 51289.8113 | 2031.4987 | 231791.161 | -6160.9018
341.72 | 10.3014 | 1.1728 |  | 199620.574 | -31185.0434 | 435736.945 | 2654873.93 | 4941030.59 | -41441.601 | 82919.5793 | 31753.084 | 210998.016 | -256683.082 | 1371530.36 | -20316.4462 | 38889.3517 | 4250.7897 | 49727.9392 | -248.7755 | 237957.997 | -4954.6825
341.92 | 10.29 | 1.1728 |  | 200655.774 | -32963.2675 | 404874.154 | 2697692.13 | 4941435.8 | -40835.1223 | 82779.6175 | 30947.9398 | 204058.265 | -250260.868 | 1382472.58 | -20987.9226 | 39961.7989 | 4057.7877 | 48560.7517 | 137.2876 | 238023.76 | -5252.4259
342.12 | 10.3145 | 1.1728 |  | 214531.628 | -54781.803 | 374541.346 | 3375772.53 | 5404613.29 | -42227.4401 | 97464.9918 | 30682.7623 | 196936.526 | -251824.939 | 1451590.53 | -22461.5257 | 37307.7919 | 4199.2716 | 46998.295 | -1162.1192 | 220666.198 | -5174.8986
342.32 | 10.3108 | 1.1728 |  | 201453.552 | -72772.143 | 343974.888 | 3983214.95 | 5424954.79 | -39700.5949 | 109649.165 | 27833.0846 | 190944.953 | -254653.743 | 1696062.96 | -27046.4603 | 41609.9195 | 5975.1604 | 46615.5447 | -14738.1748 | 219227.389 | -7981.4222
342.52 | 10.3025 | 1.1728 |  | 188162.769 | -83504.0484 | 316277.437 | 4314094.5 | 5113184.62 | -39886.6583 | 108226.729 | 21217.8791 | 185235.846 | -132257.975 | 1782931.63 | -25815.4832 | 48062.0123 | 2341.3383 | 46164.0421 | 4488.8948 | 270671.67 | -8511.9151
342.72 | 10.3427 | 1.1728 |  | 167718.797 | -111126.586 | 293380.012 | 5053955.43 | 4732745.14 | -30143.6788 | 116193.561 | 11094.5644 | 179753.265 | -34720.488 | 1766193.27 | -19425.6819 | 45177.5988 | 603.3406 | 44425.2568 | 17116.1861 | 271550.066 | -5294.7613
342.92 | 10.3846 | 1.1728 |  | 140593.492 | -140690.805 | 278139.859 | 5982881.16 | 4344397.42 | -21083.4952 | 130489.86 | -1006.3827 | 177519.523 | 78861.5066 | 1948436.28 | -16672.7307 | 46237.2849 | 143.584 | 44607.7246 | 11474.5914 | 254563.761 | -5814.2553
343.12 | 10.3741 | 1.1728 |  | 116757.016 | -176538.908 | 265484.196 | 7028230.57 | 3955389.79 | -30829.5437 | 144079.667 | -13626.4886 | 175456.846 | 229218.183 | 2129198.1 | -25172.7344 | 50463.5737 | -2711.3951 | 45188.2434 | 21957.797 | 265344.755 | -7463.86
343.32 | 10.4221 | 1.1729 |  | 101029.091 | -200610.398 | 261230.106 | 7663262.67 | 3629827.04 | -32370.7472 | 147720.534 | -22909.3917 | 171696.996 | 392149.522 | 2250238.15 | -25841.3076 | 56134.3987 | -7152.4563 | 43815.4901 | 47067.9238 | 307416.424 | -8278.1811
343.52 | 10.4582 | 1.1737 |  | 62609.277 | -212564.165 | 262294.527 | 7927445.31 | 3050513.04 | -37094.7865 | 149337.443 | -28545.2476 | 170299.084 | 409560.855 | 2329996.88 | -29168.0312 | 59190.4724 | -6094.1252 | 43071.9327 | 40237.1854 | 325577.992 | -10257.9281
343.72 | 10.4502 | 1.1759 |  | 40493.8159 | -240247.265 | 281713.087 | 8174457.68 | 2488921.6 | -34950.5145 | 139218.968 | -33284.8572 | 179711.512 | 469872.389 | 2123543.52 | -20095.735 | 54902.2834 | -8164.6467 | 45756.6036 | 53597.606 | 310658.055 | -4601.7575
343.92 | 10.476 | 1.1797 |  | 5055.9896 | -254381.011 | 301462.765 | 8509569.66 | 1626652.66 | -30680.6823 | 137151.595 | -46754.8894 | 183918.354 | 635986.773 | 2113660.29 | -18066.064 | 54843.7709 | -11158.3163 | 45687.3463 | 66615.1798 | 317873.367 | -4913.5568
344.12 | 10.507 | 1.1826 |  | -17326.6306 | -290505.631 | 322993.925 | 9438043.83 | 1252906.2 | -40792.9973 | 146724.971 | -56626.1387 | 189339.385 | 706073.611 | 2162449.81 | -23866.3819 | 52768.5073 | -10779.2486 | 47001.5129 | 64732.2772 | 309681.166 | -7228.0134
344.32 | 10.4993 | 1.1851 |  | -18585.0059 | -317240.778 | 351869.59 | 9947811.26 | 1259506.55 | -53790.5495 | 149327.184 | -58554.7037 | 194905.389 | 762448.163 | 2220510.79 | -27573.3247 | 55945.6998 | -12850.3369 | 47737.3355 | 74555.2307 | 319604.501 | -7963.4099
344.52 | 10.5336 | 1.1887 |  | -36745.2625 | -304199.432 | 383313.245 | 9703180.53 | 1032829.61 | -49919.8764 | 149164.496 | -58192.6414 | 199993.389 | 758977.476 | 2332229.22 | -28926.1166 | 59715.7734 | -12272.8449 | 48421.6491 | 71380.0949 | 337134.452 | -8989.8168
344.72 | 10.576 | 1.1914 |  | -28608.1 | -304856.26 | 418697.049 | 9484202.73 | 1197563.57 | -54909.426 | 139374.143 | -51208.706 | 208801.541 | 700458.565 | 2224773.65 | -30510.9101 | 61273.864 | -12613.3036 | 49814.4093 | 75976.4715 | 350787.569 | -9815.2885
344.92 | 10.5987 | 1.1935 |  | -37892.8968 | -295644.334 | 462551.046 | 9072517.68 | 914083.208 | -42640.4828 | 134980.931 | -51456.2629 | 222832.095 | 630220.134 | 2029766.77 | -22416.0322 | 53765.1656 | -9873.4435 | 52636.0011 | 62526.6957 | 309050.423 | -6551.1073
345.12 | 10.6239 | 1.1958 |  | -35664.7867 | -275069.25 | 499417.107 | 8504877.71 | 701123 | -42421.1622 | 126125.297 | -52640.164 | 233040.473 | 684676.835 | 1946780.85 | -21721.8062 | 49824.642 | -10788.8332 | 55024.3959 | 63792.677 | 285941.959 | -6685.4324
345.32 | 10.6703 | 1.198 |  | -16377.1411 | -262726.464 | 529420.548 | 8147102.22 | 994528.613 | -41467.733 | 122422.444 | -46988.9297 | 238245.671 | 625195.295 | 1794989.17 | -24055.3676 | 44269.2827 | -9806.6975 | 54966.1644 | 63469.3726 | 268321.559 | -7783.1456
345.52 | 10.6845 | 1.1992 |  | 6562.2384 | -253077.189 | 562226.822 | 7688269.52 | 1431513.58 | -39186.1464 | 117508.293 | -37529.1577 | 246739.038 | 485086.552 | 1706451.54 | -20058.5794 | 40745.9334 | -6439.1316 | 56672.2346 | 44640.0488 | 232919.722 | -5872.5721
345.72 | 10.7165 | 1.2012 |  | 32061.5861 | -225651.915 | 581887.751 | 6964214.23 | 1933309.96 | -40670.9893 | 110001.813 | -25580.0579 | 251940.916 | 367089.494 | 1642134.9 | -19315.6374 | 41373.3835 | -5021.1744 | 57529.7633 | 39571.5033 | 242761.216 | -5917.9038
345.92 | 10.7744 | 1.2028 |  | 58689.6019 | -190173.043 | 599827.959 | 6249859.56 | 2464875.67 | -37232.3504 | 107181.083 | -15676.8533 | 256829.06 | 264222.702 | 1671448.71 | -21385.3774 | 43662.8674 | -3356.6913 | 58830.999 | 31058.3275 | 246447.16 | -7337.4044
346.12 | 10.7926 | 1.1999 |  | 85908.4434 | -165892.586 | 609736.43 | 5762324.65 | 2984317.18 | -35278.3826 | 109289.472 | -8542.5809 | 261212.569 | 162295.005 | 1639291.57 | -22281.0383 | 40520.5182 | -761.455 | 59802.0799 | 18784.314 | 230774.724 | -6865.2226
346.32 | 10.8377 | 1.1952 |  | 115186.914 | -133678.896 | 609238.989 | 5269197.76 | 3472085.54 | -25898.2035 | 112257.957 | -4128.7146 | 262145.483 | 124700.207 | 1679227.74 | -19100.651 | 40900.4543 | -283.6065 | 60295.0115 | 16677.1561 | 231012.829 | -7193.9497
346.52 | 10.8969 | 1.189 |  | 148689.28 | -120799.88 | 603318.301 | 4959592.83 | 4203219.92 | -38787.2992 | 113168.656 | 7426.8266 | 259827.213 | 8536.7551 | 1662582.75 | -29178.1103 | 41332.4415 | 920.8624 | 59242.0897 | 14612.9571 | 239168.82 | -9633.8925
346.72 | 10.9372 | 1.1828 |  | 174755.742 | -98675.2837 | 589391.98 | 4196621.62 | 4711444.21 | -44007.3103 | 101980.34 | 20855.3533 | 257725.037 | -157633.174 | 1553424.34 | -27777.1048 | 40493.6179 | 4096.9914 | 59087.3791 | -820.4506 | 236166.645 | -8757.091
346.92 | 10.9744 | 1.1773 |  | 191051.95 | -57759.2492 | 566332.061 | 3116594.21 | 4961125.4 | -46926.2771 | 88265.3752 | 32226.484 | 254556.683 | -275211.807 | 1439596.67 | -26554.5776 | 37901.7001 | 5873.8363 | 58911.7246 | -8169.5639 | 225035.747 | -7866.9117
347.12 | 11.0171 | 1.1734 |  | 202037.78 | -33386.7095 | 544915.66 | 2462676.91 | 5049248.93 | -42023.1356 | 78126.7802 | 36858.8372 | 252553.908 | -300204.98 | 1396792.27 | -16302.4838 | 38513.9334 | 5686.6963 | 58661.8051 | -6775.514 | 238251.85 | -4259.0271
347.32 | 11.0502 | 1.1727 |  | 216753.07 | -49133.1857 | 514124.316 | 2887892.74 | 5337609.95 | -58251.2798 | 81853.263 | 36828.3584 | 247202.537 | -318220.6 | 1362664.26 | -29786.6673 | 39494.8412 | 6071.6257 | 58146.7317 | -8503.8967 | 236431.64 | -8029.9016
347.52 | 11.0735 | 1.1728 |  | 213274.214 | -44038.0277 | 479096.236 | 2849215.43 | 5250666.26 | -52923.2862 | 85617.382 | 34701.117 | 239806.483 | -281918.873 | 1386071.24 | -26262.1313 | 38019.5028 | 4973.3237 | 57040.8897 | -3371.9145 | 223151.775 | -6491.5846
347.72 | 11.1301 | 1.1728 |  | 211130.437 | -37297.8956 | 442296.155 | 2995191.9 | 5320191.94 | -39765.9051 | 94942.2511 | 31985.0132 | 230374.786 | -248496.545 | 1537625.72 | -22046.8282 | 39415.0878 | 4846.3415 | 55211.2278 | -5723.9796 | 222861.469 | -6396.8078
347.92 | 11.1817 | 1.1728 |  | 220537.333 | -78145.3432 | 418313.935 | 3980454.98 | 5790835.18 | -48702.5949 | 108284.822 | 32296.5814 | 227062.108 | -267017.607 | 1692173.16 | -24223.5421 | 39010.8296 | 6160.0811 | 55134.9805 | -15853.0622 | 200202.422 | -4848.4678
348.12 | 11.2212 | 1.1728 |  | 201961.772 | -89954.198 | 388381.421 | 4638651.42 | 5659703.42 | -40082.303 | 120056.246 | 26196.7272 | 222553.484 | -190020.291 | 1944543.86 | -26737.3392 | 51104.4904 | 3732.7641 | 55442.7072 | -3316.3351 | 270187.499 | -6472.9977
348.32 | 11.2873 | 1.1728 |  | 177278.123 | -119935.125 | 367010.989 | 5654365.4 | 5319333.65 | -30551.3267 | 135692.339 | 13846.224 | 218994.477 | -51915.4782 | 2128105.35 | -26504.9932 | 54602.4242 | 1372.7851 | 54594.7487 | 12913.7095 | 312911.831 | -7901.741
348.52 | 11.331 | 1.1728 |  | 154380.769 | -157673.438 | 356987.675 | 6846228.63 | 4819857.1 | -25444.694 | 150883.588 | -4239.2173 | 218726.469 | 168663.34 | 2340594.58 | -23665.2672 | 58881.2887 | -2546.8093 | 55486.4757 | 27490.6191 | 326320.406 | -6636.0687
348.72 | 11.3653 | 1.1741 |  | 125493.307 | -201143.876 | 341166.163 | 8021039.22 | 4262935.59 | -38394.3389 | 156626.263 | -18018.6709 | 212226.002 | 359325.741 | 2541568.97 | -29778.5789 | 70451.8127 | -7707.0883 | 53974.232 | 52150.174 | 387699.362 | -8332.4175
348.92 | 11.4032 | 1.1991 |  | 95535.1057 | -232204.345 | 337016.17 | 8839834.47 | 3799391.25 | -43548.6928 | 166717.191 | -28549.2403 | 207940.546 | 479694.586 | 2702343.37 | -36881.1705 | 72215.1623 | -8537.7266 | 52288.2029 | 56938.9304 | 406192.166 | -12031.8417
349.12 | 11.4166 | 1.2409 |  | 67982.8872 | -265634.371 | 344600.996 | 9406212.2 | 3411973.26 | -48420.6545 | 169189.528 | -32625.0659 | 210733.64 | 497236.146 | 2625296.72 | -35111.5629 | 67090.5358 | -8315.2667 | 52683.2404 | 56928.0923 | 376470.862 | -10418.2551
349.32 | 11.4287 | 1.2702 |  | 35838.4184 | -280236.158 | 363190.788 | 9698010.99 | 2627602.15 | -38621.3274 | 165068.657 | -44413.2914 | 218492.827 | 604901.679 | 2564846.49 | -24965.5947 | 65960.4905 | -9863.0543 | 54992.591 | 62955.1843 | 373465.826 | -6830.9596
349.52 | 11.4675 | 1.2898 |  | 11606.8433 | -308866.981 | 392200.092 | 10388956.2 | 2104089.31 | -45614.782 | 170775.208 | -56353.4427 | 226345.462 | 761729.442 | 2603236.88 | -27193.2794 | 65288.9083 | -12641.734 | 56364.1881 | 73113.9654 | 365844.708 | -6639.7594
349.72 | 11.4937 | 1.3094 |  | -5794.3926 | -337808.716 | 423636.34 | 11050006.3 | 1804832 | -61789.2656 | 173536.31 | -62621.4112 | 231780.739 | 842750.756 | 2718258.36 | -34239.4859 | 71349.053 | -14225.794 | 57181.2427 | 78650.8618 | 393314.468 | -9658.7539
349.92 | 11.5219 | 1.327 |  | -12541.3619 | -350395.269 | 453031.034 | 11379890.4 | 1787534.25 | -70471.4253 | 178868.479 | -63798.8062 | 237779.34 | 839468.002 | 2740891.94 | -39774.7123 | 71950.8184 | -13955.1574 | 57729.5985 | 84132.7069 | 415240.704 | -11098.6014
350.12 | 11.5503 | 1.3487 |  | -17963.3821 | -329385.45 | 494016.917 | 10898355.5 | 1665402.06 | -67115.3768 | 176162.976 | -62349.9818 | 246542.335 | 853786.237 | 2775308.52 | -41106.3763 | 72963.7999 | -14658.7171 | 59538.2714 | 87240.2382 | 410068.148 | -11646.7735
350.32 | 11.5969 | 1.3837 |  | -18882.6151 | -310446.993 | 538574.313 | 10100516.1 | 1527724.37 | -61041.9375 | 162143.915 | -56311.5333 | 257792.961 | 782414.94 | 2564195.42 | -37839.2973 | 67768.0003 | -13441.6601 | 61026.6013 | 84317.3488 | 387127.264 | -11252.7884
350.52 | 11.638 | 1.4292 |  | -14414.2476 | -284265.709 | 585860.87 | 9184450.54 | 1384304.54 | -38053.7089 | 148493.911 | -52567.1019 | 271942.615 | 703309.78 | 2288426.66 | -19014.3359 | 60506.2248 | -11979.764 | 63609.3429 | 76237.7215 | 349929.048 | -3825.762
350.72 | 11.6636 | 1.4707 |  | -4552.1854 | -270339.249 | 622091.838 | 8820693.93 | 1510652.75 | -47040.5308 | 142995.021 | -47616.8283 | 281506.144 | 649807.646 | 2297130.48 | -29693.7267 | 62207.951 | -10329.6073 | 65970.9182 | 62440.2189 | 336712.42 | -7829.8346
350.92 | 11.6737 | 1.4944 |  | 28666.1117 | -257242.063 | 645212.026 | 8299902.87 | 2110414.66 | -52886.7165 | 134455.575 | -35450.1947 | 286433.546 | 547194.317 | 2114824.14 | -34250.0365 | 57218.5285 | -9456.9008 | 66275.0556 | 66601.6484 | 338564.97 | -9401.5019
351.12 | 11.7116 | 1.4916 |  | 44228.3987 | -196113.121 | 666801.642 | 6821472.17 | 2288030.09 | -36328.0942 | 120986.843 | -24601.6983 | 289103.059 | 419735.134 | 2062513.01 | -24107.533 | 58481.2002 | -7086.8758 | 66064.9399 | 54789.7178 | 343287.922 | -7761.6014
351.32 | 11.7392 | 1.5014 |  | 86555.8715 | -186765.417 | 684355.492 | 6538873.31 | 3171494.65 | -41708.511 | 121651.751 | -12046.5139 | 297176.476 | 247574.883 | 1937690.76 | -25942.517 | 54061.8296 | -3700.7024 | 67990.8304 | 39938.0006 | 322038.879 | -6225.9085
351.52 | 11.7502 | 1.5247 |  | 113922.029 | -157040.692 | 691438.492 | 5866505.41 | 3686498.66 | -46085.2296 | 120238.421 | -2375.2637 | 300043.023 | 143309.215 | 1915836.36 | -31543.9541 | 49628.6928 | -1116.7017 | 68850.7002 | 25634.6649 | 285925.813 | -9164.1107
351.72 | 11.7796 | 1.5461 |  | 142089.795 | -130765.092 | 685795.492 | 5242779.48 | 4160642.79 | -41224.8357 | 115619.721 | 6713.3903 | 300322.857 | 39504.4881 | 1811560.81 | -30633.1188 | 46531.246 | 485.0433 | 69116.1421 | 18837.3885 | 269337.068 | -8154.1047
351.92 | 11.8115 | 1.5971 |  | 163858.651 | -87141.193 | 671313.634 | 4234077.4 | 4486896.27 | -46092.4924 | 107370.415 | 16133.0658 | 296720.467 | -48488.8348 | 1761658.32 | -32160.3502 | 46282.3448 | 1640.5425 | 68536.336 | 13047.3807 | 263988.819 | -9530.9973
352.12 | 11.8528 | 1.6465 |  | 183056.886 | -52395.3983 | 652064.552 | 3270249.4 | 4806601.9 | -46134.7263 | 94355.2606 | 27120.1925 | 292335.628 | -175784.83 | 1651664.86 | -28075.6467 | 46232.7389 | 3736.8897 | 67257.8278 | 5059.3408 | 281303.169 | -8136.4923
352.32 | 11.8921 | 1.6846 |  | 205965.739 | -36852.0684 | 625849.56 | 2805072.13 | 5280196.57 | -51591.0135 | 88186.0898 | 36633.3447 | 288512.822 | -290055.863 | 1597278.89 | -27739.8601 | 45526.9706 | 5785.2527 | 66731.2041 | -4375.8393 | 280513.014 | -7571.6872
352.52 | 11.9093 | 1.7001 |  | 225831.351 | -50637.6578 | 593637.254 | 3071215.74 | 5742699.1 | -62625.5979 | 91860.2315 | 41359.1709 | 285034.591 | -380702.294 | 1466204.01 | -35715.395 | 39779.2863 | 8076.3175 | 66745.4031 | -15664.2839 | 245594.523 | -9552.1436
352.72 | 11.9044 | 1.6786 |  | 221283.844 | -52339.936 | 558756.232 | 3033528.29 | 5484796.38 | -55121.3736 | 88950.4727 | 37246.1004 | 280318.468 | -322794.806 | 1416831.12 | -26574.234 | 37704.2533 | 6615.5889 | 66814.2294 | -10010.2402 | 228313.362 | -7552.9527
352.92 | 11.9398 | 1.6432 |  | 212183.253 | -66541.2284 | 518886.914 | 3506082.71 | 5293157.95 | -50544.9348 | 94921.9872 | 30291.6893 | 270498.232 | -236723.382 | 1467348.12 | -27209.9841 | 36883.5167 | 5167.5757 | 64695.4528 | -4746.7522 | 220509.628 | -8417.0932
353.12 | 11.9247 | 1.6228 |  | 203035.652 | -88423.514 | 484165.832 | 4276592.98 | 5244961.7 | -40330.7379 | 107846.774 | 23332.1181 | 262771.928 | -174203.074 | 1608407.82 | -26148.9359 | 39494.6659 | 4306.0489 | 63634.7714 | -2887.8364 | 224349.415 | -6693.4818
353.32 | 11.9259 | 1.5926 |  | 190557.792 | -126456.501 | 446778.356 | 5476869.99 | 5250865.61 | -43906.9116 | 124737.136 | 15055.9593 | 253177.709 | -74823.4688 | 1900067.57 | -31575.7516 | 47516.3684 | 2582.3215 | 62147.9459 | 4962.4628 | 259223.544 | -10047.7462
353.52 | 11.9602 | 1.5642 |  | 188177.734 | -167978.692 | 421198.608 | 6830768.3 | 5535897.63 | -40634.8915 | 150035.451 | 7658.6628 | 247332.096 | 37469.5154 | 2200484.58 | -31986.0899 | 52133.4549 | 46.6877 | 61499.7666 | 13596.1997 | 263094.302 | -9031.4637
353.72 | 11.9622 | 1.5337 |  | 154822.658 | -215968.679 | 405636.139 | 8307339.54 | 5150552.51 | -38790.9472 | 174323.568 | -8476.3472 | 245626.562 | 146335.901 | 2507619.63 | -31989.1102 | 56617.8409 | 651.3386 | 62050.9467 | 8354.9323 | 289163.057 | -8979.8021
353.92 | 11.9993 | 1.5044 |  | 129893.167 | -248895.188 | 401306.231 | 9385028.93 | 4612716.91 | -39739.1412 | 185777.178 | -25842.7415 | 245759.768 | 426580.146 | 2752552.25 | -35744.4347 | 65554.1413 | -6235.1227 | 63012.7007 | 41117.9779 | 340262.29 | -11251.1406
354.12 | 12.0129 | 1.4852 |  | 70552.4681 | -254002.915 | 395973.487 | 9651951.94 | 3395527.92 | -47936.2237 | 181675.53 | -40629.5433 | 238925.425 | 628851.137 | 2913633.94 | -40851.9177 | 75427.9034 | -10459.3 | 60343.4926 | 64940.3211 | 417452.371 | -13252.2565
354.32 | 11.9993 | 1.4475 |  | 32463.1599 | -273000.681 | 405807.636 | 9701152.62 | 2411582.43 | -57631.58 | 163626.574 | -48593.8409 | 237966.712 | 740596.207 | 2729838.74 | -38571.5907 | 76401.4375 | -13972.6265 | 59210.9081 | 87078.5057 | 446727.74 | -11875.1543
354.52 | 11.9852 | 1.3985 |  | 18512.0478 | -299451.505 | 423400.996 | 10076555.9 | 2126381.34 | -56068.5294 | 161321.563 | -52658.5465 | 241172.69 | 770107.488 | 2565563.85 | -30531.8249 | 69297.7621 | -14525.3951 | 58852.8053 | 91624.4167 | 409160.473 | -5743.7361
354.72 | 11.9707 | 1.3628 |  | -12800.1103 | -291784.047 | 448694.743 | 9904865.98 | 1713604.01 | -55267.4315 | 161234.11 | -53572.0671 | 244396.593 | 757454.469 | 2752607.42 | -35811.5135 | 75448.3888 | -12764.5226 | 59996.8618 | 73481.2882 | 411160.04 | -10047.9401
354.92 | 11.9246 | 1.3791 |  | -14417.6034 | -312221.856 | 484351.486 | 10376623.3 | 1764213.8 | -53457.5743 | 166088.256 | -55451.727 | 256210.194 | 807641.686 | 2770428.75 | -32287.8764 | 78064.0104 | -15776.5558 | 62400.3475 | 95823.1358 | 453720.768 | -6359.1744
355.12 | 11.9248 | 1.4325 |  | -25728.2164 | -332815.514 | 518522.011 | 11188094 | 1514658.64 | -71584.6308 | 182157.882 | -67128.0453 | 263866.265 | 918219.713 | 2925732.7 | -43580.8174 | 77316.8615 | -15624.1554 | 64016.8365 | 91542.1928 | 432198.298 | -11055.7815
355.32 | 11.9258 | 1.4783 |  | -22837.5718 | -346127.642 | 553599.254 | 11493947.1 | 1559246.04 | -80329.2923 | 185983.957 | -69172.9835 | 270861.02 | 974360.85 | 2917453.62 | -47139.0937 | 75725.7201 | -17236.5879 | 65312.7874 | 100036.316 | 422962.257 | -11923.419
355.52 | 11.9234 | 1.5002 |  | -28615.7559 | -315368.823 | 588917.517 | 10546425.2 | 1257106.12 | -73325.1543 | 171322.982 | -65611.0586 | 275400.505 | 876565.505 | 2703089.08 | -47579.1526 | 74140.6691 | -14397.6095 | 64849.3505 | 89394.9904 | 429757.45 | -15753.4513
355.72 | 11.929 | 1.5247 |  | -8888.8598 | -264459.572 | 629822.631 | 8822483.83 | 1403821.84 | -44099.8248 | 144150.581 | -50319.8671 | 285034.175 | 753717.145 | 2330874.37 | -26185.5911 | 63613.2607 | -14332.711 | 66422.2387 | 91628.4649 | 367462.074 | -6587.972
355.92 | 11.9378 | 1.5714 |  | 1561.0797 | -225323.336 | 666138.493 | 7363693.42 | 1478979.38 | -43944.079 | 120781.646 | -35050.8762 | 293450.699 | 502020.384 | 2040536.6 | -28071.7396 | 57044.3125 | -7330.4775 | 66723.2687 | 56811.6413 | 345632.671 | -7794.6884
356.12 | 11.9017 | 1.6215 |  | 31279.3501 | -177936.015 | 688129.265 | 6035311.64 | 1953424.47 | -33930.4641 | 107702.264 | -20191.3981 | 302567.003 | 352136.132 | 1816451.44 | -21991.4299 | 50773.0975 | -5594.7399 | 69665.3949 | 49021.1886 | 308017.609 | -4923.8622
356.32 | 11.8749 | 1.6222 |  | 55092.3582 | -146112.498 | 702257.379 | 5274022.31 | 2206983.94 | -43023.0639 | 98743.5191 | -14167.2931 | 305820.872 | 276920.982 | 1757369.28 | -28699.537 | 49339.9541 | -3244.2151 | 69990.7214 | 34715.1374 | 294926.087 | -9468.9101
356.52 | 11.8475 | 1.574 |  | 91309.4027 | -135553.846 | 703958.902 | 4998798.93 | 2849895.17 | -46304.0504 | 98648.2485 | -5577.4961 | 307518.091 | 189220.14 | 1618449.11 | -29476.0926 | 43998.3727 | -2518.7277 | 70558.602 | 32481.8666 | 259034.98 | -6785.9575
356.72 | 11.8113 | 1.5238 |  | 108486.551 | -93330.7659 | 689773.295 | 4167618.22 | 3153426.57 | -39598.4057 | 94540.8252 | 2229.5264 | 300936.091 | 114397.692 | 1663168.68 | -29183.4228 | 45933.1078 | -1212.1962 | 68914.01 | 25186.1008 | 261143.253 | -9534.7276
356.92 | 11.8047 | 1.4914 |  | 151574.409 | -77967.4492 | 669765.685 | 3918961.45 | 4071478.07 | -43584.6913 | 98527.1684 | 13052.4525 | 295875.782 | -13520.4804 | 1641631.52 | -28400.5716 | 44236.484 | 855.2519 | 68180.895 | 15360.3274 | 249942.19 | -7299.7333
357.12 | 11.8324 | 1.4823 |  | 191980.012 | -63859.8552 | 644760.115 | 3673387.36 | 5101014.34 | -49427.6427 | 104762.442 | 27238.0911 | 288912.105 | -180181.467 | 1718481.93 | -29336.6977 | 45006.5494 | 3922.7356 | 66382.9425 | 2605.5181 | 256628.49 | -8301.4785
357.32 | 11.82 | 1.4878 |  | 212404.215 | -56327.7912 | 621201.749 | 3613147.94 | 5666142.47 | -42296.8151 | 110237.487 | 33906.0558 | 287771.453 | -310309.906 | 1758326.67 | -26357.733 | 45410.4488 | 7637.7894 | 67228.4756 | -17203.1327 | 260852.153 | -8574.0606
357.52 | 11.8419 | 1.4895 |  | 240304.222 | -81365.0042 | 594550.099 | 4175758.44 | 6154775.69 | -53254.9412 | 115883.581 | 34544.7987 | 286284.237 | -285900.242 | 1695949.76 | -30291.3607 | 40726.7483 | 6169.4701 | 67811.8464 | -9356.2937 | 227998.043 | -7791.7919
357.72 | 11.8443 | 1.4998 |  | 224454.238 | -76180.4837 | 555418.23 | 4216607.02 | 5749705.36 | -45849.0783 | 114378.949 | 28402.7817 | 277257.716 | -218926.408 | 1758124.58 | -31276.561 | 45078.8992 | 4992.3027 | 66435.6328 | -5975.5508 | 242847.67 | -9054.854
357.92 | 11.81 | 1.4666 |  | 203737.511 | -67210.6814 | 510603.565 | 4062624.08 | 5226204.29 | -39242.533 | 107262.228 | 22759.2614 | 264455.571 | -98140.8635 | 1849159.59 | -26027.1144 | 52910.1271 | 978.9873 | 64025.8654 | 16105.7465 | 303308.768 | -7752.4022
358.12 | 11.7842 | 1.3928 |  | 194453.729 | -76920.2709 | 470241.205 | 4345712.27 | 5064210.03 | -43380.4611 | 108721.217 | 18809.7522 | 250453.425 | -28009.1125 | 1962401.39 | -28997.4487 | 57884.1719 | -912.3055 | 60250.2277 | 28760.2098 | 343964.751 | -9037.724
358.32 | 11.7474 | 1.3041 |  | 184807.553 | -98848.2582 | 429734.041 | 5031310.77 | 5143330.79 | -39821.488 | 122610.456 | 15541.4658 | 239846.199 | -16564.6722 | 2085767.6 | -29304.7547 | 58010.1429 | -501.1426 | 58456.4615 | 24583.6335 | 333805.068 | -7861.7993
358.52 | 11.7248 | 1.2036 |  | 173634.135 | -132689.232 | 401849.018 | 5917529.38 | 5186478.1 | -41061.8843 | 136105.985 | 10703.0096 | 233103.303 | 14400.9212 | 2189171.74 | -31174.5048 | 58600.4406 | -379.6355 | 57153.7243 | 21690.2529 | 331737.246 | -10085.7996
358.72 | 11.7164 | 1.172 |  | 151950.178 | -183519.913 | 385510.03 | 7232996.25 | 4940422.19 | -36958.5402 | 152945.97 | -902.0191 | 233171.129 | 68148.174 | 2240938.06 | -29925.5991 | 54310.0694 | 847.775 | 58072.4301 | 11852.0496 | 308215.862 | -8889.1263
358.92 | 11.7057 | 1.1715 |  | 116238.33 | -214520.41 | 380751.93 | 8218900.25 | 4205309.11 | -32093.9557 | 164950.172 | -19330.7448 | 235076.756 | 310745.816 | 2444733.08 | -27235.9317 | 58228.4251 | -3808.0264 | 60047.9881 | 28195.5848 | 300400.871 | -8333.9228
359.12 | 11.7202 | 1.1727 |  | 79248.7174 | -260246.802 | 373874.191 | 9340277.39 | 3388163.35 | -51353.1027 | 163720.995 | -34676.468 | 229996.437 | 547033.747 | 2571567.82 | -37011.4902 | 68576.1957 | -9988.5554 | 58122.7789 | 63515.1032 | 385642.12 | -10678.9041
359.32 | 11.716 | 1.1729 |  | 40574.2741 | -269209.681 | 373158.591 | 9678392.68 | 2576349.68 | -48800.0593 | 165376.918 | -47564.0751 | 224504.091 | 696417.497 | 2695075.79 | -35769.8704 | 72827.6734 | -12367.2688 | 56341.3898 | 75753.4726 | 414916.746 | -11510.8602
359.52 | 11.6906 | 1.1728 |  | 27972.1493 | -317960.103 | 398003.404 | 10367819.3 | 2361292.37 | -63377.0954 | 162329.099 | -49418.0545 | 230767.258 | 728691.49 | 2549294.92 | -36025.5984 | 69219.3314 | -14242.4285 | 56918.4155 | 90630.5898 | 401901.046 | -7856.0193
359.72 | 11.6927 | 1.1728 |  | -5422.7438 | -301508.959 | 420139.138 | 9932767.05 | 1695568.01 | -58583.7609 | 152263.101 | -52791.6197 | 232472.377 | 781043.406 | 2625641.74 | -34411.6614 | 75281.6661 | -15025.0154 | 56903.1966 | 89950.6088 | 429623.373 | -9786.8561
359.92 | 11.6511 | 1.1728 |  | -28435.8055 | -298631.417 | 451225.691 | 9815458.63 | 1233869.65 | -55520.3527 | 153812.707 | -58231.1966 | 240955.265 | 817425.2 | 2614308.43 | -34877.6025 | 72296.1233 | -14250.5261 | 58543.0467 | 85315.0828 | 419065.722 | -9324.6821
360.12 | 11.6142 | 1.1728 |  | -33144.1175 | -310265.339 | 486908.116 | 10180012.6 | 1058587.21 | -54085.402 | 160655.513 | -65253.5708 | 250732.802 | 910555.479 | 2581906.87 | -29451.7476 | 68291.8261 | -16511.503 | 60741.6256 | 96106.4732 | 390531.451 | -5694.9238
360.32 | 11.6223 | 1.1728 |  | -39682.6434 | -312077.238 | 516340.888 | 10418014.5 | 1019373.69 | -64873.0746 | 170022.995 | -68438.2576 | 253893.707 | 935018.472 | 2721438.82 | -41203.6966 | 68790.18 | -15238.5612 | 60983.0615 | 87855.5195 | 383156.577 | -11603.6733
360.52 | 11.609 | 1.1728 |  | -33692.9447 | -291017.752 | 549422.254 | 9877752.98 | 1162482.45 | -56986.2326 | 163383.969 | -61781.5084 | 259706.276 | 873248.65 | 2681566.35 | -37149.4398 | 71596.5603 | -15215.163 | 61837.3949 | 89145.6838 | 403767.61 | -10104.3547
360.72 | 11.6227 | 1.1728 |  | -26727.7981 | -256250.673 | 589651.794 | 8781958.69 | 1193001.13 | -52960.0351 | 149059.856 | -52060.0783 | 268476.266 | 744144.749 | 2473516.15 | -39591.7512 | 66892.2712 | -12381.06 | 62937.2607 | 78473.5204 | 381232.268 | -13260.6926
360.92 | 11.6591 | 1.1728 |  | -7635.6747 | -213580.832 | 627696.685 | 7237258.41 | 1336881.81 | -37935.2902 | 122820.262 | -37398.2567 | 279477.684 | 607167.656 | 2125819.75 | -26245.0401 | 61336.1282 | -11922.2655 | 64405.5028 | 83570.9357 | 369778.637 | -5928.0207
361.12 | 11.6532 | 1.1728 |  | -12032.0079 | -168513.496 | 655756.893 | 5816878.27 | 1048847.95 | -32440.7056 | 102397.011 | -28063.8889 | 288017.379 | 393229.199 | 1786533.97 | -26649.7838 | 52343.5257 | -4982.8882 | 65818.6291 | 47960.8393 | 331856.024 | -8508.2665
361.32 | 11.6292 | 1.1728 |  | 24751.7403 | -132794.036 | 674066.047 | 4778772.9 | 1521660.59 | -34484.7615 | 87044.6515 | -17222.8282 | 294160.72 | 364200.233 | 1548398.98 | -22456.4035 | 45777.5662 | -7197.2788 | 67517.2054 | 56689.5087 | 286703.732 | -5140.7354
361.52 | 11.6226 | 1.1728 |  | 55249.7237 | -129344.621 | 680149.166 | 4547659.97 | 1998355.8 | -47014.5382 | 83749.5525 | -10412.3026 | 294568.394 | 186870.908 | 1398886.22 | -28833.3308 | 38643.1954 | -819.1736 | 66957.2055 | 20975.2598 | 237409.585 | -8647.5671
361.72 | 11.5795 | 1.1728 |  | 102673.778 | -108860.741 | 676482.259 | 4015036.36 | 2868982.38 | -51135.589 | 80277.8188 | 2154.478 | 294296.061 | 83734.1591 | 1257237.05 | -27886.8925 | 35314.3834 | -674.473 | 67442.0266 | 22346.6373 | 214947.432 | -7727.4557
361.92 | 11.5668 | 1.1728 |  | 130225.644 | -81621.1773 | 661899.89 | 3587122.57 | 3498075.77 | -45958.536 | 87016.1293 | 10709.5116 | 289542.063 | -47481.1924 | 1320493.79 | -26620.9591 | 33953.1696 | 2738.956 | 65844.9585 | 5891.5532 | 209795.126 | -8272.1256
362.12 | 11.5618 | 1.1728 |  | 176203.47 | -93571.499 | 645714.167 | 3873548.79 | 4573788.98 | -53475.3721 | 92671.2598 | 22163.0374 | 287778.799 | -168942.041 | 1317659.03 | -27254.6846 | 33251.2178 | 4082.073 | 66328.012 | 181.7867 | 195241.759 | -6186.9338
362.32 | 11.5506 | 1.1728 |  | 189911.446 | -59662.5753 | 617836.019 | 3431017.96 | 4895278.74 | -45776.6597 | 95173.3986 | 26742.4508 | 281698.971 | -199728.51 | 1551387.05 | -28150.3879 | 41185.358 | 4677.0089 | 65585.7085 | -4675.6042 | 229028.803 | -7985.9912
362.52 | 11.5597 | 1.1728 |  | 210263.017 | -59304.1425 | 579562.502 | 3629115.63 | 5399359.1 | -44403.0968 | 105694.283 | 29075.7429 | 272715.309 | -213073.254 | 1648314.17 | -26026.5063 | 40063.1249 | 4955.1555 | 64030.3009 | -5646.7681 | 218930.867 | -8414.6341
362.72 | 11.5702 | 1.1728 |  | 224352.54 | -63769.049 | 550316.522 | 3876593.24 | 5702456.65 | -37231.1703 | 113456.928 | 28838.7468 | 267323.619 | -222183.205 | 1697671.44 | -24247.0097 | 41716.5945 | 4991.4589 | 63492.327 | -6322.0073 | 219822.631 | -6816.3776
362.92 | 11.553 | 1.1728 |  | 216403.362 | -57672.4874 | 508647.639 | 3937609.05 | 5685366.13 | -35974.6857 | 118049.218 | 28342.2984 | 255882.907 | -182872.38 | 1945974.26 | -26019.0378 | 49949.1729 | 3711.2702 | 61008.9615 | -606.7502 | 273940.879 | -8531.3254
363.12 | 11.5449 | 1.1728 |  | 216232.841 | -70758.5591 | 473376.747 | 4435105.06 | 5694843.77 | -36796.1973 | 123766.553 | 23269.7567 | 248191.847 | -115870.364 | 2068948.48 | -29533.04 | 54842.1613 | 2141.9786 | 60559.7925 | 7839.652 | 304863.008 | -8446.2443
363.32 | 11.5192 | 1.1728 |  | 201552.097 | -87799.9216 | 434210.053 | 4973598.97 | 5563530.59 | -32395.4136 | 131713.414 | 18969.3134 | 236948.978 | -53769.9831 | 2178601.89 | -29053.3728 | 58043.6917 | 298.1764 | 57598.5502 | 18508.3874 | 322566.064 | -7856.2947
363.52 | 11.4905 | 1.1728 |  | 177879.531 | -107656.594 | 399941.19 | 5493254 | 5128903.06 | -34832.6593 | 134406.446 | 10338.4588 | 228668.81 | 56589.4148 | 2318962.15 | -27834.9458 | 65159.4535 | -2308.4717 | 56965.9908 | 31481.6665 | 366542.608 | -8211.2322
363.72 | 11.4821 | 1.1728 |  | 166666.573 | -146688.542 | 374529.615 | 6674137.21 | 4983966.64 | -36425.5023 | 148836.494 | -1280.0972 | 221429.566 | 195358.683 | 2409338.02 | -30960.4151 | 64025.8563 | -4697.1491 | 54809.7073 | 42611.8144 | 363411.272 | -7994.4496
363.92 | 11.4829 | 1.1728 |  | 143987.882 | -201192.564 | 357674.308 | 7965822.21 | 4756644.29 | -35222.2072 | 161406.092 | -10289.8277 | 217493.793 | 248933.58 | 2488609.64 | -30070.5626 | 64722.379 | -4889.982 | 54342.1907 | 43109.9518 | 366009.354 | -7557.8288
364.12 | 11.4651 | 1.1728 |  | 119805.488 | -232207.863 | 344647.789 | 8851691.05 | 4359497.22 | -39481.9466 | 171565.098 | -21631.2153 | 215310.589 | 366680.337 | 2589395.44 | -33943.5921 | 65056.0238 | -6241.2338 | 54480.6156 | 47912.8393 | 367599.401 | -9481.0012
364.32 | 11.4715 | 1.1728 |  | 77335.6754 | -245585.015 | 348760.611 | 9156786.36 | 3434765.27 | -43901.6878 | 168042.271 | -34900.5888 | 214172.606 | 547181.582 | 2679504.8 | -33793.2465 | 70531.3769 | -9803.1591 | 53980.4375 | 61598.9093 | 392025.177 | -10695.2973
364.52 | 11.4782 | 1.1728 |  | 46951.2628 | -273801.469 | 358517.873 | 9452180.16 | 2795536.67 | -58584.807 | 160207.77 | -39719.5993 | 217618.039 | 578539.52 | 2463966.72 | -41678.5255 | 65758.4845 | -10254.7255 | 54501.884 | 68907.1338 | 382732.199 | -11013.483
364.72 | 11.4281 | 1.1728 |  | -6297.226 | -229937.707 | 376904.282 | 8249621.78 | 1506752.11 | -32427.7278 | 138907.861 | -46553.79 | 217962.666 | 722669.309 | 2489360.2 | -22696.4408 | 72039.9181 | -14660.694 | 53838.789 | 88463.6459 | 418151.379 | -5015.0712
364.92 | 11.4344 | 1.1728 |  | -28568.5591 | -251889.919 | 403530.2 | 8534878.49 | 1027913.28 | -58379.7498 | 133687.746 | -51455.5856 | 223002.6 | 749964.22 | 2402635.93 | -41831.9867 | 69947.3397 | -13302.6491 | 54303.6005 | 86766.9081 | 427699.379 | -13853.3713
365.12 | 11.3966 | 1.1728 |  | -37684.8558 | -257723.497 | 444396.46 | 8286794.69 | 779501.754 | -52611.6201 | 126562.514 | -50278.0552 | 235060.014 | 728773.359 | 2138967.86 | -34934.6436 | 62784.8228 | -13984.8864 | 56462.2772 | 91336.4582 | 378259.892 | -7290.4734
365.32 | 11.36 | 1.1728 |  | -76916.7663 | -214023.068 | 470886.018 | 7293118.88 | -124000.552 | -34485.648 | 112515.902 | -54191.6247 | 238368.289 | 775109.894 | 2183241.11 | -27753.7693 | 66499.3518 | -14225.6531 | 56949.7851 | 84585.8679 | 385970.114 | -8942.2942
365.52 | 11.3676 | 1.1728 |  | -56095.4524 | -242016.291 | 513006.687 | 7641344.73 | 169566.364 | -51831.5585 | 110297.996 | -52592.5446 | 250155.958 | 757401.231 | 1928682.01 | -31754.0846 | 56383.4247 | -13913.8454 | 59133.5687 | 85843.8306 | 340474.196 | -8258.707
365.72 | 11.3418 | 1.1728 |  | -63717.6269 | -226637.705 | 544889.206 | 7268097.4 | 123595.426 | -38521.6038 | 111700.203 | -49340.3488 | 256443.952 | 659324.972 | 1861723.81 | -25442.0255 | 49070.8558 | -10019.7827 | 59731.7702 | 62173.8074 | 283488.68 | -6482.5257
365.92 | 11.302 | 1.1729 |  | -47683.1735 | -216088.221 | 577721.244 | 6910791.26 | 287832.161 | -38598.7497 | 105541.73 | -45974.0312 | 265042.781 | 615317.597 | 1775072.66 | -25903.3393 | 49566.2364 | -9241.7816 | 62034.4109 | 59642.8027 | 300837.494 | -8948.5376
366.12 | 11.3236 | 1.1751 |  | -14212.7035 | -208775.759 | 608214.996 | 6742998.38 | 992345.156 | -39576.0965 | 109143.128 | -36778.2941 | 270543.661 | 544970.852 | 1715349.25 | -25735.0987 | 43727.478 | -8955.7408 | 62002.1448 | 61741.6862 | 259567.672 | -6755.0302
366.32 | 11.3109 | 1.1783 |  | 394.5495 | -187739.096 | 629144.201 | 6291256.71 | 1358467.82 | -38239.0079 | 108904.875 | -28708.7043 | 275654.493 | 390734.879 | 1758816.88 | -28225.8889 | 46021.8513 | -4377.9111 | 63429.5545 | 34695.4834 | 261326.48 | -9162.9359
366.52 | 11.2536 | 1.1846 |  | 34025.3395 | -171547.501 | 644671.69 | 5860774.04 | 1859514.02 | -50566.4913 | 104774.651 | -21753.3744 | 280746.739 | 348759.862 | 1676553.37 | -31802.7407 | 42130.8905 | -4353.4097 | 64817.1215 | 35690.6089 | 236615.813 | -10321.1062
366.72 | 11.2629 | 1.1937 |  | 63025.5831 | -146165.049 | 650284.461 | 5141063.85 | 2206067.09 | -48041.281 | 94572.021 | -14217.1288 | 280683.111 | 275123.522 | 1448786.96 | -28339.6739 | 36515.5811 | -3811.259 | 64206.6005 | 35157.3509 | 211265.016 | -8232.3525
366.92 | 11.2438 | 1.2017 |  | 72837.3602 | -101141.148 | 644217.908 | 3860268.28 | 2287607.64 | -41580.4766 | 75860.6114 | -2460.5578 | 277085.033 | 113369.682 | 1273510.52 | -22179.0229 | 37121.3816 | -681.9205 | 62863.8778 | 21138.8579 | 229446.99 | -6307.8501
367.12 | 11.1928 | 1.2097 |  | 105863.305 | -69994.6219 | 634798.904 | 3152392.83 | 2906283.09 | -36357.4609 | 69320.0105 | 8982.1839 | 275265.758 | 27164.8775 | 1312100.02 | -18594.0388 | 39724.1847 | -365.8072 | 62966.9186 | 21554.9127 | 240372.463 | -5572.6215
367.32 | 11.183 | 1.2132 |  | 148212.572 | -70719.1531 | 617490.673 | 3360304.72 | 3903303.18 | -48311.5551 | 83592.333 | 17336.393 | 270503.583 | -74394.1146 | 1428395.71 | -27922.767 | 41002.8976 | 1634.4388 | 61939.0416 | 12591.8009 | 240570.458 | -7489.0839
367.52 | 11.1644 | 1.2126 |  | 178288.127 | -61833.9578 | 590557.359 | 3337123.41 | 4643231.21 | -48719.5997 | 90135.5225 | 25716.7877 | 264608.513 | -183517.735 | 1501945.01 | -28581.2241 | 42595.6295 | 3759.6153 | 61001.3464 | 2910.5114 | 256916.469 | -8343.6736
367.72 | 11.1236 | 1.2122 |  | 198402.151 | -61557.2219 | 556976.645 | 3529267.62 | 5082446.86 | -43333.4039 | 99056.965 | 27230.242 | 258265.394 | -212829.667 | 1571919.66 | -25401.2894 | 41182.6067 | 4756.0825 | 60393.6921 | -4337.0377 | 234736.97 | -7650.0557
367.92 | 11.1317 | 1.2121 |  | 223908.645 | -73779.0155 | 521533.733 | 4042612.54 | 5625830.78 | -44322.41 | 109393.076 | 27618.9618 | 250023.741 | -196104.853 | 1619972.86 | -27761.1848 | 40343.0021 | 3673.6248 | 59089.2043 | 596.9238 | 220725.156 | -8052.8216
368.12 | 11.1105 | 1.2108 |  | 215478.377 | -70323.4598 | 480313.258 | 4106375.55 | 5625604.36 | -39214.2826 | 114788.174 | 27699.4214 | 238951.874 | -213100.332 | 1795571.79 | -27654.5044 | 46302.4042 | 4454.5314 | 56923.8312 | -4005.7685 | 253024.162 | -8984.3626
368.32 | 11.0611 | 1.2102 |  | 207509.253 | -64513.8846 | 440451.321 | 4175717.05 | 5437788.75 | -31730.6026 | 117185.793 | 22695.0474 | 230115.209 | -135398.274 | 1924087.69 | -25094.1063 | 50472.3927 | 2901.7367 | 56186.221 | 2836.1696 | 282056.076 | -8009.5575
368.52 | 11.0588 | 1.2101 |  | 210144.93 | -90827.895 | 409048.703 | 4696657.7 | 5455677.42 | -33103.5507 | 117650.96 | 19315.5035 | 220327.46 | -62767.3762 | 1918609.27 | -20320.0278 | 52211.3305 | 115.9611 | 53119.3144 | 20995.1385 | 308015.431 | -6299.2146
368.72 | 11.0488 | 1.2086 |  | 197085.38 | -132042.35 | 373717.934 | 5830849.14 | 5501394.16 | -38022.227 | 135301.606 | 13810.9504 | 213220.91 | -78289.8591 | 1995380.65 | -30350.4831 | 50904.4315 | 2100.1197 | 52204.6285 | 10777.5864 | 298947.274 | -7491.7611
368.92 | 10.9942 | 1.2073 |  | 168290.107 | -118590.906 | 343899.078 | 5666510.6 | 4977802.43 | -32742.2185 | 135888.235 | 7869.8581 | 204468.721 | 56359.9818 | 2173786.86 | -29365.5061 | 56578.4798 | -1555.5116 | 51096.4103 | 27592.0894 | 324269.09 | -9112.4937
369.12 | 10.9783 | 1.2077 |  | 132502.11 | -123712.909 | 325648.262 | 5985212.89 | 4161413.1 | -22801.2911 | 135183.707 | -6118.7686 | 199644.338 | 219377.741 | 2286019.81 | -23466.0427 | 61470.4237 | -4271.1988 | 50372.7709 | 37130.7115 | 350324.245 | -6901.9535
369.32 | 10.9795 | 1.2067 |  | 110715.129 | -155775.502 | 312267.511 | 6538614.94 | 3743949.59 | -41408.5968 | 133034.454 | -11697.3642 | 195216.717 | 314909.472 | 2219968.89 | -34516.7565 | 60982.2661 | -7222.5397 | 49234.5162 | 54515.1904 | 342369.929 | -9029.1963
369.52 | 10.9348 | 1.205 |  | 62330.891 | -146855.646 | 304546.913 | 6175890.41 | 2678991.39 | -25167.6754 | 122297.787 | -20576.0863 | 191910.861 | 390889.506 | 2139697.32 | -23592.2145 | 61015.4319 | -8245.7637 | 48134.3367 | 59452.5785 | 355806.499 | -6232.4548
369.72 | 10.9198 | 1.2047 |  | 35381.3996 | -169198.865 | 310054.511 | 6467828.7 | 2074118.49 | -28631.1797 | 116579.258 | -28128.9249 | 193757.254 | 495909.016 | 2049531.26 | -21893.5523 | 59052.3207 | -10775.2655 | 48582.8735 | 72321.4153 | 345722.535 | -3963.9827
369.92 | 10.92 | 1.2038 |  | 10801.8884 | -190299.864 | 320681.293 | 6802407.79 | 1620080.68 | -47507.8799 | 114886.472 | -33367.6002 | 193271.21 | 512066.313 | 2047318.11 | -35301.9554 | 58710.6824 | -8926.9618 | 47601.891 | 58217.4649 | 340493.255 | -11077.6525
370.12 | 10.8544 | 1.203 |  | -17267.7401 | -209611.165 | 341822.565 | 6893084.48 | 1126274.65 | -42082.7123 | 104393.837 | -34427.3501 | 201335.685 | 497912.218 | 1838384.89 | -27572.6353 | 55532.4459 | -9066.508 | 49638.201 | 62869.256 | 335594.243 | -6738.8224
370.32 | 10.8294 | 1.2037 |  | -48661.4574 | -195339.47 | 366642.393 | 6529265.27 | 244872.914 | -30613.6374 | 96663.2949 | -44405.1512 | 206543.114 | 637613.277 | 1811664.43 | -26042.1034 | 55118.6972 | -11584.8433 | 50363.4099 | 71137.6872 | 328050.709 | -9244.8525
370.52 | 10.8187 | 1.2032 |  | -63631.1589 | -216063.095 | 395240.07 | 6862933.43 | -87395.6427 | -35003.9478 | 99335.1385 | -49986.2789 | 212934.924 | 679216.152 | 1668434.02 | -22133.7341 | 46355.2275 | -11705.5667 | 51318.9972 | 69750.1982 | 275123.621 | -5483.6075
370.72 | 10.7745 | 1.2017 |  | -73685.8289 | -229401.903 | 426995.678 | 7086269.47 | -287601.315 | -39960.114 | 102292.82 | -53416.628 | 219373.708 | 668788.723 | 1640744.78 | -26101.0978 | 42757.7269 | -9705.6216 | 52506.3614 | 57628.0365 | 253059.529 | -8113.5063
370.92 | 10.756 | 1.2011 |  | -62405.523 | -234328.793 | 459287.896 | 7093710.55 | -61823.3785 | -39583.6691 | 98808.8752 | -50129.8434 | 225324.524 | 666537.119 | 1589777.89 | -22920.3477 | 43529.8782 | -10920.2587 | 53287.1199 | 64133.3672 | 251533.955 | -8010.8391
371.12 | 10.7645 | 1.2 |  | -48429.4353 | -243679.484 | 498595.881 | 7201575.96 | 264778.206 | -41616.6124 | 100405.155 | -45593.1348 | 234191.847 | 561532.271 | 1546283.19 | -23848.7227 | 40824.1227 | -7496.6339 | 54514.1961 | 46533.9342 | 239975.928 | -8154.5549
371.32 | 10.7249 | 1.1981 |  | -39311.8661 | -229936.021 | 529288.233 | 6849319.72 | 492112.381 | -46180.8214 | 100673.02 | -39818.8072 | 242538.141 | 502379.917 | 1523941.8 | -30731.7054 | 39212.3305 | -6570.1735 | 56426.1887 | 42861.4361 | 223952.961 | -10343.1479
371.52 | 10.7064 | 1.1973 |  | -29019.9909 | -196715.996 | 557243.809 | 6044325.84 | 409936.206 | -38237.8303 | 86423.2788 | -37026.6249 | 249236.729 | 503648.916 | 1389498.54 | -23648.6004 | 39340.9482 | -7809.7165 | 57814.3678 | 52275.4249 | 235700.711 | -7780.2591
371.72 | 10.7112 | 1.1957 |  | -24476.2287 | -158768.239 | 575058.365 | 5154493.82 | 407992.861 | -23246.0735 | 81277.4619 | -32464.3122 | 250320.896 | 464475.004 | 1337822.23 | -17159.1415 | 37874.5148 | -7453.5823 | 56994.6725 | 50478.4085 | 224112.875 | -7436.8886
371.92 | 10.6589 | 1.1936 |  | 9068.9264 | -165679.321 | 591860.089 | 5203410.37 | 1044517.5 | -37670.5774 | 85198.2937 | -25174.3201 | 255120.469 | 329005.236 | 1209036.62 | -22814.0414 | 29020.4511 | -3528.1078 | 58414.4683 | 28897.2006 | 165409.095 | -6366.8225
372.12 | 10.6184 | 1.1937 |  | 39726.5801 | -129726.767 | 594347.076 | 4436561.56 | 1601486.67 | -36507.228 | 80593.2412 | -15077.6536 | 253300.338 | 265472.452 | 1209502.83 | -21267.0938 | 29081.4629 | -3562.218 | 57712.6062 | 30671.5632 | 160657.433 | -7055.8707
372.32 | 10.6083 | 1.1935 |  | 67096.9742 | -112978.596 | 596267.932 | 3931891.22 | 2144417.43 | -36893.7603 | 72213.8634 | -3835.7218 | 252501.308 | 111236.419 | 1197299.3 | -18592.0273 | 33553.6637 | -339.518 | 57154.0038 | 15645.9945 | 198779.171 | -6726.7488
372.52 | 10.5738 | 1.1915 |  | 107325.705 | -106547.727 | 589744.82 | 3889508.62 | 3081554.92 | -44324.5722 | 77639.4905 | 7798.6735 | 251968.111 | -9686.4603 | 1261581.73 | -24993.7203 | 34780.2362 | 1347.897 | 57371.8404 | 10015.5904 | 205797.802 | -7198.0112
372.72 | 10.5354 | 1.1899 |  | 130643.002 | -78632.0802 | 576031.113 | 3594399.37 | 3560243.63 | -43020.9696 | 83624.5262 | 11783.9415 | 249487.225 | -37094.7172 | 1410239.52 | -24706.9312 | 38077.7374 | 1583.3154 | 57511.6284 | 5960.5674 | 197700.336 | -7147.3371
372.92 | 10.5496 | 1.1882 |  | 158671.402 | -59086.3751 | 554698.123 | 3446113.06 | 4138295.64 | -34430.368 | 92115.4366 | 15974.8534 | 243107.578 | -23029.9617 | 1575440.95 | -20119.112 | 42533.6183 | -289.1717 | 56198.3291 | 19107.1861 | 234639.463 | -5825.6652
373.12 | 10.537 | 1.1852 |  | 188998.978 | -84272.0954 | 528436.883 | 4290268.83 | 4965264.83 | -35031.7884 | 109933.938 | 18971.9061 | 236777.387 | -125979.22 | 1678522.7 | -21479.133 | 41695.6308 | 3290.7386 | 54639.2099 | -1740.0685 | 222108.284 | -5958.1065
373.32 | 10.496 | 1.1833 |  | 213900.6 | -99573.9321 | 493530.435 | 4824493.51 | 5521784.57 | -36227.4456 | 122739.34 | 19425.8431 | 230643.541 | -130753.175 | 1779797.58 | -22643.7211 | 41542.3946 | 3632.9657 | 54711.3615 | -4562.7112 | 209391.307 | -6437.1089
373.52 | 10.5079 | 1.1828 |  | 221739.763 | -88530.7056 | 456328.509 | 4732917.09 | 5664665.71 | -30188.6715 | 122140.078 | 20659.2886 | 218943.101 | -104574.278 | 1879450.98 | -23996.9643 | 47493.5621 | 1907.3289 | 51880.6636 | 9290.3694 | 266998.235 | -8124.9554
373.72 | 10.4949 | 1.1811 |  | 219607.671 | -86375.3324 | 420130.161 | 4627672.08 | 5729905.09 | -31348.4441 | 121891.254 | 23582.0611 | 209966.027 | -148990.322 | 1906254.32 | -20941.6125 | 48662.0823 | 2646.9412 | 50273.5062 | 8886.3444 | 279132.505 | -5957.9974
373.92 | 10.4557 | 1.1798 |  | 208890.507 | -84950.1467 | 379965.109 | 4794434.53 | 5547518.55 | -22579.0179 | 126414.484 | 18442.9299 | 201449.917 | -85079.8551 | 2002089.26 | -18634.1212 | 50394.7719 | 1660.0324 | 49055.0682 | 8115.261 | 278736.493 | -5242.4816
374.12 | 10.4458 | 1.1794 |  | 206217.252 | -108250.2 | 350031.438 | 5346287.58 | 5494609.22 | -28474.9613 | 127961.061 | 14846.0349 | 194009.371 | -8638.7454 | 2060944.04 | -21097.8856 | 52910.4221 | -736.7901 | 48057.9703 | 16665.2949 | 280861.106 | -5363.2508
374.32 | 10.4278 | 1.1788 |  | 188369.005 | -118866.916 | 316776.337 | 5811045.92 | 5271149.17 | -20650.4797 | 137004.227 | 8230.3928 | 184325.999 | 65730.9623 | 2224575.97 | -20783.0403 | 58808.2717 | -2654.229 | 46018.1669 | 26238.018 | 316233.253 | -5311.7676
374.52 | 10.4086 | 1.178 |  | 171336.3 | -148393.593 | 290436.105 | 6677779.6 | 5057357.98 | -24851.3037 | 149663.713 | -616.7724 | 178543.682 | 127762.215 | 2298325.91 | -27147.751 | 58160.5969 | -2664.4121 | 44884.4846 | 31893.1021 | 328744.31 | -7538.8398
374.72 | 10.3993 | 1.1769 |  | 147765.322 | -159200.749 | 270669.481 | 6929442.06 | 4586150.45 | -23647.4429 | 149487.813 | -8363.3502 | 173068.176 | 245825.252 | 2312390.87 | -24357.3872 | 59409.2792 | -5659.7209 | 43710.3471 | 46284.4955 | 338923.866 | -6765.9591
374.92 | 10.4144 | 1.1755 |  | 109177.711 | -163443.336 | 259011.947 | 6790475.96 | 3748733.32 | -30043.8454 | 136850.527 | -13822.3586 | 168845.925 | 289682.575 | 2212329.24 | -28632.0797 | 60196.7708 | -5955.6887 | 42711.9026 | 46434.3128 | 344551.139 | -9532.8007
375.12 | 10.4039 | 1.174 |  | 75221.8297 | -158442.357 | 261756.092 | 6160810.4 | 2927984.84 | -22817.4905 | 118884.328 | -15877.9652 | 170557.788 | 324925.694 | 1982851.94 | -18911.3124 | 54822.8915 | -7262.2803 | 43135.2343 | 54513.5956 | 315741.937 | -4080.6426
375.32 | 10.4024 | 1.1731 |  | 33431.6692 | -142438.858 | 264361.967 | 5586450.31 | 1985506.37 | -25938.2018 | 103124.817 | -21131.3958 | 170332.42 | 413852.117 | 1937744.73 | -18480.2157 | 57777.6527 | -9575.3409 | 42644.9569 | 63796.5258 | 337284.642 | -4402.2159
375.52 | 10.4151 | 1.1728 |  | 7731.704 | -162960.563 | 279100.669 | 5896895.71 | 1463932.83 | -29087.2166 | 100617.06 | -27706.7779 | 174448.95 | 455090.477 | 1878803.53 | -22372.469 | 56049.4802 | -9040.4708 | 43209.0375 | 60833.1065 | 337398.428 | -6266.5559
375.72 | 10.3911 | 1.1728 |  | -8469.8096 | -196023.287 | 297604.722 | 6581055.73 | 1216537.6 | -36332.2548 | 107882.826 | -34176.9523 | 180698.955 | 480636.865 | 1772286.76 | -25721.1813 | 48219.1756 | -7992.268 | 44639.358 | 53268.2539 | 289200.363 | -6989.1016
375.92 | 10.3982 | 1.1728 |  | -28492.2444 | -214650.546 | 318700.627 | 6910453.04 | 789340.344 | -38415.2465 | 105485.592 | -40682.3729 | 185879.547 | 540885.569 | 1706583.3 | -25291.2987 | 46377.9441 | -8521.7789 | 45665.1857 | 52229.0976 | 273724.625 | -8820.4442
376.12 | 10.3967 | 1.1728 |  | -52853.4654 | -211798.268 | 348814.552 | 6760635.23 | 244206.794 | -29305.2833 | 104652.971 | -46064.6901 | 193876.148 | 583939.868 | 1650215.85 | -21436.0687 | 42584.7295 | -8632.5534 | 47421.8568 | 51896.5437 | 243961.708 | -6930.9801
376.32 | 10.4041 | 1.1728 |  | -67844.9393 | -208428.63 | 380439.318 | 6508513.52 | -163565.423 | -30692.7164 | 96355.4526 | -47890.5879 | 200076.12 | 627985.507 | 1591748.5 | -23534.0206 | 42320.929 | -9821.2565 | 48065.7843 | 58497.2957 | 250755.973 | -8872.224
376.52 | 10.4091 | 1.1728 |  | -73214.0218 | -206512.423 | 414594.779 | 6340740.46 | -306501.173 | -29905.642 | 91655.3436 | -47237.9655 | 208107.525 | 602366.798 | 1474653.38 | -21474.1776 | 38823.172 | -9080.288 | 49460.8758 | 55095.7505 | 232044.391 | -6957.7333
376.72 | 10.4115 | 1.1728 |  | -69433.9183 | -202803.817 | 450151.75 | 6033922.36 | -311069.001 | -30663.1729 | 81352.5036 | -43379.4978 | 216151.89 | 573064.565 | 1404177.77 | -19269.5353 | 40320.6232 | -9188.695 | 50680.4454 | 56818.0205 | 243032.89 | -6594.8956
376.92 | 10.4267 | 1.1728 |  | -58178.1257 | -206226.599 | 484308.232 | 6070520.32 | -72363.6072 | -28121.346 | 81631.0566 | -40125.9429 | 224737.774 | 525851.786 | 1370273.93 | -17093.087 | 38404.9137 | -7972.8399 | 52149.29 | 50494.9732 | 230284.021 | -6218.9303
377.12 | 10.4377 | 1.1728 |  | -28975.2967 | -213597.325 | 518511.33 | 6278361.6 | 492912.434 | -41474.3652 | 88737.9937 | -36218.3577 | 233558.031 | 478284.354 | 1337995.69 | -24650.5468 | 35122.2353 | -7026.9048 | 54087.5277 | 45972.1316 | 206410.622 | -7160.0479
377.32 | 10.4581 | 1.1728 |  | -14196.7245 | -196623.522 | 545712.479 | 5906195.82 | 811699.136 | -37259.7689 | 86689.9256 | -29730.7902 | 239199.256 | 403727.437 | 1339477.12 | -23644.0593 | 36498.5084 | -5722.8263 | 54753.9891 | 41253.7784 | 216091.069 | -7605.0122
377.52 | 10.4673 | 1.1728 |  | 2771.2268 | -171714.94 | 563193.176 | 5414856.7 | 1058020.63 | -32110.2633 | 85654.2909 | -25223.0605 | 243768.85 | 337677.441 | 1343207.1 | -20674.061 | 36067.2472 | -3934.9934 | 55877.1313 | 30791.4254 | 212483.813 | -7776.078
377.72 | 10.463 | 1.1728 |  | 48052.7433 | -186921.704 | 581703.774 | 5733760.56 | 1964899.89 | -41584.0535 | 94564.6254 | -17175.9556 | 248736.113 | 244793.939 | 1219062.19 | -22995.9013 | 26063.268 | -2547.6004 | 56375.5698 | 27262.0624 | 155304.257 | -6375.8835
377.92 | 10.4599 | 1.1728 |  | 66633.3827 | -166024.484 | 585959.751 | 5489816.42 | 2377947.8 | -34436.6926 | 102985.242 | -13966.3902 | 250999.663 | 199338.479 | 1378335.02 | -19873.6765 | 26920.5551 | -848.6754 | 57877.7122 | 15869.1571 | 139316.152 | -3883.097
378.12 | 10.4562 | 1.1728 |  | 91788.715 | -134114.588 | 579432.422 | 5003150.11 | 2852971.53 | -38836.8167 | 98713.1412 | -6378.3368 | 246457.771 | 168294.299 | 1519958.17 | -26198.9271 | 37587.5958 | -1517.6523 | 56178.0452 | 21817.5149 | 212664.328 | -10555.7285
378.32 | 10.4453 | 1.1728 |  | 118883.521 | -113588.533 | 572129.253 | 4683655.58 | 3493753.13 | -28181.6893 | 102080.321 | 2566.44 | 243861.604 | 66173.2149 | 1597202.84 | -21207.529 | 41470.4435 | -236.7919 | 55705.0912 | 17196.0163 | 236352.672 | -6920.0279
378.52 | 10.4142 | 1.1728 |  | 150088.859 | -99726.0047 | 557096.247 | 4617895.73 | 4209616.09 | -25912.2285 | 110961.041 | 8714.4827 | 241132.916 | 28765.6724 | 1784113.43 | -17860.1117 | 47419.8479 | -762.2239 | 55893.753 | 16984.6604 | 251109.349 | -4765.5029
378.72 | 10.437 | 1.1728 |  | 188041.992 | -102608.46 | 530789.16 | 5060056.26 | 5071620.56 | -33885.1033 | 125739.632 | 12281.2162 | 234202.953 | 239.4872 | 1959690.92 | -25165.4454 | 50238.354 | -162.5381 | 54563.8217 | 18270.0375 | 272696.786 | -7051.5977
378.92 | 10.4459 | 1.1728 |  | 204927.194 | -97363.405 | 506284.785 | 5149255.36 | 5556571.69 | -26011.1065 | 132023.117 | 16809.6163 | 227961.153 | -57644.9943 | 2116795.33 | -19806.9993 | 55145.3797 | 959.9136 | 53505.1629 | 12564.2106 | 297994.245 | -6358.5219
379.12 | 10.4178 | 1.1728 |  | 217027.128 | -101241.34 | 471626.036 | 5531845.6 | 5867629.8 | -22455.3713 | 143063.568 | 15655.1725 | 221207.84 | -68535.4114 | 2185357.88 | -23764.3758 | 54594.3416 | 1909.3695 | 52627.2143 | 6513.753 | 292371.635 | -7896.8659
379.32 | 10.4324 | 1.1728 |  | 230616.098 | -112898.696 | 442667.219 | 5746088.17 | 5922533.9 | -20186.3098 | 138909.785 | 12809.8329 | 216021.823 | 30294.8167 | 2170419.5 | -15990.4002 | 58407.8455 | -2733.7915 | 52174.1196 | 30738.6116 | 319096.156 | -3903.1749
379.52 | 10.4462 | 1.1728 |  | 212043.55 | -92928.4106 | 396235.299 | 5448335.93 | 5649153.51 | -18517.6904 | 141985.136 | 12016.0711 | 200208.513 | 44777.4334 | 2306301.38 | -23533.2591 | 58856.2557 | -1743.8776 | 48042.2203 | 31051.7376 | 333348.281 | -7625.7685
379.72 | 10.3848 | 1.1728 |  | 205967.904 | -94155.4433 | 360410.359 | 5297885.01 | 5513371.1 | -22475.849 | 133968.235 | 13060.977 | 192353.403 | 54648.7881 | 2263803.88 | -18672.264 | 61346.4801 | -3446.7542 | 47339.1935 | 37572.1457 | 345123.773 | -4179.7863
379.92 | 10.3834 | 1.1728 |  | 199843.029 | -99730.7815 | 332013.736 | 5443806.96 | 5379299.96 | -21772.2361 | 134018.405 | 10087.6808 | 184730.332 | 89609.8699 | 2234789.73 | -19303.8709 | 60753.1548 | -4232.6267 | 45470.7434 | 39431.3232 | 336746.378 | -4847.3769
380.12 | 10.3655 | 1.1728 |  | 180859.511 | -129119.802 | 305062.79 | 6042475.86 | 5124633.14 | -20294.5286 | 140390.667 | 4379.4085 | 179920.499 | 75822.3467 | 2195556.7 | -18721.4343 | 56770.9694 | -2179.4149 | 44706.8813 | 29199.0426 | 318155.868 | -3711.855
380.32 | 10.3109 | 1.1728 |  | 157335.828 | -154704.802 | 280491.24 | 6763483.94 | 4677382.29 | -17510.1967 | 147675.932 | -7148.1577 | 176273.437 | 183175.952 | 2226631.89 | -17339.7656 | 56198.919 | -3516.069 | 44598.9244 | 31581.0689 | 310687.201 | -3735.3931
380.52 | 10.3011 | 1.1728 |  | 129736.453 | -160835.91 | 258872.508 | 7049632.93 | 4068040.22 | -22583.0402 | 146530.799 | -16752.3177 | 169415.165 | 380542.617 | 2348280.74 | -21625.488 | 62052.9038 | -9145.0401 | 43818.1129 | 61142.2797 | 347134.939 | -4886.3839
380.72 | 10.3047 | 1.1728 |  | 90768.1295 | -157374.334 | 246386.432 | 6891812.03 | 3298198.47 | -29046.9283 | 137975.941 | -22120.2944 | 159899.847 | 469109.862 | 2452220.32 | -29175.8349 | 69080.3115 | -10973.0853 | 40369.1083 | 71401.5378 | 389435.195 | -9088.4762
380.92 | 10.2628 | 1.1728 |  | 63127.7477 | -166074.21 | 241103.932 | 6889474.68 | 2855346.62 | -30240.1893 | 135683.094 | -24467.9025 | 159711.798 | 457880.763 | 2346475.63 | -28562.2662 | 64783.2109 | -9967.2389 | 40979.8326 | 66128.4695 | 363726.415 | -7674.7177
381.12 | 10.2323 | 1.1728 |  | 38782.9274 | -172552.855 | 252549.56 | 6704362.95 | 2267741.43 | -24591.0292 | 126415.939 | -28509.6336 | 164162.573 | 494023.611 | 2139505.09 | -18131.191 | 61089.4048 | -11469.251 | 41456.1296 | 75642.4069 | 353780.441 | -2203.4154
381.32 | 10.2408 | 1.1728 |  | 2437.9638 | -184022.636 | 261062.76 | 6947004.53 | 1562737.18 | -26160.851 | 126275.886 | -38025.8026 | 165692.663 | 559553.04 | 2124617.88 | -20948.6577 | 60496.1959 | -10928.5784 | 41190.2809 | 72883.4338 | 368555.732 | -6378.12
381.52 | 10.1932 | 1.1728 |  | -13882.0311 | -224409.888 | 282244.873 | 7747854.81 | 1200708.1 | -38627.4847 | 129862.895 | -46313.9723 | 174174.435 | 633146.891 | 2039298.15 | -27455.6885 | 54320.6132 | -11294.3138 | 43848.7563 | 69948.7042 | 317498.632 | -6006.3246
381.72 | 10.1498 | 1.1728 |  | -43024.3078 | -215824.027 | 296206.747 | 7498311.95 | 463840.548 | -32419.2647 | 120546.655 | -53564.084 | 173361.017 | 751995.025 | 2033725.34 | -25466.3426 | 56354.6889 | -13902.1727 | 42907.7962 | 79963.0131 | 328228.815 | -8355.4658
381.92 | 10.1398 | 1.1728 |  | -62523.6352 | -223117.867 | 323833.899 | 7525058.59 | 90413.4757 | -22790.9488 | 115793.931 | -56001.7481 | 179258.773 | 774393.091 | 1980112.07 | -17275.8491 | 54595.9379 | -14209.7639 | 43793.2849 | 80412.7449 | 315188.172 | -4172.4378
382.12 | 10.105 | 1.1728 |  | -61836.1854 | -243419.578 | 353346.848 | 7688663.56 | 79484.4737 | -44662.768 | 108415.708 | -53696.1392 | 184729.604 | 740292.535 | 1929063.13 | -26152.6174 | 57186.0577 | -13596.2432 | 44515.779 | 77832.6595 | 328532.276 | -8318.6685
382.32 | 10.0428 | 1.1728 |  | -69684.3106 | -242261.447 | 387296.17 | 7496412.44 | -55439.7186 | -37240.8629 | 105674.775 | -52112.9074 | 193346.434 | 695723.229 | 1814480.91 | -24565.2304 | 52157.6341 | -12161.8533 | 46311.7205 | 71300.7072 | 295465.224 | -7582.8802
382.52 | 10.0209 | 1.1728 |  | -66759.9663 | -232088.796 | 416759.87 | 7140219.55 | -133499.445 | -35225.8803 | 98913.2015 | -50768.2291 | 199995.388 | 692743.436 | 1685047.64 | -22351.9705 | 48014.0268 | -12455.295 | 47333.8832 | 71828.5901 | 275100.059 | -6567.4533
382.72 | 9.9735 | 1.1728 |  | -68498.8133 | -218089.925 | 446964.558 | 6703605.99 | -296809.588 | -31534.8643 | 92742.8922 | -49844.9163 | 205995.243 | 661785.285 | 1598091.97 | -21136.1992 | 44927.2056 | -10942.4973 | 48070.7881 | 63883.8121 | 260777.029 | -7201.9353
382.92 | 9.8938 | 1.1728 |  | -51879.3389 | -218567.778 | 476286.041 | 6586809.31 | -110227.451 | -28275.0396 | 91973.083 | -48062.4922 | 212959.416 | 613164.888 | 1411764.53 | -18375.0081 | 36582.2024 | -9360.2561 | 49361.2798 | 56082.9919 | 219126.94 | -5927.1629
383.12 | 9.8533 | 1.1728 |  | -29754.0587 | -198216.967 | 494663.291 | 6149768.37 | 260966.262 | -21780.1817 | 91886.6543 | -42718.4253 | 214434.355 | 558982.539 | 1344359.6 | -16799.7844 | 32094.0029 | -8293.0692 | 48997.6986 | 49281.0903 | 182236.268 | -6255.6918
383.32 | 9.8338 | 1.1728 |  | -9193.9781 | -172782.448 | 510209.787 | 5490635.27 | 764963.015 | -25351.0391 | 88784.254 | -31045.3817 | 215968.681 | 411383.32 | 1360624.07 | -16858.5623 | 34190.3638 | -5477.1987 | 49028.9848 | 36210.066 | 191609.457 | -6079.8876
383.52 | 9.7673 | 1.1728 |  | 19553.047 | -151884.448 | 518919.968 | 5062371.37 | 1467705.05 | -31934.8097 | 89074.6157 | -18824.7843 | 218077.28 | 269423.136 | 1366623.02 | -24167.1884 | 34098.7974 | -2957.3657 | 49498.6722 | 26149.9596 | 193115.481 | -7756.6561
383.72 | 9.7337 | 1.1728 |  | 52839.0754 | -138923.019 | 529307.612 | 4732854.08 | 2024542.68 | -33804.1878 | 84610.9703 | -11267.2339 | 221558.475 | 210721.877 | 1325002.01 | -19242.0076 | 34392.6462 | -2839.5011 | 50615.017 | 25878.9885 | 192567.97 | -5314.1993
383.92 | 9.712 | 1.1728 |  | 67297.0821 | -113492.273 | 526627.494 | 4266321.2 | 2259614.82 | -33734.2501 | 82306.7035 | -6260.658 | 219663.121 | 154594.612 | 1360806.79 | -22570.5126 | 36340.9432 | -1680.2344 | 49828.218 | 21848.8235 | 210274.72 | -7255.6312
384.12 | 9.6631 | 1.1728 |  | 86004.7789 | -92225.2606 | 517844.22 | 3805891.73 | 2549887.59 | -32476.1492 | 78046.5994 | -652.6208 | 216908.252 | 120416.669 | 1359451.04 | -20710.288 | 38686.9487 | -2139.0132 | 49395.1351 | 27055.6351 | 231536.573 | -6437.014
384.32 | 9.6086 | 1.1728 |  | 116930.364 | -93327.1985 | 505430.495 | 3891770.3 | 3126082.34 | -32461.0458 | 84258.133 | 3277.8781 | 212896.486 | 52690.9323 | 1274573.29 | -19170.601 | 34658.0362 | -847.4313 | 48273.5181 | 24607.5238 | 224087.438 | -4760.3115
384.52 | 9.5702 | 1.1728 |  | 146005.691 | -83949.1142 | 482386.946 | 3868813.14 | 3782808.48 | -33707.0439 | 92366.313 | 8889.8559 | 206244.831 | 6778.8975 | 1407063.65 | -20344.2131 | 35998.4123 | -154.2183 | 47255.8457 | 15449.336 | 198342.941 | -5410.7464
384.72 | 9.5 | 1.1728 |  | 160021.286 | -64598.1971 | 454484.398 | 3551900.63 | 4151830.43 | -35102.7911 | 93526.4697 | 14823.244 | 197679.812 | -68516.6405 | 1546339.26 | -19813.5623 | 41069.5151 | 1755.9114 | 45577.4979 | 5864.7852 | 233070.412 | -6695.1466
384.92 | 9.4236 | 1.1728 |  | 180970.898 | -61054.8821 | 425925.18 | 3510477.76 | 4596486.79 | -35340.1802 | 94119.0118 | 20021.6805 | 190954.107 | -104822.316 | 1542402.76 | -18063.1951 | 41215.1285 | 1428.9932 | 44544.8236 | 9609.3839 | 233815.328 | -5176.938
385.12 | 9.3582 | 1.1728 |  | 189093.501 | -52976.1691 | 389529.66 | 3588564.24 | 4728213.96 | -30375.8805 | 101709.674 | 17287.5879 | 181559.035 | -85617.6885 | 1600003.4 | -18533.2662 | 40311.7101 | 1707.9405 | 42941.2597 | 6082.199 | 223855.597 | -5159.0882
385.32 | 9.3123 | 1.1728 |  | 199681.676 | -61660.4725 | 355348.709 | 3819487.13 | 5010624.85 | -30528.296 | 103933.98 | 19787.2575 | 171997.948 | -87270.7307 | 1625291.08 | -17327.2746 | 42189.8115 | 333.9105 | 40899.9697 | 14366.1162 | 232486.477 | -4162.45
385.52 | 9.2337 | 1.1728 |  | 190224.584 | -55696.6868 | 316021.677 | 3912865.62 | 4883949.85 | -18742.3565 | 109346.818 | 16310.5036 | 162120.118 | -69552.9358 | 1745572.43 | -13284.7598 | 45077.2699 | 713.1855 | 39505.2406 | 10282.2886 | 244306.788 | -3304.1943
385.72 | 9.2028 | 1.1728 |  | 196065.385 | -66671.5374 | 282989.75 | 4318492.54 | 5058211.81 | -19430.7757 | 115358.791 | 14408.92 | 152133.725 | -4395.3906 | 1821220.68 | -16691.7434 | 47828.9557 | -1889.8005 | 37028.0346 | 27153.4943 | 271169.786 | -5145.3985
385.92 | 9.1585 | 1.1728 |  | 180124.016 | -84963.9778 | 247629.324 | 4734409.77 | 4873996.41 | -20031.7356 | 119396.565 | 11210.5265 | 143181.661 | -39185.2152 | 1860767.67 | -17718.6173 | 47751.4773 | 625.2393 | 35465.925 | 11474.3732 | 264820.083 | -5194.6576
386.12 | 9.0828 | 1.1728 |  | 165707.186 | -83217.9631 | 219876.659 | 4659799.13 | 4496935.57 | -15564.0823 | 115416.427 | 6624.6543 | 136935.508 | 69829.5973 | 1857395.98 | -14133.2416 | 49507.212 | -3387.6308 | 34818.119 | 32352.3848 | 274699.015 | -3878.9937
386.32 | 9.0452 | 1.1728 |  | 146204.781 | -103575.515 | 199447.545 | 5160975.08 | 3978609.67 | -16477.9219 | 119320.521 | -5233.4221 | 132290.357 | 190372.857 | 1792889.03 | -15498.1217 | 45093.9544 | -5028.8433 | 33872.1613 | 35565.2956 | 234471.729 | -3833.9838
386.52 | 8.9953 | 1.1728 |  | 121452.971 | -128603.288 | 181646.882 | 5463059.67 | 3356382.14 | -23199.8496 | 107768.605 | -11089.9636 | 126495.882 | 274593.973 | 1692423.91 | -14872.18 | 44872.0536 | -7168.7502 | 32387.4719 | 47133.8895 | 242818.055 | -3644.9846
386.72 | 8.913 | 1.1728 |  | 82429.7529 | -112677.752 | 159697.822 | 5022061.95 | 2453098.69 | -9175.7775 | 97995.81 | -19211.1198 | 117216.041 | 347033.481 | 1664813.49 | -10433.5973 | 46659.1164 | -7569.7661 | 29905.4527 | 49054.3431 | 270230.764 | -5240.7806
386.92 | 8.8479 | 1.1728 |  | 62599.3653 | -125413.945 | 146908.446 | 5182206.9 | 2243279.05 | -6380.6456 | 101544.678 | -19922.8179 | 113090.501 | 350209.955 | 1607426.62 | -5528.0725 | 41895.924 | -8053.95 | 29124.8755 | 51052.2532 | 226496.397 | 229.7076
387.12 | 8.7971 | 1.1728 |  | 52271.8943 | -151504.086 | 143604.968 | 5763091.34 | 2197052.26 | -14945.8215 | 107245.682 | -23299.0899 | 111486.067 | 333389.007 | 1670193.76 | -11647.9722 | 43222.0453 | -5799.5521 | 28695.0306 | 36142.1029 | 240556.763 | -3576.2369
387.32 | 8.7264 | 1.1728 |  | 34028.7057 | -163895.018 | 141184.048 | 6220769.63 | 2003330.63 | -16687.1533 | 113753.342 | -28437.5778 | 111704.649 | 411879.962 | 1801214.56 | -13661.4749 | 48311.2813 | -8052.6335 | 29325.0924 | 47740.5051 | 267447.474 | -4729.7866
387.52 | 8.6819 | 1.1728 |  | 5757.7473 | -185236.333 | 147613.257 | 6778939.83 | 1379456.88 | -22624.1683 | 117446.045 | -40367.2109 | 112709.162 | 519575.768 | 1828276.01 | -17649.9359 | 49776.7799 | -9338.7013 | 29382.0212 | 56425.5159 | 286340.764 | -6419.905
387.72 | 8.6393 | 1.1728 |  | -17524.5905 | -200481.402 | 155213.856 | 7180844.25 | 874240.348 | -16737.3102 | 117324.382 | -48937.4191 | 114009.438 | 673264.054 | 1849166.66 | -12232.955 | 49145.5589 | -13220.6004 | 29686.5868 | 74740.0812 | 271494.24 | -3632.3418
387.92 | 8.5899 | 1.1728 |  | -47294.4372 | -210729.695 | 167734.718 | 7415301.28 | 194379.237 | -17569.8553 | 114343.697 | -58082.5702 | 114659.454 | 786403.248 | 1927356.58 | -13664.3665 | 54563.1741 | -15200.9928 | 29616.3206 | 82981.3655 | 309600.571 | -5064.2364
388.12 | 8.5508 | 1.1728 |  | -55445.2371 | -221826.449 | 184769.023 | 7644933.69 | 72269.4195 | -23129.2356 | 117368.372 | -60492.6337 | 116193.173 | 851126.309 | 1918347.37 | -17919.4337 | 51753.2582 | -17201.2549 | 29468.3479 | 92589.7561 | 286291.171 | -5588.5122
388.32 | 8.5128 | 1.1728 |  | -64691.9464 | -235181.662 | 208749.235 | 7569232.56 | -92868.89 | -28896.611 | 110811.954 | -58551.0447 | 120506.068 | 766459.925 | 1816834.33 | -18281.4864 | 48051.9187 | -13571.0925 | 29724.4884 | 72309.7203 | 269661.133 | -5690.8708
388.52 | 8.4596 | 1.1728 |  | -72592.301 | -213909.97 | 233317.313 | 6785203.06 | -264368.107 | -21065.9876 | 98517.0888 | -52545.7927 | 126263.643 | 708963.13 | 1673446.69 | -14337.7612 | 46190.7247 | -13274.4263 | 30903.1867 | 72270.5615 | 258462.222 | -4965.4973
388.72 | 8.4134 | 1.1728 |  | -84251.1429 | -204568.449 | 261821.528 | 6280958.45 | -663617.23 | -12353.0396 | 84696.0753 | -52003.6467 | 134114.547 | 674560.891 | 1481188.11 | -9354.6559 | 42662.4494 | -12127.0434 | 32348.5247 | 66211.5541 | 241204.568 | -3420.747
388.92 | 8.342 | 1.1728 |  | -89201.2068 | -208330.113 | 292659 | 6178925.66 | -950645.932 | -12742.4501 | 76540.626 | -53968.1406 | 142242.091 | 725214.251 | 1370011.71 | -7259.156 | 41433.0323 | -14212.2136 | 33940.0468 | 76516.4324 | 237166.689 | -1635.484
389.12 | 8.2983 | 1.1728 |  | -88263.4223 | -220081.06 | 312001.512 | 6542358.33 | -1002589.56 | -18917.3809 | 81697.1095 | -58545.6639 | 144626.949 | 760670.642 | 1365508.85 | -12521.9407 | 37861.997 | -13526.8414 | 33920.3042 | 72834.7762 | 218650.568 | -4973.8474
389.32 | 8.2471 | 1.1728 |  | -67046.4022 | -229065.37 | 333024.854 | 6724438.01 | -511282.114 | -25727.5235 | 86124.1443 | -53189.6025 | 147512.543 | 695161.197 | 1313011.22 | -13410.4147 | 33641.877 | -12310.6271 | 34139.0313 | 68445.5001 | 189156.295 | -4145.6937
389.52 | 8.1803 | 1.1728 |  | -61920.6653 | -208620.375 | 352006.331 | 6153289.19 | -339482.645 | -17921.0414 | 79678.0233 | -45406.319 | 150088.442 | 555296.208 | 1254268.45 | -14331.6164 | 34000.8904 | -8563.2621 | 34071.6202 | 50848.1952 | 205522.138 | -5931.6166
389.72 | 8.1179 | 1.1728 |  | -47915.5447 | -179433.96 | 368686.131 | 5286292.73 | -180888.301 | -16410.4048 | 65754.4423 | -36789.4342 | 154473.416 | 498891.196 | 1152926.09 | -9490.5291 | 35789.0707 | -9255.8953 | 35456.3386 | 56304.4182 | 213470.55 | -3464.592
389.92 | 8.0937 | 1.1728 |  | -39695.352 | -146495.749 | 385460.791 | 4629482.92 | -78943.5696 | -3214.8625 | 62408.2388 | -32957.0443 | 157406.911 | 470317.426 | 1139999.37 | -7573.3869 | 35500.2692 | -9013.907 | 35428.2317 | 55065.295 | 209244.604 | -2745.4335
390.12 | 8.0595 | 1.1728 |  | -18884.218 | -142690.063 | 395460.032 | 4747191.66 | 461173.184 | -13986.8073 | 75438.9807 | -29373.1372 | 159636.464 | 413923.441 | 1219554.77 | -12723.7046 | 31033.5846 | -6820.2915 | 36074.2892 | 40952.4392 | 169652.931 | -3621.7516
390.32 | 8.0115 | 1.1728 |  | 11865.3984 | -146707.315 | 403013.922 | 4979383.63 | 1146085.15 | -23519.1572 | 86595.6331 | -24983.2067 | 160604.748 | 346978.929 | 1268488.6 | -16809.5108 | 29249.8628 | -4870.137 | 36117.3523 | 29877.7507 | 154443.154 | -5155.8151
390.52 | 7.9509 | 1.1728 |  | 33079.1432 | -130799.318 | 405981.654 | 4659823.75 | 1456189.42 | -20679.7124 | 83265.4398 | -20954.8588 | 160802.139 | 292341.244 | 1243116.14 | -14463.698 | 30600.7519 | -3802.9085 | 36249.4087 | 25171.1886 | 168189.324 | -5421.1365
390.72 | 7.9156 | 1.1728 |  | 49645.5031 | -98480.6252 | 402074.06 | 3852394.77 | 1665607.75 | -15193.6883 | 75008.8957 | -13433.5711 | 158337 | 254152.607 | 1208794.98 | -10778.1701 | 31536.0197 | -4703.2301 | 35492.7118 | 33358.561 | 175950.77 | -3519.9037
390.92 | 7.8723 | 1.1728 |  | 63889.803 | -72790.6575 | 396201.208 | 3174113.14 | 1901076.55 | -17106.6031 | 67091.1486 | -5294.7356 | 155692.25 | 163887.146 | 1169463.6 | -9722.8189 | 33195.1812 | -3570.6719 | 34792.0922 | 30712.6235 | 193357.15 | -2872.9588
391.12 | 7.793 | 1.1728 |  | 83860.6895 | -60294.1481 | 382952.795 | 2907199.56 | 2301110.87 | -18935.193 | 65807.0979 | 1014.687 | 152001.703 | 102093.549 | 1187466.95 | -12543.4181 | 35165.2323 | -2874.5583 | 34095.8115 | 28341.9754 | 206962.957 | -3711.4818
391.32 | 7.7291 | 1.1728 |  | 105836.984 | -49578.0786 | 368085.143 | 2688061.6 | 2707664.83 | -29043.4868 | 63996.4245 | 6767.7129 | 147026.754 | 42992.0877 | 1188411.79 | -16392.6664 | 35454.5464 | -1914.1159 | 33177.1995 | 23776.7503 | 196685.339 | -5543.3781
391.52 | 7.655 | 1.1728 |  | 128409.041 | -40927.0707 | 348979.56 | 2460731.08 | 3158455.06 | -28740.7266 | 65987.5737 | 13058.8087 | 142105.399 | -26517.1509 | 1119025.28 | -11729.5454 | 31285.411 | -1226.087 | 32287.8685 | 21595.889 | 173341.378 | -1978.7628
391.72 | 7.598 | 1.1728 |  | 142026.242 | -22597.6666 | 324292.117 | 2239980.2 | 3402778.62 | -21489.3679 | 69226.8815 | 14256.0841 | 135507.152 | -55784.8469 | 1135262.03 | -9624.6236 | 30639.3039 | 7.2277 | 30902.27 | 14658.3067 | 178225.397 | -2253.94
391.92 | 7.5478 | 1.1728 |  | 159769.247 | -29638.3113 | 302970.014 | 2468666.71 | 3815087.44 | -24888.4644 | 76531.1708 | 16209.371 | 129825.834 | -93665.6666 | 1170066.46 | -10074.0308 | 29539.6819 | 1089.2917 | 29782.9396 | 6638.5384 | 164538.828 | -2238.4763
392.12 | 7.4809 | 1.1728 |  | 172442.762 | -37403.0656 | 277102.115 | 2718384.06 | 4167916.9 | -31689.5205 | 81191.0801 | 19028.1042 | 122532.013 | -145539.483 | 1218046.76 | -14810.3204 | 29854.0023 | 2698.392 | 28329.1859 | -1791.3936 | 164249.865 | -4379.5154
392.32 | 7.4232 | 1.1728 |  | 179865.614 | -25573.4377 | 247568.232 | 2520772.5 | 4360830.37 | -28539.2793 | 80562.6751 | 23036.3645 | 115029.871 | -158884.181 | 1246323.69 | -13341.6514 | 30923.1417 | 1756.9411 | 27232.5296 | 4401.5861 | 165013.125 | -3140.6668
392.52 | 7.3932 | 1.1728 |  | 178322.834 | -12367.5072 | 224416.006 | 2136145.9 | 4275771.45 | -25703.1833 | 73736.0204 | 24950.7647 | 108715.409 | -164145.577 | 1206872 | -12266.7407 | 31718.1793 | 1256.2794 | 25733.7728 | 6079.5114 | 173306.31 | -3945.3041
392.72 | 7.3591 | 1.1728 |  | 174102.764 | -11686.8419 | 202176.001 | 1947125.73 | 4086361.5 | -25986.4887 | 66031.8562 | 24545.0005 | 103817.339 | -172315.086 | 1091364.18 | -8259.3803 | 30057.1023 | 1574.1983 | 24989.9572 | 4900.8007 | 169564.462 | -1063.787
392.92 | 7.303 | 1.1728 |  | 156878.163 | 2491.1284 | 173705.841 | 1650090.49 | 3723356.73 | -20476.273 | 63278.7308 | 21948.1739 | 95739.6712 | -148220.714 | 1100053.73 | -8973.2792 | 30369.0638 | 1604.0309 | 23271.2788 | 3261.9533 | 168363.685 | -2841.0759
393.12 | 7.2344 | 1.1728 |  | 155927.324 | -10358.1635 | 150464.851 | 1875612.09 | 3662652.33 | -22748.1601 | 63083.2716 | 19605.1237 | 89628.6471 | -140390.538 | 1005633.44 | -10358.0596 | 26656.5432 | 1641.2439 | 22249.6036 | 3552.7607 | 153736.53 | -2546.9131
393.32 | 7.1798 | 1.1728 |  | 152541.219 | -22046.1874 | 127171.897 | 2063294.22 | 3634605.33 | -23675.8108 | 64137.3162 | 19056.8811 | 82759.3829 | -145529.4 | 968419.086 | -9240.8037 | 25294.6971 | 1608.3859 | 20495.5207 | 3655.1305 | 148174.552 | -1809.5864
393.52 | 7.1166 | 1.1728 |  | 136255 | -28689.1497 | 101899.987 | 2227524.67 | 3425257.23 | -26242.6021 | 66696.0212 | 16853.9467 | 76412.2465 | -135699.499 | 1066344.02 | -9800.0242 | 28142.8938 | 1804.9448 | 19692.3716 | -141.3724 | 152396.716 | -2605.1834
393.72 | 7.0432 | 1.1728 |  | 129127.168 | -39549.5672 | 83408.1539 | 2565574.51 | 3262687.26 | -22442.532 | 69320.6732 | 11188.6126 | 71539.556 | -47702.0973 | 1113217.07 | -10993.6295 | 29389.4858 | -210.0179 | 18748.8821 | 10814.3196 | 166015.049 | -3506.7967
393.92 | 7.0005 | 1.1728 |  | 113352.705 | -58398.2579 | 64075.6068 | 3006799.86 | 2958862.49 | -19180.485 | 72109.8596 | 4608.2026 | 65992.3341 | 18432.0421 | 1112671.96 | -11107.2302 | 27582.7437 | -930.6234 | 17515.3821 | 12587.3812 | 151088.834 | -2913.3996
394.12 | 6.9334 | 1.1728 |  | 85913.5096 | -60795.7401 | 46923.5452 | 3004916.77 | 2378922.29 | -11080.6664 | 67418.3771 | -993.6749 | 61022.8692 | 93470.0565 | 1095914.66 | -6387.3206 | 29437.1363 | -2964.3216 | 16656.5742 | 21938.175 | 158036.524 | -2366.5406
394.32 | 6.8827 | 1.1728 |  | 65635.7686 | -66583.4778 | 35113.5686 | 3117821.61 | 1908071.97 | -7344.4712 | 66374.8976 | -8160.3961 | 57324.1219 | 194069.854 | 1071360.23 | -6182.0227 | 28041.4098 | -4974.0601 | 15965.2746 | 31491.4377 | 151996.999 | -2069.0281
394.52 | 6.842 | 1.1728 |  | 44782.4571 | -82922.3865 | 27413.1887 | 3310787.73 | 1499533.41 | -13040.9775 | 61573.2192 | -11924.3239 | 53376.6667 | 205270.182 | 996825.16 | -9665.3298 | 27128.4008 | -4343.3371 | 14552.0193 | 28075.4937 | 156974.855 | -3423.8958
394.72 | 6.792 | 1.1728 |  | 25430.5572 | -81834.5766 | 22933.5814 | 3133462.64 | 1208543.38 | -5647.2823 | 57730.9155 | -11461.2478 | 51727.7356 | 183376.261 | 954512.533 | -6716.4996 | 26050.148 | -3746.2745 | 14356.7603 | 24488.2478 | 148265.522 | -2677.1799
394.92 | 6.7352 | 1.1728 |  | 10733.7095 | -96639.9629 | 23981.8777 | 3358382.25 | 936197.71 | -7121.2535 | 57658.1796 | -15248.8961 | 52595.1475 | 205790.877 | 912614.247 | -5538.2071 | 23418.1066 | -3428.3724 | 14601.7559 | 21670.7698 | 134937.004 | -1799.5581
395.12 | 6.7097 | 1.1728 |  | -6877.8897 | -110851.413 | 28604.6772 | 3647804.75 | 520452.155 | -8788.7991 | 54714.9623 | -21574.2354 | 53907.5844 | 294622.188 | 917979.662 | -4114.9405 | 26907.2672 | -5846.4404 | 15044.5977 | 34351.0162 | 160172.793 | -2515.8266
395.32 | 6.6621 | 1.1728 |  | -35505.5962 | -118066.222 | 31999.5471 | 4060063.43 | -1554.4447 | 1365.5391 | 61917.3198 | -31657.4794 | 54450.3816 | 393508.098 | 1018346.1 | -5949.5331 | 27688.4426 | -6701.5342 | 15083.9536 | 35076.3063 | 152781.879 | -3137.503
395.52 | 6.593 | 1.1728 |  | -47156.0092 | -145709.769 | 39024.7437 | 4699658.08 | -324342.137 | -775.6512 | 65521.7032 | -40891.5254 | 55649.8435 | 516256.837 | 1017459.21 | -4904.1167 | 26131.084 | -9106.843 | 15434.9652 | 45313.9697 | 142561.441 | -2653.5751
395.72 | 6.5586 | 1.1728 |  | -61599.9442 | -148937.256 | 45606.3313 | 4822265.9 | -657556.757 | 2860.8753 | 65035.7708 | -46336.4734 | 54916.5711 | 610496.162 | 1065040.28 | -3398.8647 | 28920.3478 | -11709.2506 | 14854.2612 | 59657.6227 | 161520.724 | -3224.8387
395.92 | 6.5144 | 1.1728 |  | -72740.5108 | -161403.541 | 55181.7722 | 4983951.92 | -788129.591 | 2849.5541 | 65031.8817 | -46220.494 | 56041.8985 | 581300.014 | 1053985.58 | -3170.4892 | 28481.2271 | -10625.1721 | 14862.7192 | 54079.2978 | 154412.972 | -2388.1025
396.12 | 6.4422 | 1.1728 |  | -76923.6145 | -166181.349 | 69605.6504 | 4963884.94 | -842404.105 | -1984.428 | 61021.6703 | -44802.1622 | 59170.496 | 587544.738 | 1030722.77 | -3781.3977 | 27983.8036 | -11048.9402 | 15447.0326 | 56251.7639 | 153769.206 | -2430.3612
396.32 | 6.3941 | 1.1728 |  | -95992.0631 | -153527.539 | 84772.3239 | 4727523.57 | -1203688.43 | 10271.1835 | 60559.1013 | -47926.5832 | 62530.9154 | 602988.754 | 1035016.95 | -3171.0658 | 28826.139 | -10892.8409 | 16075.1973 | 55246.1556 | 162111.936 | -2560.6753
396.52 | 6.3468 | 1.1728 |  | -100811.171 | -159331.275 | 105219.089 | 4740358.79 | -1419525.44 | 9816.1606 | 57976.9894 | -50991.2988 | 67585.6791 | 663443.771 | 981154.426 | -687.1929 | 27070.4706 | -12736.4691 | 17120.0517 | 64607.4977 | 150064.448 | -1756.1806
396.72 | 6.2977 | 1.1728 |  | -110878.293 | -166057.584 | 124476.635 | 4870954.09 | -1720132.57 | 10791.4929 | 55389.7827 | -55662.3322 | 71540.3967 | 721743.249 | 967524.068 | 738.488 | 27178.442 | -13714.7439 | 17706.6729 | 67444.4855 | 151896.757 | -1031.297
396.92 | 6.2477 | 1.1728 |  | -117040.241 | -167374.847 | 140260.384 | 5000873.34 | -1852835.95 | 13560.4504 | 57373.4027 | -58981.3607 | 73862.8086 | 755767.084 | 1017464.27 | 168.1168 | 29227.5512 | -14027.4409 | 17915.751 | 68769.0343 | 164872.641 | -2229.6773
397.12 | 6.2042 | 1.1728 |  | -105165.722 | -176294.055 | 158668.413 | 5253673.91 | -1515374.98 | 6693.8032 | 64113.7024 | -56609.4406 | 77067.4678 | 734400.316 | 1034418.03 | -1935.3041 | 27935.4705 | -14046.7724 | 18405.4823 | 69929.5879 | 150645.773 | -2246.6371
397.32 | 6.1779 | 1.1728 |  | -93561.3377 | -188705.505 | 179611.427 | 5487710.87 | -1165629.46 | -1140.4344 | 67788.3553 | -52741.7032 | 81336.6914 | 647947.446 | 1023989.73 | -2720.4815 | 26252.4437 | -11331.6689 | 18827.665 | 55735.0635 | 143735.187 | -1977.1386
397.52 | 6.1441 | 1.1728 |  | -86975.8778 | -178789.795 | 198247.634 | 5227799.33 | -960859.597 | -2526.0599 | 66738.1217 | -47422.8725 | 85731.1765 | 586808.113 | 1055557.66 | -5848.2311 | 27547.7972 | -9958.8315 | 19912.5294 | 49332.1473 | 144603.813 | -3661.0099
397.72 | 6.0966 | 1.1728 |  | -85000.6301 | -163718.372 | 218469.133 | 4696178.97 | -1028145.96 | -3349.3592 | 55820.915 | -42909.0279 | 90552.4755 | 558059.26 | 982754.786 | -3969.7591 | 28513.9891 | -10398.3526 | 20809.3508 | 55436.3681 | 159603.089 | -2795.4218
397.92 | 6.0651 | 1.1728 |  | -84449.6721 | -147546.741 | 235407.485 | 4342221.63 | -1204939.83 | 8359.0063 | 49235.3238 | -43880.3071 | 95026.8483 | 577522.672 | 868059.636 | -686.1502 | 25180.7891 | -10961.8061 | 21731.6297 | 56869.1167 | 139792.296 | -1488.8156
398.12 | 6.0372 | 1.1728 |  | -76945.8489 | -147852.302 | 249736.397 | 4300798.45 | -1172770.16 | 5636.1916 | 47515.8926 | -44000.9554 | 97585.0077 | 589931.21 | 798436.507 | 209.6034 | 22996.6171 | -11596.0979 | 21968.6424 | 60876.1568 | 125048.62 | -493.0158
398.32 | 6.002 | 1.1728 |  | -67536.1434 | -148021.207 | 259585.846 | 4322076.37 | -958396.83 | -303.4456 | 50735.7935 | -41780.7634 | 98187.069 | 520044.782 | 798866.936 | -4472.1807 | 22655.9647 | -9131.8788 | 21586.9984 | 50607.3747 | 136416.369 | -3245.0047
398.52 | 5.968 | 1.1728 |  | -40867.2657 | -144419.557 | 267803.744 | 4181162.28 | -293910.7 | -6850.5548 | 56503.2573 | -33021.5548 | 99029.6249 | 400709.188 | 746524.326 | -6946.6998 | 15695.6465 | -6319.9959 | 21523.4802 | 37168.9297 | 94111.694 | -3021.9713
398.72 | 5.9393 | 1.1728 |  | -28635.2803 | -122737.386 | 277832.466 | 3485737.87 | -17193.3013 | -7539.8025 | 48193.0911 | -23002.6383 | 101648.766 | 271326.965 | 682907.058 | -3606.148 | 15526.3327 | -3637.3713 | 22112.3356 | 23121.6678 | 85639.4634 | -1605.3853
398.92 | 5.9285 | 1.1728 |  | -19812.7056 | -101796.649 | 285949.502 | 2931439.86 | 103839.699 | -4072.9118 | 40220.4418 | -17136.7253 | 104605.345 | 222837.189 | 650694.147 | -2467.1677 | 17978.4377 | -3496.0756 | 22932.6211 | 23472.535 | 105993.399 | -1813.9207
399.12 | 5.91 | 1.1728 |  | -2320.9332 | -101144.378 | 295673.713 | 3008962.73 | 364792.202 | -7806.1374 | 42658.8032 | -16352.5813 | 107226.947 | 221217.671 | 636111.45 | -4905.4541 | 16196.6662 | -3536.5083 | 23473.6527 | 22765.0227 | 89906.4284 | -1703.1877
399.32 | 5.869 | 1.1728 |  | 9031.0779 | -96836.7182 | 295558.802 | 3083819.7 | 525414.211 | -9688.2258 | 46057.1505 | -17430.3011 | 106920.103 | 251056.06 | 707324.643 | -5219.5153 | 18772.5286 | -4470.9793 | 23515.1295 | 27015.0387 | 102744.551 | -1487.2172
399.52 | 5.8539 | 1.1728 |  | 23469.7684 | -77994.2704 | 293594.008 | 2783537.02 | 787729.022 | -8454.9283 | 45532.0468 | -13747.3837 | 104223.574 | 245277.98 | 786306.212 | -7827.0663 | 22462.1831 | -5188.0338 | 22477.6783 | 33301.9612 | 128052.144 | -4018.0796
399.72 | 5.8245 | 1.1728 |  | 48107.2039 | -72447.7019 | 289693.359 | 2532581.89 | 1352997.4 | -19304.3591 | 46909.3477 | -4272.6853 | 102283.648 | 93395.1988 | 692236.236 | -8867.6801 | 16823.5149 | -1472.8225 | 21968.4234 | 14772.9303 | 92598.8103 | -2275.9978
399.92 | 5.7784 | 1.1728 |  | 62027.6451 | -40285.1128 | 284740.394 | 1667788.56 | 1638116.56 | -17512.3988 | 39329.8071 | 5582.9896 | 101305.962 | -19404.8051 | 638746.778 | -6873.6077 | 16175.1347 | 612.4901 | 21831.7965 | 4022.8633 | 90116.5303 | -1479.5078
400.12 | 5.7646 | 1.1728 |  | 76530.8495 | -21871.6936 | 278438.839 | 1196490.96 | 1889072.61 | -23324.3375 | 32899.3757 | 11624.6912 | 100482.971 | -63168.3195 | 653842.569 | -5286.0845 | 19542.0114 | 706.2383 | 21991.2539 | 3889.7614 | 108833.31 | -1710.7638
400.32 | 5.743 | 1.1728 |  | 99039.9861 | -29958.6965 | 269254.36 | 1668319.72 | 2422304.1 | -28378.7238 | 46703.3172 | 12512.8947 | 98441.1487 | -94685.4501 | 722268.1 | -10249.2944 | 17212.242 | 2016.6334 | 21494.9987 | -5240.9965 | 79790.84 | -2348.9739
400.52 | 5.7027 | 1.1728 |  | 118650.785 | -40959.4008 | 259345.008 | 2083534.91 | 2831877.82 | -28772.6378 | 53926.3178 | 13158.9951 | 96012.5424 | -98609.5144 | 766435.769 | -11760.2461 | 17710.9386 | 1721.9124 | 21204.7587 | -2236.6041 | 87182.72 | -2480.3085
400.72 | 5.6744 | 1.1728 |  | 122064.354 | -16988.8515 | 241122.67 | 1694921.37 | 2832854.14 | -26899.294 | 51085.0076 | 14345.0723 | 90604.5616 | -74498.1437 | 859573.396 | -8892.4754 | 24252.4462 | -67.2982 | 20135.9051 | 10713.0122 | 137179.151 | -3405.2131
400.92 | 5.6734 | 1.1728 |  | 135195.274 | -10597.164 | 227404.996 | 1501355.97 | 3098749.58 | -26020.5486 | 51754.1726 | 18171.3627 | 86430.2176 | -125592.727 | 798636.656 | -8051.2431 | 20808.3698 | 923.5983 | 19082.4071 | 5334.5473 | 108334.027 | -2452.499
401.12 | 5.6708 | 1.1728 |  | 148522.658 | -7197.8992 | 214703.643 | 1264762.06 | 3401930.71 | -36521.2701 | 49120.3329 | 24611.4206 | 83489.1619 | -221317.372 | 691303.813 | -9073.5593 | 16366.7461 | 3149.9621 | 18541.1117 | -6720.2912 | 81246.0707 | -489.0627
401.32 | 5.6531 | 1.1728 |  | 145926.007 | 23072.724 | 198592.873 | 581822.408 | 3325900.95 | -27292.4195 | 40817.0002 | 28451.1484 | 80161.6316 | -250275.957 | 737266.33 | -6311.3005 | 21385.9798 | 3321.1547 | 18168.1545 | -5358.6139 | 122070.309 | -1774.7507
401.52 | 5.645 | 1.1728 |  | 153373.548 | 18948.427 | 185016.576 | 700826.288 | 3481362.13 | -29523.0092 | 44894.8775 | 28543.4519 | 77245.3926 | -261186.351 | 725552.496 | -7408.6748 | 19129.7207 | 3806.7137 | 17653.7473 | -8966.7502 | 101602.998 | -1552.0959
401.72 | 5.6383 | 1.1728 |  | 167703.513 | 1809.1677 | 169580.178 | 1119841.89 | 3767425.23 | -34803.4199 | 50004.3399 | 28491.7633 | 73625.1251 | -256287.509 | 694741.864 | -10053.0061 | 16058.0427 | 3455.1148 | 16910.5812 | -7569.415 | 80170.187 | -1029.5126
401.92 | 5.6099 | 1.1728 |  | 154002.584 | 23401.552 | 148008.268 | 735818.463 | 3449082.38 | -26425.3931 | 44826.4486 | 26803.1006 | 67696.6995 | -230042.532 | 787504.345 | -10102.1725 | 22437.4804 | 2956.6452 | 15680.771 | -4726.3408 | 125120.863 | -3939.5309
402.12 | 5.5837 | 1.1728 |  | 157378.62 | 19383.4045 | 127061.319 | 722297.812 | 3462954.95 | -29368.4439 | 43414.0566 | 26926.1042 | 62300.6204 | -231855.911 | 680166.504 | -9145.8006 | 17274.2641 | 2968.6395 | 14784.6215 | -5653.2256 | 92049.5404 | -2597.9161
402.32 | 5.5781 | 1.1728 |  | 164705.72 | 16294.0553 | 111245.967 | 575417.438 | 3556345.61 | -32618.5143 | 39226.8915 | 29712.7643 | 58019.6331 | -273647.341 | 527187.187 | -7606.7307 | 12210.5015 | 3572.2337 | 13814.8624 | -8163.5833 | 66674.3881 | -313.9169
402.52 | 5.5634 | 1.1728 |  | 152583.678 | 31799.7629 | 91288.6326 | 166884.785 | 3379874.61 | -30436.4193 | 33374.2912 | 31983.5352 | 53439.5448 | -310611.288 | 593183.568 | -5352.3093 | 17392.3278 | 4594.9441 | 13122.2762 | -13313.8888 | 98560.5378 | -909.7873
402.72 | 5.5228 | 1.1728 |  | 149306.67 | 26853.1517 | 68280.0527 | 410498.306 | 3444195.77 | -30745.4015 | 39061.7663 | 31536.6858 | 47957.9919 | -312723.287 | 661730.614 | -9360.7379 | 18467.9984 | 4755.5186 | 12159.535 | -13284.1814 | 104594.356 | -2024.7841
402.92 | 5.4967 | 1.1728 |  | 155270.798 | 6117.0156 | 54254.5236 | 948512.749 | 3549097.7 | -34042.6868 | 44870.6768 | 27790.3873 | 44707.184 | -263744.64 | 685235.253 | -10774.4203 | 17901.6153 | 3702.8965 | 11627.8036 | -8548.3372 | 102946.38 | -1939.7825
403.12 | 5.4857 | 1.1728 |  | 141734.89 | -477.6564 | 30811.3891 | 1199056.87 | 3384470.62 | -31149.6624 | 48816.1395 | 24458.0785 | 38454.5593 | -226366.861 | 762558.176 | -10133.5747 | 19824.9078 | 3059.4182 | 10338.7417 | -7594.664 | 106045.564 | -1962.2891
403.32 | 5.46 | 1.1728 |  | 129471.689 | -1219.3348 | 15620.7669 | 1312168.85 | 3119634.19 | -21370.1361 | 50726.7188 | 19615.1228 | 34652.0414 | -179825.423 | 796672.877 | -10343.4795 | 20293.4362 | 2655.1746 | 9663.3376 | -6993.4865 | 109861.717 | -2757.6322
403.52 | 5.4477 | 1.1728 |  | 123623.574 | -16502.1748 | 1183.305 | 1510925.31 | 2964552.23 | -28870.955 | 50253.6511 | 16544.4573 | 30566.9053 | -152489.803 | 721597.869 | -10101.1188 | 16746.2751 | 2416.2002 | 8755.4023 | -7355.9159 | 87666.7838 | -2543.0594
403.72 | 5.4274 | 1.1728 |  | 104909.39 | -12852.6276 | -11387.8177 | 1276077.64 | 2577556.34 | -22316.8242 | 43979.6151 | 15177.0184 | 27270.4774 | -151487.715 | 658867.269 | -8516.7525 | 15899.8417 | 2647.7354 | 8084.0779 | -7603.9208 | 86123.2624 | -2048.8256
403.92 | 5.415 | 1.1728 |  | 84860.2599 | -52.5916 | -22912.6241 | 893087.805 | 2152248.61 | -13847.503 | 36404.311 | 13846.1782 | 24523.7092 | -120799.935 | 626548.246 | -5952.6734 | 17235.1127 | 1576.6501 | 7675.8934 | -1595.7491 | 97605.0392 | -2093.6902
404.12 | 5.4113 | 1.1728 |  | 73598.1481 | -12047.4497 | -29390.4099 | 1027020.2 | 1906496.14 | -12701.8359 | 33439.1037 | 11358.1686 | 23237.0808 | -98131.3184 | 535604.11 | -4096.916 | 14366.7177 | 1141.9844 | 7516.719 | 125.8868 | 81686.6227 | -494.782
404.32 | 5.4099 | 1.1728 |  | 61365.8111 | -17197.1147 | -34278.375 | 1190905.43 | 1621377.07 | -12973.5762 | 33966.5572 | 5952.0195 | 22012.4098 | -31470.5919 | 567458.057 | -5800.0386 | 15098.5677 | 218.5322 | 7205.7269 | 1768.8581 | 82106.2034 | -2107.8881
404.52 | 5.4022 | 1.1728 |  | 46766.2374 | -27145.8731 | -40451.9334 | 1473917.47 | 1411324.51 | -11104.8416 | 37586.5669 | 1983.5093 | 20178.822 | 1312.5207 | 619678.41 | -6660.3749 | 15938.5989 | 46.2136 | 6785.5377 | 1852.8235 | 86515.6364 | -2165.2599
404.72 | 5.3887 | 1.1728 |  | 38495.8603 | -41518.4117 | -42029.9578 | 1735727.93 | 1266901.29 | -12316.4064 | 37816.2447 | -561.7196 | 19704.2896 | 42448.3623 | 634631.982 | -7070.3966 | 17162.1654 | -1174.856 | 6743.0411 | 8666.5629 | 93464.1954 | -2438.5446
404.92 | 5.381 | 1.1728 |  | 21457.5119 | -47645.2789 | -44927.5856 | 1876146.88 | 941002.534 | -9505.5876 | 38082.6826 | -4898.1794 | 18938.5832 | 82592.226 | 634830.016 | -6466.8156 | 16888.4696 | -1555.23 | 6554.2082 | 10183.5389 | 93059.2163 | -2461.5186
405.12 | 5.363 | 1.1728 |  | 3270.8696 | -49669.6894 | -42448.6979 | 1903305.46 | 537647.529 | -144.7212 | 35580.7781 | -9473.1982 | 19889.7436 | 144122.664 | 624617.708 | -3231.9038 | 17752.3719 | -2973.4102 | 6931.5163 | 17317.5702 | 99726.4719 | -1430.4862
405.32 | 5.3412 | 1.1728 |  | -14870.6692 | -58725.2341 | -40755.8162 | 2119022.4 | 141491.103 | 1510.4295 | 33930.7479 | -15543.0578 | 19948.2723 | 222270.179 | 637208.337 | -3296.8096 | 19183.7061 | -4530.5427 | 6844.3103 | 24801.882 | 113339.339 | -2075.5351
405.52 | 5.3213 | 1.1728 |  | -30189.1508 | -70449.716 | -37898.9013 | 2407177.68 | -184505.236 | 2104.7206 | 34940.2462 | -21233.4113 | 20393.4503 | 290521.088 | 651673.861 | -2782.6753 | 19833.6352 | -5953.0387 | 6937.1635 | 31514.7125 | 116746.988 | -1960.9747
405.72 | 5.3008 | 1.1728 |  | -42841.4233 | -80109.0711 | -31579.5489 | 2664245.77 | -429525.196 | 5347.7144 | 35217.367 | -25787.078 | 21502.4148 | 356120.621 | 672364.906 | -389.5868 | 21416.5387 | -7471.8236 | 7111.4948 | 37613.7011 | 108397.282 | -2193.9345
405.92 | 5.2874 | 1.1728 |  | -54317.2022 | -102387.392 | -18769.577 | 3096079.85 | -644208.422 | 9278.211 | 40203.4534 | -30874.6647 | 24776.1273 | 387486.741 | 670363.666 | 1.9605 | 18464.9108 | -7222.3498 | 7718.8564 | 35811.4348 | 104055.15 | -985.6974
406.12 | 5.2658 | 1.1728 |  | -64738.5643 | -111632.2 | -10797.2471 | 3392523.81 | -818401.9 | 8420.1134 | 42123.8582 | -35027.6906 | 26309.7089 | 459697.192 | 750365.687 | -1986.8954 | 21846.9631 | -9105.5215 | 7947.2946 | 44347.1674 | 116639.007 | -2038.0839
406.32 | 5.2467 | 1.1728 |  | -77923.0713 | -124688.187 | 1132.5994 | 3705936.02 | -1029001.74 | 8356.8717 | 46518.5925 | -39134.3551 | 28768.4446 | 478836.019 | 777251.906 | -2299.1047 | 20946.1102 | -8521.4263 | 8291.3852 | 40952.5273 | 116519.212 | -2043.4444
406.52 | 5.2257 | 1.1728 |  | -83866.3754 | -129420.446 | 15474.1931 | 3808797.42 | -1142559.04 | 8981.474 | 47024.2462 | -41066.0745 | 32254.9604 | 518903.704 | 759072.62 | -509.3712 | 19534.6813 | -9659.9282 | 9034.7034 | 47209.1827 | 105391.06 | -1394.2594
406.72 | 5.204 | 1.1728 |  | -101302.585 | -127152.666 | 25574.4355 | 3740372.96 | -1536023.03 | 13667.9727 | 43214.6071 | -44793.1772 | 34522.9224 | 548929.518 | 748119.521 | 338.2515 | 20819.9397 | -9840.5428 | 9379.6655 | 47061.441 | 111033.074 | -1959.6341
406.92 | 5.1826 | 1.1728 |  | -107594.539 | -128617.656 | 44100.7223 | 3629731.2 | -1782999.74 | 18842.0507 | 37656.8073 | -46739.2314 | 38924.0529 | 593565.872 | 668374.197 | 2618.0066 | 19169.103 | -11286.0436 | 10279.7517 | 54149.6167 | 101139.294 | -1526.5658
407.12 | 5.1776 | 1.1728 |  | -111530.329 | -136523.723 | 56613.0189 | 3708405.47 | -1865769.75 | 16263.4074 | 36313.1675 | -47333.5153 | 41426.9634 | 594494.929 | 609375.011 | 4554.5146 | 16937.4861 | -11169.4811 | 10531.2233 | 53868.3719 | 92035.4256 | 181.9436
407.32 | 5.1608 | 1.1728 |  | -117282.713 | -130080.537 | 71119.6157 | 3574086.32 | -1952110.22 | 17061.3596 | 33960.8625 | -46480.388 | 44500.6603 | 587416.874 | 676660.127 | 1671.4687 | 21369.5419 | -11126.3282 | 11127.9369 | 54039.5608 | 118595.264 | -1763.8262
407.52 | 5.1506 | 1.1728 |  | -111447.155 | -137575.422 | 86437.3816 | 3682833.64 | -1769524.45 | 8141.9447 | 35531.5863 | -43915.4039 | 47754.2933 | 556200.989 | 693404.001 | -1150.0932 | 21188.1505 | -10614.2142 | 11514.5417 | 51408.1768 | 112574.97 | -2479.1531
407.72 | 5.1483 | 1.1728 |  | -104249.276 | -145759.92 | 101922.574 | 3905803.43 | -1555405.66 | 10913.8948 | 43313.0927 | -43536.6221 | 52208.5507 | 531452.803 | 670818.856 | 1069.1164 | 16880.2106 | -9440.8493 | 12507.1094 | 46445.018 | 87765.1151 | -291.5596
407.92 | 5.1517 | 1.1728 |  | -108142.669 | -143271.382 | 117638.711 | 3948747.55 | -1632386.09 | 13502.7515 | 44541.9042 | -45534.8052 | 56163.626 | 554007.243 | 738921.978 | -103.2056 | 19473.0303 | -9470.8738 | 13197.6565 | 45617.9217 | 106079.305 | -2106.9463
408.12 | 5.142 | 1.1728 |  | -108519.48 | -151004.822 | 134184.611 | 4110427.89 | -1699897.69 | 10050.4459 | 43927.9215 | -47464.5234 | 60431.0483 | 577440.951 | 744791.145 | 42.7319 | 20524.5469 | -9973.0083 | 14187.6195 | 48208.7054 | 111142.739 | -2123.6758
408.32 | 5.1288 | 1.1728 |  | -104535.86 | -148789.83 | 149737.582 | 4085031.36 | -1700603.2 | 11046.2098 | 43484.9219 | -48282.7981 | 63622.2905 | 615712.73 | 698976.135 | 713.8412 | 18402.2853 | -11461.2267 | 14614.2397 | 56493.827 | 100636.731 | -1432.0046
408.52 | 5.1355 | 1.1728 |  | -103617.217 | -141260.559 | 165996.665 | 3751334.12 | -1770942.06 | 11552.2804 | 34607.2119 | -45630.1611 | 66657.5241 | 581394.222 | 625408.17 | 1816.9341 | 18169.0111 | -10718.4444 | 15006.4499 | 53179.1073 | 102442.565 | -1621.4101
408.72 | 5.1216 | 1.1728 |  | -97925.2748 | -120449.618 | 181023.123 | 3183234.42 | -1651642.61 | 15828.9382 | 30814.9068 | -39600.4319 | 69700.0726 | 493824.485 | 542512.393 | 1353.4771 | 15258.6002 | -8769.3724 | 15406.6404 | 44295.0025 | 84673.4969 | -983.8259
408.92 | 5.1021 | 1.1728 |  | -92814.5808 | -105288.612 | 197131.65 | 2688764.09 | -1558015.76 | 12308.5849 | 24205.5318 | -33853.7127 | 73796.7514 | 413610.946 | 467859.492 | 1329.2162 | 13915.523 | -7028.3451 | 16191.3859 | 35855.3465 | 78943.7678 | -779.1042
409.12 | 5.091 | 1.1728 |  | -82354.7752 | -95408.9942 | 210613.392 | 2455015.06 | -1358794.53 | 8771.7645 | 22890.6258 | -29888.0309 | 77055.5076 | 370065.394 | 423726.882 | -1244.7497 | 12218.7858 | -6289.917 | 16809.4929 | 33630.3161 | 72811.661 | -1504.2007
409.32 | 5.0809 | 1.1728 |  | -68758.3387 | -92926.9597 | 226208.471 | 2362622.64 | -1131826.41 | 4369.1529 | 21996.2103 | -27202.3574 | 80596.5561 | 328104.122 | 382587.87 | -2876.6856 | 11008.9497 | -5158.2508 | 17394.8198 | 27291.5745 | 66887.4877 | -2082.1651
409.52 | 5.0695 | 1.1728 |  | -59402.2175 | -80628.3499 | 235094.64 | 2118577.87 | -952403.475 | 4818.8957 | 23003.6373 | -23903.9712 | 82561.6375 | 291427.382 | 369821.094 | -3162.3071 | 9293.646 | -4489.3871 | 17711.4518 | 23894.4075 | 51044.7788 | -1952.4973
409.72 | 5.0692 | 1.1728 |  | -41295.53 | -78218.6204 | 243571.839 | 1969880.15 | -659243.831 | -691.6658 | 20893.7336 | -19823.4692 | 84293.0711 | 246512.516 | 312935.439 | -2027.1857 | 7542.2652 | -3790.977 | 18022.2749 | 20805.4512 | 39527.5978 | -1555.4356
409.92 | 5.0768 | 1.1728 |  | -26469.385 | -66539.5147 | 250670.143 | 1694361.29 | -361029.37 | -5931.151 | 19982.0758 | -14745.9898 | 85752.2008 | 183857.298 | 300032.061 | -3029.7071 | 7194.2125 | -2566.8348 | 18171.9525 | 15580.4905 | 39536.4307 | -1812.853
410.12 | 5.0676 | 1.1728 |  | -13132.546 | -59784.6222 | 254424.882 | 1569721.67 | -36556.7463 | -8079.0499 | 21333.1939 | -9993.3046 | 86964.6254 | 119723.845 | 324718.193 | -4305.8369 | 7967.3546 | -1092.1811 | 18462.8186 | 8115.327 | 42954.3715 | -1845.9877
410.32 | 5.054 | 1.1728 |  | 187.1727 | -50523.2115 | 258290.593 | 1512074.84 | 247000.252 | -7136.5863 | 25384.086 | -7587.191 | 88437.8662 | 112860.059 | 409780.739 | -4100.6014 | 9749.95 | -1424.2391 | 18958.05 | 9532.5756 | 49172.6675 | -1241.174
410.52 | 5.0471 | 1.1728 |  | 14253.4334 | -52404.9447 | 259477.616 | 1765031.17 | 572260.364 | -8946.2206 | 31120.3314 | -6841.5353 | 88894.0003 | 123724.963 | 533331.626 | -3699.3726 | 14781.9612 | -2122.012 | 19125.5481 | 14968.814 | 80991.8379 | -1686.5841
410.72 | 5.0439 | 1.1728 |  | 28630.9766 | -52857.3414 | 261892.933 | 2109225.46 | 975705.996 | -4152.0082 | 43506.7621 | -6674.4777 | 89165.5227 | 115675.656 | 643181.895 | -6672.611 | 16279.6918 | -1818.4669 | 19101.1233 | 13787.1757 | 86788.7124 | -2349.3953
410.92 | 5.0358 | 1.1728 |  | 47457.9159 | -57553.5199 | 258277.34 | 2292533.62 | 1381334.79 | -16236.6572 | 49777.3493 | -4203.0709 | 87677.4044 | 90584.67 | 734997.512 | -8293.2383 | 17004.864 | -1187.2323 | 18638.4544 | 10192.4822 | 91582.9289 | -2761.985
411.12 | 5.0314 | 1.1728 |  | 62258.9316 | -49159.3633 | 254878.684 | 2115050.47 | 1683263.76 | -15195.7451 | 46673.2323 | 813.4317 | 86975.9244 | 53430.5403 | 746040.509 | -5735.8062 | 20835.0077 | -1635.0488 | 18770.9196 | 15023.2651 | 116960.557 | -1620.4278
411.32 | 5.0601 | 1.1728 |  | 77507.2989 | -38228.2406 | 253162.391 | 1907641.8 | 2007062.71 | -17977.2494 | 46807.0298 | 5566.3194 | 86363.2553 | 19824.1593 | 807187.988 | -5078.6911 | 23550.7548 | -1704.2277 | 18550.5167 | 17098.9338 | 131964.214 | -1761.8954
411.52 | 5.0702 | 1.1728 |  | 94383.2107 | -44247.1515 | 245643.721 | 2134236.38 | 2424239.64 | -25279.2478 | 52725.0111 | 8873.8314 | 84833.7412 | -50335.3359 | 815759.029 | -9930.052 | 21490.3113 | 506.2847 | 18252.1271 | 5676.5715 | 118751.184 | -2925.0017
411.72 | 5.0551 | 1.1728 |  | 108119.868 | -40007.7162 | 238462.265 | 2023407.07 | 2599138.15 | -28521.2259 | 52829.4799 | 10557.368 | 83586.1484 | -64250.8798 | 762144.414 | -11302.3341 | 17652.6998 | 827.1233 | 18104.6155 | 2972.5803 | 89867.6004 | -3145.9547
411.92 | 5.066 | 1.1728 |  | 109969.582 | -10470.4995 | 225603.527 | 1229490.43 | 2459158.52 | -25622.1725 | 40909.375 | 13662.8055 | 79970.219 | -79167.8179 | 630695.159 | -8743.2505 | 15781.5421 | 491.8228 | 17317.9898 | 5777.8937 | 86034.5919 | -2871.9371
412.12 | 5.0846 | 1.1728 |  | 112591.552 | 10920.1002 | 214776.238 | 405094.07 | 2409850.85 | -32947.337 | 26984.3403 | 20992.2011 | 77040.5191 | -184126.178 | 428556.116 | -6691.4563 | 11133.3651 | 2670.2777 | 16667.0289 | -5639.7787 | 60784.7094 | -1306.0659
412.32 | 5.0751 | 1.1728 |  | 124339.425 | 31596.221 | 200205.341 | -228662.139 | 2619046.01 | -31575.2262 | 20170.1225 | 28204.0062 | 74003.7958 | -278575.394 | 285924.329 | -5161.2 | 6804.776 | 4369.1657 | 16268.2075 | -12778.9085 | 35824.1145 | 697.137
412.52 | 5.073 | 1.1728 |  | 128973.614 | 46261.4306 | 186293.355 | -536350.163 | 2710337.41 | -34599.0542 | 16829.8246 | 31098.463 | 71469.8888 | -309078.991 | 341084.642 | -4591.4063 | 10981.6072 | 4940.7045 | 15859.9185 | -16020.4559 | 67533.2006 | -66.9782
412.72 | 5.0842 | 1.1728 |  | 144671.167 | 34548.4269 | 171483.964 | -36679.1332 | 3182248.57 | -41638.754 | 29656.4205 | 32427.4654 | 68075.0523 | -324655.855 | 473635.872 | -8261.7944 | 12363.8379 | 5289.0185 | 15252.8563 | -17835.7469 | 65600.4613 | -1070.5963
412.92 | 5.0906 | 1.1728 |  | 162887.168 | 12554.6223 | 159419.855 | 715019.046 | 3717336.87 | -40892.9439 | 44867.9193 | 32292.5634 | 65545.1336 | -332199.811 | 635617.827 | -11563.8955 | 15027.1545 | 5493.2814 | 14929.7346 | -18525.1011 | 75140.8275 | -1537.8129
413.12 | 5.105 | 1.1728 |  | 167891.544 | 14079.6066 | 143146.18 | 971200.432 | 3901997.09 | -37834.6056 | 51822.1968 | 31034.022 | 61534.2989 | -296327.014 | 835304.031 | -13252.3074 | 22273.3924 | 4441.8636 | 14325.2871 | -11774.5114 | 120554.436 | -3461.583
413.32 | 5.122 | 1.1728 |  | 170962.502 | 9529.3763 | 125695.688 | 1090118.75 | 3976730.92 | -42866.5001 | 54894.2986 | 30523.5396 | 56690.5035 | -285318.456 | 844632.617 | -15210.2345 | 20616.5554 | 4393.0398 | 12952.8442 | -12573.8878 | 107232.933 | -4598.2698
413.52 | 5.1238 | 1.1728 |  | 172023.185 | 9005.1259 | 113080.376 | 832821.544 | 3799988.54 | -45103.7066 | 45715.2314 | 30274.0056 | 54103.9281 | -294211.504 | 635114.519 | -14230.2861 | 14162.0288 | 4706.2224 | 12634.5013 | -15937.1087 | 74492.3564 | -3176.0604
413.72 | 5.1474 | 1.1728 |  | 159267.956 | 37156.3985 | 94995.3602 | -65426.3019 | 3378384.63 | -42164.1575 | 29327.5211 | 32590.8331 | 49237.3445 | -296531.217 | 481490.124 | -10164.4175 | 12689.2288 | 3914.2004 | 11575.8518 | -10052.1525 | 70383.9188 | -2956.8635
413.92 | 5.1667 | 1.1728 |  | 152126.602 | 48197.4656 | 82345.0298 | -580498.954 | 3162898.46 | -38201.6616 | 19751.5763 | 34811.4565 | 46407.317 | -366858.513 | 316319.103 | -8454.4258 | 8281.563 | 6220.1442 | 11329.2112 | -23220.7357 | 46980.4932 | -1494.8409
414.12 | 5.1723 | 1.1728 |  | 152374.05 | 49747.9051 | 66656.5461 | -684571.513 | 3230565.86 | -44169.1792 | 17201.1306 | 38204.3324 | 43312.0187 | -385637.295 | 269537.311 | -6114.8517 | 7361.8418 | 5685.5817 | 10747.7771 | -19123.2865 | 42636.9947 | 324.6571
414.32 | 5.1841 | 1.1731 |  | 145148.884 | 44809.9857 | 52145.1167 | -393669.444 | 3156317.72 | -35086.6974 | 22311.7615 | 34467.6418 | 41034.7629 | -351167.909 | 416454.294 | -5700.219 | 12940.5042 | 5372.0984 | 10769.1148 | -17838.2404 | 74228.3862 | -753.9353
414.52 | 5.2164 | 1.174 |  | 151302.331 | 25309.8034 | 38505.8045 | 390101.781 | 3439379.62 | -32798.6438 | 37344.0671 | 30635.8961 | 37686.1661 | -284705.007 | 622696.398 | -7391.0655 | 17258.0136 | 3736.7114 | 9893.5435 | -9850.2011 | 97461.6375 | -1559.2833
414.72 | 5.239 | 1.1751 |  | 150578.177 | -1952.4988 | 21957.1151 | 1301366.35 | 3659859.27 | -32149.2111 | 54702.6694 | 26193.6562 | 33772.2692 | -268335.368 | 811404.76 | -11405.0186 | 19503.2093 | 4577.098 | 9245.7295 | -14525.2869 | 106141.13 | -2229.2602
414.92 | 5.276 | 1.1764 |  | 145978.636 | -6983.7267 | 5481.1764 | 1601072.36 | 3694218.46 | -30286.8215 | 60765.1084 | 24187.9222 | 29934.2761 | -211096.1 | 959610.909 | -11168.1294 | 24610.72 | 2504.3714 | 8679.17 | -4132.4025 | 133834.771 | -3151.4109
415.12 | 5.3233 | 1.1775 |  | 129274.607 | -7832.0606 | -6906.8116 | 1589262.36 | 3360115.46 | -23891.2715 | 59046.4488 | 20891.2514 | 27202.5877 | -191555.678 | 950563.692 | -11014.5984 | 24506.1203 | 2705.4924 | 8159.4303 | -7008.4676 | 129166.762 | -4189.695
415.32 | 5.3541 | 1.1786 |  | 116040.511 | -13552.3564 | -16082.9437 | 1484210.15 | 2973817.14 | -23298.7957 | 52604.348 | 17947.8934 | 26188.7766 | -162569.884 | 747898.632 | -8811.2866 | 17343.0163 | 2035.73 | 8180.3862 | -4468.4012 | 85829.8669 | -1150.6306
415.52 | 5.3965 | 1.1798 |  | 85830.2275 | 4485.6448 | -24186.2642 | 798323.564 | 2106553.41 | -11763.2351 | 33508.3627 | 12818.1922 | 24436.4934 | -87011.0097 | 625517.56 | -2339.0999 | 18906.6903 | 364.7531 | 7756.8133 | 5082.2232 | 114560.247 | -967.6749
415.72 | 5.4528 | 1.1807 |  | 69013.8804 | -1145.4447 | -30359.3291 | 736825.931 | 1732434.7 | -13503.4448 | 27354.1972 | 11121.9377 | 22582.8994 | -79145.7886 | 524489.262 | -2790.1631 | 16626.6985 | 324.8734 | 7266.2461 | 5262.4341 | 101856.628 | -1001.4261
415.92 | 5.4832 | 1.1816 |  | 69176.193 | -27976.2877 | -33034.2869 | 1240272.93 | 1872466.06 | -24115.2371 | 34058.3716 | 11114.2059 | 22097.218 | -113287.869 | 460329.771 | -6728.3332 | 10524.0185 | 1876.37 | 7039.8149 | -4283.6576 | 59661.7207 | -606.9323
416.12 | 5.5212 | 1.1827 |  | 54535.5196 | -37836.1279 | -35255.5777 | 1480346.86 | 1713811.57 | -23493.751 | 36623.6529 | 8843.5408 | 22785.1572 | -110644.602 | 558261.375 | -8104.7379 | 14725.2084 | 2407.2381 | 7486.0337 | -8373.2295 | 79290.0344 | -2143.5842
416.32 | 5.5723 | 1.1839 |  | 44534.4004 | -40649.747 | -35100.3938 | 1697085.16 | 1556353.39 | -17167.4468 | 39749.0545 | 4581.6601 | 23656.0148 | -34633.5706 | 669038.135 | -8878.965 | 19206.5853 | 458.5029 | 7783.2966 | 886.332 | 106335.626 | -3515.4911
416.52 | 5.6151 | 1.1853 |  | 32730.4499 | -62974.0309 | -31466.4358 | 2290511.14 | 1351099.93 | -13719.4133 | 47423.4722 | -2770.1712 | 25536.9018 | 28870.2159 | 697639.958 | -7372.0483 | 16935.615 | 223.2234 | 8194.5642 | 847.3137 | 95913.0735 | -1744.9187
416.72 | 5.6821 | 1.1868 |  | 16282.409 | -76204.9312 | -28567.4684 | 2687786.24 | 1004945.8 | -12555.2312 | 48864.6355 | -9599.6797 | 27144.1224 | 144789.663 | 788245.295 | -5734.5623 | 20594.741 | -2801.6171 | 8661.5097 | 16003.1501 | 110785.477 | -2342.4471
416.92 | 5.7456 | 1.1881 |  | -2454.3711 | -81198.4868 | -23466.9231 | 2885931.85 | 600947.999 | -1588.4669 | 49830.5759 | -16533.3112 | 28521.883 | 234510.169 | 839760.986 | -4004.4682 | 23272.589 | -4600.5525 | 9003.9251 | 25333.1048 | 130699.553 | -2224.6019
417.12 | 5.819 | 1.1897 |  | -11539.6232 | -96350.7788 | -14973.3214 | 3216919.92 | 451306.716 | -3958.7203 | 52137.7533 | -19754.2429 | 30866.2255 | 276438.573 | 825239.931 | -3082.8877 | 21784.513 | -5703.0877 | 9339.5071 | 30515.1948 | 118406.979 | -1410.2945
417.32 | 5.8985 | 1.1912 |  | -22751.7085 | -107044.375 | -2181.9632 | 3405190.93 | 304201.14 | -1876.3306 | 54355.7552 | -21913.4252 | 34876.5165 | 286222.241 | 836365.782 | -2975.6865 | 22274.8019 | -5626.9584 | 10162.5276 | 29285.8095 | 120254.139 | -1107.7856
417.52 | 5.9666 | 1.1929 |  | -41010.8453 | -112794.041 | 12691.1969 | 3520476.38 | -16555.1645 | -2626.437 | 52759.2057 | -24440.1231 | 39620.048 | 315543.895 | 885756.821 | -2966.1843 | 24445.526 | -5894.9225 | 11185.2744 | 31837.964 | 136186.812 | -2152.169
417.72 | 6.0276 | 1.1948 |  | -50913.3875 | -136645.131 | 31812.3767 | 3992888.97 | -255440.394 | -1823.3537 | 54616.0754 | -30380.9866 | 45947.0717 | 377083.403 | 855855.284 | -2631.3487 | 22223.8922 | -6695.584 | 12639.782 | 35498.7728 | 123851.73 | -1593.0923
417.92 | 6.0854 | 1.1972 |  | -64434.6668 | -147785.743 | 51437.6937 | 4264423.32 | -585801.934 | -2996.0328 | 53065.4572 | -35786.4802 | 51342.8632 | 474865.933 | 893171.888 | -2789.2932 | 24550.5509 | -9205.7369 | 13773.724 | 49033.1172 | 137717.978 | -1731.1655
418.12 | 6.1459 | 1.1999 |  | -83056.1117 | -147979.138 | 68565.8642 | 4388359.84 | -941109.391 | 1224.3585 | 54088.4237 | -40905.3797 | 55086.6113 | 528380.538 | 985438.521 | -2685.6259 | 28429.7673 | -9765.0064 | 14266.3781 | 50209.4316 | 159784.621 | -3132.2875
418.32 | 6.1926 | 1.2028 |  | -82248.1426 | -163954.685 | 91605.7367 | 4761049.75 | -861330.059 | -473.7554 | 59564.6878 | -42271.1574 | 61308.0476 | 539372.912 | 963436.737 | -4137.9536 | 25407.5622 | -9898.1179 | 15443.8574 | 51626.5587 | 140651.824 | -2482.6334
418.52 | 6.2488 | 1.2064 |  | -87416.3724 | -166103.689 | 116746.177 | 4743530.93 | -960856.813 | -1602.2075 | 58506.2185 | -42748.1888 | 67763.3878 | 521044.63 | 940088.346 | -4643.7162 | 24886.2657 | -8878.9239 | 16645.6979 | 44888.8292 | 136874.688 | -2472.8414
418.72 | 6.3408 | 1.2098 |  | -89250.978 | -151642.803 | 137568.736 | 4370522.3 | -943290.824 | 2101.3667 | 53476.1384 | -38817.7537 | 72941.795 | 492480.019 | 931608.353 | -5114.2174 | 27195.7799 | -8976.1577 | 17511.4338 | 47740.0233 | 154705.993 | -3527.7957
418.92 | 6.424 | 1.2127 |  | -85351.4344 | -155628.111 | 163858.98 | 4312260.67 | -842189.093 | -3252.1111 | 53618.1935 | -36219.7153 | 80862.2733 | 416923.29 | 847777.985 | -5533.3741 | 22225.9858 | -6186.6742 | 19038.2299 | 33293.9293 | 128542.392 | -3145.2446
419.12 | 6.5107 | 1.2163 |  | -74043.8493 | -168059.89 | 192041.457 | 4396997.78 | -677164.696 | -9636.7999 | 53288.0377 | -34669.5973 | 89776.2252 | 386219.928 | 706110.284 | -3739.1023 | 15203.6445 | -5208.9275 | 20985.4009 | 28537.9228 | 88340.1088 | -1682.1865
419.32 | 6.5935 | 1.2203 |  | -81994.5313 | -155013.75 | 217221.684 | 4202016.6 | -933538.849 | 929.0717 | 50434.0804 | -37718.1778 | 97690.3534 | 414896.149 | 732207.218 | -3118.0166 | 17296.104 | -5219.5433 | 22702.786 | 25153.1646 | 91919.6473 | -2910.4622
419.52 | 6.681 | 1.2239 |  | -78268.8813 | -154153.903 | 235824.068 | 4250958.02 | -930722.74 | -1604.8108 | 53272.1513 | -40021.6003 | 102803.636 | 466511.291 | 786280.889 | -4525.7841 | 19538.8108 | -6833.4434 | 23680.2403 | 34942.9294 | 116614.072 | -3727.0005
419.72 | 6.7579 | 1.2273 |  | -57618.729 | -167370.815 | 259913.887 | 4602014.42 | -441785.721 | -9208.6864 | 59475.8568 | -35923.6838 | 108428.004 | 431873.692 | 799534.221 | -6828.5078 | 18166.4765 | -6605.534 | 24448.0272 | 34055.2048 | 95464.962 | -3033.9501
419.92 | 6.8158 | 1.2308 |  | -46420.4938 | -161665.929 | 277864.059 | 4530696.48 | -109018.067 | -15687.0944 | 63262.3232 | -31046.4188 | 113261.335 | 366233.564 | 906870.785 | -9940.7734 | 20647.8154 | -4876.307 | 25492.7387 | 25083.4265 | 103604.734 | -4083.3157
420.12 | 6.9092 | 1.2347 |  | -29466.8546 | -147868.384 | 299362.719 | 4211994.35 | 266247.877 | -19230.0094 | 60015.3676 | -23941.332 | 119288.069 | 301111.81 | 881673.429 | -9010.7725 | 21741.0903 | -4419.8257 | 26769.4858 | 25837.523 | 115729.329 | -3977.5214
420.32 | 7.0008 | 1.2381 |  | -18221.1512 | -138310.502 | 319866.124 | 3979246.96 | 475572.081 | -16565.4737 | 61825.662 | -20989.7231 | 126381.033 | 232581.308 | 838747.01 | -8219.2633 | 17993.0571 | -2048.2465 | 28282.1151 | 15565.921 | 103001.12 | -2866.6439
420.52 | 7.0914 | 1.2416 |  | -5020.2107 | -121233.765 | 338681.093 | 3640470.09 | 603467.935 | -16123.2279 | 55985.5866 | -17997.1937 | 132684.832 | 233734.754 | 852002.586 | -5607.6668 | 21247.2468 | -2913.6532 | 29773.8464 | 20565.6186 | 122638.202 | -2461.6383
420.72 | 7.1985 | 1.2457 |  | 16894.6496 | -108511.619 | 354156.695 | 3523469.76 | 1078607.27 | -23791.2241 | 58285.1964 | -12064.0864 | 135989.142 | 202568.567 | 942512.57 | -12674.65 | 25348.214 | -3390.8036 | 29965.2341 | 24254.2898 | 143366.941 | -5383.1195
420.92 | 7.2914 | 1.2493 |  | 44977.2538 | -99787.379 | 363249.891 | 3349059.61 | 1759340.32 | -26138.1781 | 62709.2389 | -2616.8609 | 138820.595 | 55950.1754 | 921732.14 | -16530.1665 | 23457.597 | 46.2688 | 30626.6881 | 9373.1966 | 135237.563 | -4819.5504
421.12 | 7.3964 | 1.2528 |  | 68398.6417 | -62058.0694 | 371218.919 | 2415351.49 | 2213645.05 | -23179.6088 | 55095.7662 | 8837.3703 | 142306.89 | -48468.3808 | 919598.564 | -11828.2054 | 25780.9157 | 1166.3685 | 31445.3294 | 5870.5381 | 150840.455 | -4130.4256
421.32 | 7.5079 | 1.2561 |  | 90834.1348 | -46692.2868 | 376486.535 | 2050065.95 | 2704756.98 | -25419.1681 | 56298.8454 | 16686.889 | 146357.767 | -149479.014 | 915395.851 | -11275.2059 | 24827.3894 | 3289.8891 | 32561.73 | -4111.2312 | 148085.101 | -2835.8504
421.52 | 7.5891 | 1.2595 |  | 112163.066 | -43307.0394 | 375621.822 | 2218751.6 | 3113256.92 | -31035.142 | 65025.5892 | 17301.8705 | 149339.667 | -166448.113 | 998829.363 | -12188.2224 | 24049.46 | 4369.07 | 33599.0917 | -13068.2787 | 127618.186 | -3399.9975
421.72 | 7.6755 | 1.2636 |  | 134103.986 | -49347.2307 | 372825.279 | 2595673.09 | 3493047.38 | -29899.6677 | 70647.3195 | 16553.7133 | 150680.59 | -102677.719 | 1103484.51 | -10904.054 | 28740.0668 | 1432.8985 | 34357.1276 | 3584.8358 | 147847.578 | -3521.8516
421.92 | 7.7681 | 1.2678 |  | 146486.627 | -49621.619 | 357667.81 | 2872776.73 | 3734986.16 | -32032.866 | 76281.0604 | 15847.0799 | 146547.596 | -83137.8846 | 1279910.09 | -13157.6887 | 35697.7716 | 787.4819 | 33485.2381 | 7760.2165 | 195760.358 | -4160.4671
422.12 | 7.8659 | 1.2717 |  | 173352.358 | -36562.4647 | 343552.216 | 2838611.73 | 4438405.48 | -27370.7077 | 85915.3305 | 23121.5215 | 142489.726 | -122860.532 | 1431728.13 | -14154.6557 | 38642.0122 | 333.1559 | 32586.5533 | 14101.2489 | 212949.546 | -3804.4833
422.32 | 7.9681 | 1.2751 |  | 193182.932 | -36067.2436 | 333177.522 | 2802240.69 | 4996776.09 | -28478.044 | 88480.2561 | 31386.4556 | 141598.82 | -236386.558 | 1490064.15 | -13523.0146 | 41122.766 | 2555.3529 | 32450.0754 | 3241.9482 | 227710.002 | -3498.033
422.52 | 8.0924 | 1.2783 |  | 209147.558 | -36269.3466 | 321209.557 | 2862926.48 | 5395289.39 | -28296.1348 | 93159.1189 | 34866.377 | 141999.351 | -308126.919 | 1492241.47 | -13530.1452 | 40076.352 | 4766.9254 | 32935.1144 | -7828.861 | 222652.363 | -3698.0781
422.72 | 8.2143 | 1.2808 |  | 216234.157 | -46350.7167 | 307927.215 | 3081211.84 | 5535280.47 | -38260.1888 | 96633.5884 | 34814.24 | 142485.771 | -330450.323 | 1488720.1 | -16636.422 | 37070.6886 | 6216.3507 | 33688.2387 | -16281.7191 | 201858.26 | -3548.3624
422.92 | 8.3269 | 1.283 |  | 215136.434 | -31459.8528 | 289629.17 | 2872152.69 | 5412263.73 | -29987.8789 | 94606.3867 | 32772.2358 | 140504.678 | -253087.23 | 1530553.19 | -13783.5763 | 40414.3864 | 3166.644 | 33832.0172 | -189.0915 | 220759.141 | -3239.7396
423.12 | 8.4705 | 1.2855 |  | 211436.862 | -30362.8955 | 270198.873 | 2933955.34 | 5277468.18 | -22101.9764 | 92583.8865 | 30038.4023 | 136892.631 | -204343.439 | 1528276.84 | -10470.8962 | 42882.1898 | 1198.8702 | 32961.3843 | 10983.0928 | 240874.417 | -2899.9897
423.32 | 8.6075 | 1.2858 |  | 213107.637 | -49383.5939 | 251614.679 | 3364495.45 | 5420776.98 | -29578.5456 | 100459.551 | 29533.7451 | 134718.969 | -224470.48 | 1516110.68 | -14588.4182 | 38342.1851 | 2405.1663 | 32695.9853 | 2968.4077 | 199451.826 | -3284.8474
423.52 | 8.7184 | 1.2858 |  | 206123.24 | -50566.9359 | 230163.93 | 3364024.5 | 5304504.78 | -26363.5285 | 96575.8092 | 28695.0555 | 132010.755 | -213717.321 | 1531518.46 | -11102.9241 | 41604.133 | 1990.5636 | 32571.1032 | 7732.0511 | 237638.48 | -1650.0693
423.72 | 8.8762 | 1.2861 |  | 185890.258 | -40304.5526 | 210082.407 | 3110368.35 | 4969545.72 | -26789.9443 | 92547.8785 | 27599.7993 | 127533.343 | -208583.76 | 1614369.22 | -13549.6922 | 45041.6652 | 2812.7757 | 31629.2917 | 4608.4811 | 260932.882 | -5407.4955
423.92 | 9.0003 | 1.2852 |  | 181117.761 | -64802.0562 | 198482.509 | 3634843.67 | 5028426.88 | -22178.9223 | 100632.817 | 26093.2603 | 130385.381 | -200620.374 | 1550638.39 | -8710.6929 | 40191.8445 | 2170.7835 | 32870.115 | 7145.3652 | 224059.526 | -65.5178
424.12 | 9.1219 | 1.2849 |  | 155298.395 | -96486.0055 | 193411.84 | 4414144.7 | 4482232.15 | -28635.2253 | 106646.737 | 13465.1808 | 132442.293 | -107581.313 | 1645627.61 | -15477.5348 | 40709.495 | 2936.9453 | 33755.3841 | -3239.2926 | 225292.564 | -4931.4293
424.32 | 9.2721 | 1.2834 |  | 132729.775 | -110933.061 | 182391.27 | 4960637.68 | 4202689.04 | -24620.1169 | 117669.631 | 6127.7803 | 131154.393 | 20762.1962 | 1760763.64 | -20278.0775 | 41912.0173 | -635.2084 | 33752.9333 | 15560.5324 | 225755.036 | -6181.3618
424.52 | 9.3932 | 1.2801 |  | 101343.058 | -140759.235 | 186403.463 | 5494566.83 | 3577698.94 | -28682.0685 | 115311.75 | -2075.3018 | 133918.165 | 41486.7587 | 1761608.29 | -19778.3955 | 43762.5427 | 1093.4691 | 34259.9026 | 4132.6019 | 242443.951 | -7001.215
424.72 | 9.4835 | 1.2783 |  | 84308.4701 | -158132.563 | 194780.153 | 5856577.94 | 3188013.57 | -25827.4401 | 117181.686 | -9572.5161 | 139867.594 | 160471.795 | 1707728.6 | -17598.5991 | 40415.6824 | -1916.1603 | 36137.0856 | 20137.2897 | 222123.727 | -5515.3286
424.92 | 9.6294 | 1.2777 |  | 54309.8647 | -179829.503 | 210638.426 | 6191523.68 | 2540630.95 | -26044.8749 | 111596.952 | -17719.9954 | 145114.868 | 265126.46 | 1702919.26 | -12555.8632 | 42710.0645 | -3856.6258 | 36819.5782 | 27296.338 | 234532.013 | -4250.3344
425.12 | 9.7611 | 1.276 |  | 29734.8594 | -195251.111 | 226632.749 | 6752763.41 | 2171600.9 | -19738.5626 | 119241.456 | -25475.7337 | 151329.967 | 360326.284 | 1863556.5 | -13584.8594 | 48037.0247 | -5758.0705 | 38562.9057 | 34206.3519 | 255910.97 | -4780.261
425.32 | 9.8521 | 1.2747 |  | 20241.3364 | -241693.732 | 248143.899 | 8044576.38 | 2146806.75 | -32927.8067 | 137116.803 | -35076.0928 | 159292.778 | 452269.76 | 2024598.43 | -24735.017 | 48654.6869 | -6436.3667 | 40391.7172 | 38600.8202 | 262896.613 | -7178.5285
425.52 | 9.9744 | 1.2738 |  | 12768.2862 | -267474.561 | 273709.113 | 8644650.08 | 2007825.67 | -43812.6977 | 140112.246 | -40598.167 | 166039.474 | 545663.661 | 2092575.02 | -24515.5214 | 52212.9644 | -8923.1005 | 41692.2821 | 54040.7144 | 294205.735 | -8202.014
425.72 | 10.1217 | 1.2718 |  | -13267.8748 | -265779.923 | 308582.307 | 8669753.69 | 1580943.09 | -28997.2185 | 139844.583 | -45085.2212 | 175367.142 | 576005.053 | 2186713.95 | -17645.9123 | 56801.3655 | -8909.6652 | 43228.8963 | 52427.0947 | 314530.167 | -6226.4757
425.92 | 10.2147 | 1.2684 |  | -22989.426 | -273888.903 | 346643.4 | 8845603.88 | 1371398.35 | -46184.0769 | 140925.888 | -47847.4862 | 187768.607 | 648809.757 | 2280335.72 | -28001.4929 | 60572.7657 | -11044.7223 | 46739.9082 | 63115.7752 | 334668.36 | -7543.4394
426.12 | 10.3254 | 1.2655 |  | -29985.7456 | -264088.515 | 384564.208 | 8654805.33 | 1173644.77 | -40522.7072 | 134807.538 | -48298.7343 | 195669.007 | 729649.172 | 2306329.22 | -24199.9425 | 65908.0966 | -15201.6982 | 47039.6578 | 90060.6298 | 378310.051 | -6788.994
426.32 | 10.4592 | 1.2619 |  | -29165.0047 | -293016.577 | 431798.338 | 9285175.02 | 1158039.81 | -46857.1696 | 142895.28 | -54008.932 | 210334.571 | 698569.944 | 2278368.47 | -25224.2423 | 59987.6685 | -10894.539 | 49977.5212 | 65854.6979 | 346834.266 | -7739.1152
426.52 | 10.5525 | 1.2578 |  | -1642.8876 | -315865.837 | 478401.775 | 9790659.5 | 1755479.39 | -52060.5359 | 153435.796 | -50687.8528 | 225464.715 | 672469.798 | 2207598.48 | -26517.2292 | 52159.5665 | -10614.7891 | 53381.9603 | 62345.9568 | 282634.836 | -6583.0213
426.72 | 10.6094 | 1.2539 |  | -7407.2693 | -275851.616 | 515419.434 | 9029105.31 | 1544749.11 | -38574.1062 | 151769.493 | -51179.7004 | 234772.986 | 659513.971 | 2293389.15 | -24261.3863 | 57405.8721 | -9779.1413 | 55655.6824 | 52391.7564 | 296870.071 | -6732.5627
426.92 | 10.7145 | 1.2504 |  | 11081.1076 | -229455.766 | 549177.219 | 7923360.25 | 1740900.37 | -43008.4318 | 139330.107 | -42242.1023 | 240649.576 | 658283.252 | 2295667.03 | -29863.2215 | 60640.9434 | -11848.4195 | 56284.69 | 68711.6182 | 327815.656 | -9689.0742
427.12 | 10.7847 | 1.2455 |  | 23230.39 | -194737.351 | 575926.596 | 6868313.14 | 1941960.53 | -32781.5807 | 121488.018 | -29140.3899 | 246599.189 | 488336.694 | 2193724.46 | -20364.0157 | 62289.4922 | -8973.3286 | 56662.6482 | 57155.3656 | 339195.345 | -5395.5166
427.32 | 10.8501 | 1.2412 |  | 56738.4634 | -164396.381 | 600358.229 | 6126609.94 | 2594788.39 | -33151.0996 | 118151.646 | -16808.3432 | 255482.952 | 367625.731 | 2126907.78 | -22575.9968 | 58343.6473 | -7070.6604 | 58751.0285 | 52217.2344 | 329232.369 | -5489.8394
427.52 | 10.9288 | 1.2375 |  | 91034.0924 | -146355.556 | 615396.666 | 5686775.6 | 3243308.31 | -41308.7234 | 115767.031 | -6297.3708 | 261299.146 | 227106.656 | 2019775.2 | -29552.5058 | 56287.9755 | -4333.1267 | 59566.9359 | 42733.6759 | 325711.436 | -7473.0418
427.72 | 11.002 | 1.2337 |  | 112964.75 | -112531.118 | 621264.862 | 4853750.09 | 3657427.41 | -33528.1422 | 109856.995 | 4310.6294 | 265049.358 | 98418.1953 | 1915532.31 | -23168.6226 | 52888.744 | -1946.6809 | 60636.7839 | 31571.1581 | 305402.815 | -6019.1848
427.92 | 11.0885 | 1.2296 |  | 144936.796 | -93395.8897 | 619539.174 | 4389290.12 | 4229218.61 | -35470.2266 | 105903.905 | 12968.1237 | 266735.766 | -5186.87 | 1853157.28 | -21554.7301 | 51341.9338 | 198.5147 | 61090.3327 | 18510.978 | 294472.438 | -6198.743
428.12 | 11.1697 | 1.2247 |  | 181848.295 | -91578.3927 | 610766.355 | 4452189.48 | 5054225.57 | -37724.4374 | 111466.11 | 21708.6949 | 268354.392 | -115328.483 | 1853778.04 | -23618.0908 | 51387.0567 | 1856.2408 | 62064.2596 | 10200.8748 | 284870.393 | -5438.7105
428.32 | 11.2186 | 1.2192 |  | 201160.201 | -87985.5739 | 593685.398 | 4380513.22 | 5446580.89 | -48618.853 | 112052.682 | 26849.236 | 266372.663 | -177162.179 | 1909129.42 | -30130.0621 | 53340.6361 | 3435.1809 | 61893.7919 | 6368.7652 | 311173.259 | -8949.4181
428.52 | 11.271 | 1.2144 |  | 218080.008 | -72683.7239 | 569758.172 | 4178963.29 | 5699555.03 | -34347.5466 | 113951.2 | 28337.2505 | 263257.401 | -159999.893 | 1907031.72 | -24834.0595 | 51632.4734 | 2208.5942 | 61822.6899 | 12743.0715 | 296772.788 | -6635.0352
428.72 | 11.313 | 1.2097 |  | 219977.385 | -68332.4029 | 539203.176 | 4168799.84 | 5698120.23 | -40918.0223 | 114608.474 | 27401.2853 | 255387.612 | -161443.912 | 1957187.93 | -28219.1412 | 54572.7515 | 2622.8561 | 59905.8147 | 10010.1229 | 320996.366 | -8539.5109
428.92 | 11.3253 | 1.205 |  | 231599.774 | -79389.161 | 506810.182 | 4465374.43 | 6009929.06 | -37294.8188 | 122105.544 | 28907.4515 | 249775.192 | -189276.623 | 1901530.1 | -27499.9875 | 49796.1984 | 2833.0113 | 59291.1215 | 11632.336 | 294574.622 | -6392.9691
429.12 | 11.3547 | 1.2012 |  | 233333.95 | -90780.6166 | 473315.643 | 4772852.9 | 6088201.68 | -33955.7085 | 125671.869 | 26893.1906 | 242381.896 | -186401.753 | 1925385.77 | -21609.0252 | 49188.9234 | 3384.7017 | 57802.3663 | 4260.075 | 283297.124 | -5485.151
429.32 | 11.3979 | 1.1968 |  | 226580.486 | -105099.299 | 436734.973 | 5295452.61 | 6111266.88 | -32893.7482 | 136499.661 | 23029.4341 | 235517.149 | -149518.863 | 2083792.1 | -24781.5142 | 49709.7487 | 3762.0874 | 57627.697 | -2718.4301 | 260698.149 | -7011.1936
429.52 | 11.4192 | 1.1919 |  | 217505.221 | -133566.662 | 408387.811 | 5977886.25 | 6056863.59 | -35965.5887 | 143486.307 | 18644.4429 | 230245.668 | -111189.492 | 2117739.42 | -27299.1366 | 51670.4203 | 2634.4719 | 56605.8685 | 4936.258 | 284544.435 | -7237.8545
429.72 | 11.4548 | 1.1874 |  | 184318.574 | -143091.801 | 383308.846 | 6264455.13 | 5409601.2 | -35601.7778 | 142110.23 | 10169.2083 | 225270.645 | -11165.5675 | 2192703.66 | -31099.7711 | 55877.8193 | 846.948 | 56266.0206 | 13165.3397 | 309789.765 | -9712.6213
429.92 | 11.4897 | 1.1823 |  | 145995.126 | -153121.268 | 365572.141 | 6303480.82 | 4582583.05 | -36831.0512 | 133878.059 | 1937.7746 | 221021.978 | 100092.556 | 2100550.38 | -31210.5193 | 55566.3747 | -1757.5207 | 54838.0099 | 28317.7469 | 324221.848 | -10000.5327
430.12 | 11.5064 | 1.1767 |  | 100337.993 | -162455.618 | 359846.741 | 6291644 | 3499906.26 | -36942.3111 | 123897.638 | -10194.9451 | 220748.881 | 208508.767 | 2026874.29 | -27417.2047 | 54305.0382 | -2447.1222 | 55190.8461 | 26256.9344 | 312967.922 | -8018.6122
430.32 | 11.5265 | 1.1732 |  | 75958.4917 | -189928.529 | 359886.701 | 6884738.57 | 3078855.44 | -34378.2854 | 128024.047 | -17601.3225 | 220395.927 | 291967.618 | 1956523.26 | -25527.8491 | 50781.4424 | -4584.8131 | 54268.5563 | 38919.1833 | 297683.256 | -7431.2525
430.52 | 11.5591 | 1.1727 |  | 47531.2992 | -234052.903 | 376436.917 | 7767382.03 | 2665674.83 | -43220.5585 | 134785.304 | -25986.5747 | 226235.738 | 338348.364 | 2013553.4 | -27010.4911 | 52578.5431 | -4181.5781 | 56004.1509 | 34489.5387 | 307066.116 | -9015.824
430.72 | 11.5587 | 1.1728 |  | 20047.2197 | -252103.136 | 390572.887 | 8538167.81 | 2200878.54 | -38794.4301 | 147212.418 | -39101.3297 | 232273.672 | 501421.629 | 2192755.87 | -25468.7558 | 54944.7802 | -6821.3767 | 57930.0925 | 45079.9739 | 305747.341 | -8828.467
430.92 | 11.5773 | 1.1728 |  | 3430.3281 | -296358.567 | 419053.217 | 9569213.82 | 1757913.27 | -55711.5087 | 151136.024 | -51397.4429 | 238994.582 | 688250.063 | 2293581.38 | -31245.3018 | 58449.8753 | -10969.0152 | 59428.8506 | 63798.5175 | 319461.351 | -9643.6333
431.12 | 11.5807 | 1.1728 |  | -27610.5446 | -295858.741 | 438528.981 | 9848428.54 | 1195449.02 | -50084.0416 | 158428.473 | -60926.7662 | 240015.998 | 822609.555 | 2473575.97 | -32925.8374 | 62536.7072 | -13675.0686 | 59258.4954 | 76568.0044 | 333072.821 | -8908.7474
431.32 | 11.5856 | 1.1728 |  | -36576.7154 | -300870.96 | 462840.712 | 10051262.3 | 1032597.4 | -52576.8306 | 158965.983 | -64707.3573 | 241085.151 | 893555.655 | 2614201.35 | -30025.5858 | 70986.312 | -15949.5198 | 58720.4385 | 89778.2303 | 399404.901 | -8086.4593
431.52 | 11.584 | 1.1728 |  | -25611.9928 | -326273.453 | 499847.444 | 10852331.6 | 1494602.83 | -66180.2403 | 177242.514 | -64533.9576 | 248957.637 | 882236.845 | 2782210.97 | -40799.3498 | 70761.7141 | -14802.3949 | 59719.5333 | 88327.8809 | 402785.458 | -10397.6802
431.72 | 11.5796 | 1.1728 |  | -6790.3928 | -351656.188 | 539343.495 | 11232222.3 | 1867757.74 | -71786.1196 | 176916.333 | -60976.6764 | 259716.041 | 830409.508 | 2733234.25 | -40920.1872 | 70415.3501 | -13728.5438 | 61857.9489 | 82198.8214 | 397218.561 | -11287.2738
431.92 | 11.5924 | 1.1728 |  | -12486.8039 | -322345.237 | 573108.2 | 10644120.2 | 1660790.48 | -59090.6802 | 174537.955 | -61337.5635 | 266810.252 | 821708.669 | 2729929.86 | -35561.9506 | 68490.6781 | -12549.0709 | 63279.0137 | 70771.8351 | 368560.863 | -11069.437
432.12 | 11.5759 | 1.1728 |  | 518.5003 | -318644.061 | 607120.151 | 10312464.8 | 1733666.12 | -45734.013 | 164316.908 | -57622.7608 | 277773.134 | 808361.47 | 2502510.3 | -23630.9325 | 63567.2059 | -14208.208 | 65319.4872 | 84683.1691 | 364137.523 | -4309.7321
432.32 | 11.5919 | 1.1728 |  | 8777.1449 | -285399.884 | 629306.383 | 9739024.75 | 1723313.52 | -37922.3647 | 160933.221 | -57282.7007 | 278334.724 | 780761.858 | 2541332.99 | -23735.9203 | 67342.9227 | -12869.0668 | 64661.9719 | 75664.2215 | 370636.615 | -7996.9607
432.52 | 11.6085 | 1.1728 |  | 62017.4025 | -275027.908 | 647397.24 | 9549878.25 | 2949329.03 | -46621.5345 | 168489.64 | -41154.6043 | 281916.412 | 637157.929 | 2544866.03 | -30890.7491 | 62890.2637 | -11293.4481 | 65765.9903 | 71439.9848 | 338154.642 | -6826.4138
432.72 | 11.5805 | 1.1728 |  | 92101.5592 | -235600.102 | 654294.398 | 8609334.09 | 3679605.09 | -44615.2441 | 163341.526 | -24437.1392 | 281006.977 | 409709.136 | 2576973.03 | -35910.2172 | 66425.9581 | -6180.4683 | 64596.2163 | 49984.9053 | 369167.175 | -10671.7015
432.92 | 11.5609 | 1.1728 |  | 126466.299 | -182514.921 | 661357.969 | 7179059.59 | 4161239.35 | -32693.5817 | 147251.832 | -10124.7112 | 286287.291 | 312782.879 | 2413916.34 | -24763.957 | 65381.2397 | -6960.3731 | 66528.9059 | 59521.6957 | 376937.482 | -6030.0077
433.12 | 11.5733 | 1.1728 |  | 143593.239 | -147730.579 | 655589.306 | 6408739 | 4318763.13 | -31132.7501 | 139741.125 | -5271.2371 | 284078.903 | 233973.44 | 2316367.96 | -24476.7769 | 63359.1278 | -4701.8721 | 64817.2179 | 46811.9296 | 372883.007 | -6180.2683
433.32 | 11.5251 | 1.1728 |  | 170496.467 | -145391.024 | 634428.725 | 6243824.17 | 4802719.64 | -31467.3414 | 138582.043 | 1950.9959 | 282285.168 | 140503.135 | 2221431.49 | -22544.3412 | 58681.9992 | -3093.0382 | 66031.5113 | 37836.127 | 334020.963 | -4493.6687
433.52 | 11.4662 | 1.1728 |  | 194691.874 | -122934.85 | 603776.465 | 5902501.66 | 5133953.11 | -29404.5474 | 135745.981 | 4631.9547 | 272134.078 | 154144.778 | 2218865.12 | -20999.0214 | 60231.1646 | -4453.8422 | 63110.2412 | 45876.8444 | 349757.883 | -5883.0356
433.72 | 11.4613 | 1.1728 |  | 216501.141 | -133665.3 | 566843.348 | 6147877.98 | 5690498.58 | -29751.0908 | 141652.662 | 10505.3049 | 262228.006 | 39883.0745 | 2216753.84 | -24922.5837 | 59089.0449 | -1586.4078 | 61363.716 | 32428.1 | 341890.833 | -6025.8528
433.92 | 11.4196 | 1.1728 |  | 236178.903 | -121570.169 | 533304.695 | 5942461.72 | 6265309.48 | -25894.5526 | 143757.892 | 19509.7844 | 253259.119 | -58705.663 | 2298735.87 | -23799.1494 | 61656.3819 | 20.6534 | 59358.5319 | 26508.238 | 359637.657 | -6523.9069
434.12 | 11.3979 | 1.1728 |  | 241297.892 | -109653.593 | 496783.868 | 5782594.21 | 6476497.12 | -27627.3841 | 145538.361 | 23319.0379 | 246562.374 | -75211.6529 | 2386653.18 | -28301.9085 | 64775.3467 | -588.8523 | 59177.5856 | 30664.3156 | 372418.071 | -7383.4463
434.32 | 11.4111 | 1.1728 |  | 231962.096 | -104334.674 | 461171.171 | 5768279.41 | 6301565.57 | -25049.8488 | 146955.889 | 20214.5993 | 238448.744 | -49158.688 | 2371515.94 | -28402.2511 | 63134.7989 | -627.6592 | 57294.0266 | 28871.8048 | 362194.522 | -7911.8683
434.52 | 11.3593 | 1.1728 |  | 203221.302 | -96876.2527 | 430387.612 | 5489104.56 | 5570163.59 | -26765.4693 | 138900.288 | 13145.7656 | 232275.816 | 13777.3646 | 2302626.7 | -28812.237 | 61867.1667 | -954.8449 | 57081.523 | 25227.9386 | 349697.157 | -7757.2797
434.72 | 11.3209 | 1.1728 |  | 187853.54 | -100297.519 | 402232.141 | 5321027.29 | 5004998.52 | -27799.2212 | 129126.338 | 6544.2462 | 224193.858 | 116452.728 | 2139479.73 | -23166.9536 | 58944.4888 | -3950.9989 | 54853.6982 | 41785.1877 | 344162.828 | -5721.7061
434.92 | 11.334 | 1.1728 |  | 160755.512 | -96059.66 | 369527.041 | 5285893.23 | 4660172.44 | -17547.5051 | 132869.633 | 3904.4637 | 213454.738 | 129281.498 | 2169994.09 | -21085.4149 | 58010.4615 | -3732.8455 | 52270.0376 | 34783.691 | 313097.592 | -4506.9516
435.12 | 11.2663 | 1.1728 |  | 136504.833 | -135445.121 | 350061.199 | 5944956.79 | 4420349.9 | -33796.6771 | 135279.87 | 1700.9374 | 209651.106 | 57434.4309 | 2164595.06 | -27530.5884 | 57419.2438 | 109.1751 | 51783.3478 | 17081.3705 | 330752.377 | -8427.2974
435.32 | 11.2108 | 1.1728 |  | 124198.328 | -173251.732 | 337873.026 | 6858697.89 | 4195665.1 | -37371.1872 | 145841.333 | -8844.5395 | 210949.018 | 189781.372 | 2169821.73 | -28879.9482 | 51326.3474 | -1945.1063 | 53282.9977 | 24407.3969 | 284724.21 | -8347.6776
435.52 | 11.1962 | 1.1728 |  | 82679.4467 | -199291.273 | 335600.611 | 7469034.94 | 3294828.9 | -39130.5712 | 145386.763 | -23135.1297 | 209628.741 | 367280.581 | 2255511.17 | -27620.8944 | 55312.7322 | -5009.2556 | 52988.4308 | 34194.9104 | 292808.549 | -8475.9854
435.72 | 11.1581 | 1.1728 |  | 38201.2174 | -212250.614 | 333137.313 | 7894661.94 | 2374666.87 | -37508.4699 | 143315.722 | -36658.6299 | 206519.97 | 566000.043 | 2367928.08 | -26528.2187 | 63264.1238 | -10104.1568 | 52443.9725 | 60630.1696 | 352956.779 | -8703.6373
435.92 | 11.1394 | 1.1728 |  | 10616.4275 | -252683.498 | 345680.288 | 8966908.32 | 1814357.55 | -38406.89 | 148613.841 | -50787.7616 | 207662.724 | 738141.041 | 2466056.31 | -22061.7501 | 69313.1116 | -14366.3167 | 52037.751 | 78919.9672 | 377570.772 | -6005.8483
436.12 | 11.1434 | 1.1728 |  | -907.2069 | -303017.348 | 361489.209 | 10266774.9 | 1814457.87 | -64799.3907 | 166550.969 | -57891.8843 | 209271.516 | 800605.346 | 2615997.64 | -41025.8478 | 67750.404 | -13737.2671 | 52569.5752 | 77450.5078 | 365975.525 | -11376.0671
436.32 | 11.098 | 1.1728 |  | -18145.8115 | -305448.014 | 388922.45 | 10113871.9 | 1498339.22 | -64242.2414 | 160434.622 | -58051.9882 | 213426.183 | 833532.698 | 2655136.56 | -36909.2447 | 71960.1126 | -15603.9206 | 52887.4607 | 92458.9918 | 400619.726 | -9211.7778
436.52 | 11.0762 | 1.1728 |  | -47130.9852 | -270710.093 | 416703.464 | 9375815.64 | 800736.193 | -47698.3709 | 149547.949 | -61963.0234 | 216973.393 | 925809.31 | 2690966.49 | -31681.3363 | 78077.4584 | -18780.273 | 52949.9044 | 110585.921 | 449661.702 | -8516.3021
436.72 | 11.0854 | 1.1728 |  | -39805.8135 | -307023.125 | 459681.813 | 10021541.4 | 860996.821 | -58582.5814 | 154037.989 | -65343.6617 | 229465.893 | 926333.18 | 2518728.38 | -30989.2244 | 68111.0925 | -17692.0326 | 55023.0849 | 104237.898 | 387538.229 | -6120.5802
436.92 | 11.0338 | 1.1728 |  | -34089.3889 | -331516.766 | 488293.122 | 10510519.7 | 990800.007 | -68019.7921 | 156409.389 | -65990.4231 | 236137.331 | 898853.392 | 2477957.55 | -32273.1304 | 65948.0646 | -16020.7282 | 56299.631 | 90740.3101 | 368260.334 | -7846.6941
437.12 | 11.0166 | 1.1728 |  | -31701.6195 | -317905.62 | 515963.873 | 10103096.5 | 974992.006 | -56497.9929 | 153083.795 | -63169.0119 | 241443.285 | 830495.855 | 2364189.51 | -32268.0399 | 62019.6935 | -13932.8699 | 57253.5546 | 83013.1408 | 351722.522 | -9406.1703
437.32 | 11.0132 | 1.1728 |  | -10909.4093 | -300123.947 | 547259.032 | 9527103.34 | 1342880 | -37982.8533 | 144055.578 | -54557.6603 | 247255.773 | 760105.417 | 2260433.05 | -17141.5045 | 60584.5662 | -13987.0507 | 57166.64 | 82737.1183 | 345581.755 | -3767.301
437.52 | 11.0106 | 1.1728 |  | 2090.7981 | -290904.62 | 572040.763 | 9517979.54 | 1729136.49 | -36975.3578 | 152365.952 | -51073.3976 | 255117.695 | 672011.688 | 2352854.87 | -19636.287 | 61253.3928 | -10727.2369 | 59448.5681 | 62975.6618 | 341747.154 | -4687.761
437.72 | 11.0329 | 1.1728 |  | 46890.7757 | -297527.173 | 593396.486 | 9979916.76 | 2682790.83 | -47876.7172 | 172700.276 | -47393.4532 | 260624.626 | 660909.107 | 2512004.91 | -28113.3843 | 60207.6949 | -10851.9926 | 61012.5006 | 64564.2355 | 317712.835 | -6900.6278
437.92 | 11.0329 | 1.1728 |  | 74977.5406 | -293801.008 | 606590.942 | 10036930.4 | 3366832.07 | -52310.0825 | 176929.454 | -38468.7079 | 262289.765 | 557645.199 | 2640603.21 | -35171.9862 | 64805.2798 | -8782.8518 | 61196.7299 | 58213.0563 | 350423.268 | -9809.5373
438.12 | 11.0112 | 1.1728 |  | 95013.7772 | -243447.157 | 608180.736 | 8902204.21 | 3621202.5 | -43382.2297 | 166290.398 | -29313.2418 | 261106.19 | 503359.229 | 2606411 | -34966.4432 | 67471.5046 | -9314.1863 | 60855.164 | 65648.699 | 377346.435 | -11182.3157
438.32 | 11.0064 | 1.1728 |  | 122591.63 | -213178.31 | 614200.798 | 7971451.01 | 3820119.97 | -28716.0426 | 149290.664 | -22858.546 | 264033.296 | 467565.908 | 2337735.71 | -17094.3796 | 63555.0661 | -11036.8517 | 61073.9903 | 77371.4956 | 360920.232 | -2969.0782
438.52 | 11.0506 | 1.1728 |  | 144624.462 | -193540.477 | 600992.682 | 7511614.87 | 4120410.24 | -26660.2184 | 140943.142 | -16650.9003 | 259237.698 | 373613.829 | 2317386.58 | -14344.1791 | 63187.9137 | -8047.1822 | 59601.3645 | 59708.2531 | 357048.296 | -1841.5379
438.72 | 10.9883 | 1.1728 |  | 172501.35 | -169407.92 | 574830.721 | 7149689.91 | 4831964.54 | -28952.9406 | 147436.684 | -6184.9743 | 251870.92 | 270000.271 | 2442310.79 | -18567.8203 | 66956.5102 | -6773.5217 | 58527.9928 | 52874.3806 | 371732.486 | -4835.8902
438.92 | 10.9558 | 1.1728 |  | 205804.629 | -161539.163 | 550463.795 | 7117915.71 | 5560851.25 | -21513.255 | 156092.408 | 300.6855 | 246897.486 | 196026.329 | 2462042.81 | -21022.9614 | 65411.8507 | -5661.8842 | 57994.0332 | 50418.0821 | 364797.659 | -4693.492
439.12 | 10.9963 | 1.1728 |  | 238220.265 | -144137.733 | 513195.8 | 6957406.65 | 6380713.39 | -18551.9549 | 165311.388 | 8824.5745 | 236188.748 | 120545.568 | 2567637.7 | -23788.9513 | 64821.5934 | -4405.2648 | 55568.5938 | 42212.7719 | 351591.581 | -5005.6675
439.32 | 11.0111 | 1.1728 |  | 248808.058 | -145258.355 | 484784.687 | 6905872.74 | 6796462.4 | -22754.5758 | 163820.737 | 17598.5353 | 231069.645 | -54458.0201 | 2580326.41 | -24670.8747 | 67887.1095 | 204.418 | 54813.6735 | 22080.6186 | 383634.363 | -7535.2834
439.52 | 11.0131 | 1.1728 |  | 250353.333 | -129028.267 | 455816.625 | 6508132.43 | 6788297.84 | -23767.5797 | 160065.287 | 20358.4194 | 230118.608 | -25607.4324 | 2520013.05 | -25018.4044 | 65724.6898 | -2408.234 | 56302.4244 | 35314.7169 | 354567.92 | -6955.4018
439.72 | 11.0587 | 1.1728 |  | 227301.449 | -131929.578 | 430266.377 | 6325518.45 | 5968923.38 | -22444.5268 | 144701.058 | 11206.3718 | 227064.082 | 69115.9006 | 2269273.09 | -17269.3113 | 60028.6332 | -3922.8244 | 55608.5872 | 38604.8146 | 326824.142 | -3933.4136
439.92 | 11.1048 | 1.1728 |  | 198274.669 | -114643.736 | 400617.038 | 5878272.62 | 5166705.18 | -13958.6534 | 135217.549 | 2860.0504 | 217091.502 | 189505.598 | 2212805.69 | -13213.0846 | 59616.6445 | -6463.1374 | 52732.9371 | 51455.1721 | 340585.707 | -1721.9682
440.12 | 11.1209 | 1.1728 |  | 185979.441 | -129277.872 | 365149.647 | 5976830.02 | 5135060.18 | -25760.4631 | 136764.962 | 5740.8863 | 206605.527 | 74717.1945 | 2143474.5 | -23206.1509 | 57262.0705 | -2448.2837 | 50489.8991 | 35061.8362 | 332275.617 | -4494.5694
440.32 | 11.146 | 1.1728 |  | 183869.831 | -112106.378 | 345296.795 | 5428215.02 | 5338625.69 | -30412.3535 | 132820.95 | 13921.0501 | 199835.571 | 12418.5582 | 2216423.74 | -23109.0538 | 60898.6305 | -1811.2512 | 48696.7295 | 31850.6776 | 352651.806 | -7673.2675
440.52 | 11.1293 | 1.1728 |  | 157146.156 | -144395.459 | 336012.436 | 5966474.59 | 5013707.02 | -35376.2587 | 133293.004 | 11993.4303 | 205613.723 | -79263.2577 | 2147984.4 | -26167.8736 | 57340.1652 | 2636.4228 | 51436.2612 | 5397.25 | 323820.431 | -6270.6736
440.72 | 11.1413 | 1.1728 |  | 127575.042 | -156202.832 | 337272.632 | 6255365.56 | 4205416.78 | -29224.9043 | 130510.588 | -1276.1091 | 210195.626 | 161551.426 | 2191247.28 | -21737.4214 | 60658.7006 | -4242.9564 | 53151.3894 | 38896.0893 | 343632.354 | -5517.7412
440.92 | 11.146 | 1.1728 |  | 79752.0045 | -190141.936 | 328960.837 | 7394801.43 | 3173046.97 | -34053.848 | 141343.726 | -24229.127 | 207796.783 | 428174.569 | 2313844.8 | -28313.2745 | 61470.6278 | -8066.8523 | 52823.8395 | 54331.3947 | 345883.202 | -7474.9426
441.12 | 11.1422 | 1.1728 |  | 52143.172 | -234705.353 | 327595.537 | 8466251.16 | 2514979.64 | -48820.4077 | 144979.145 | -39654.8144 | 203873.488 | 620282.035 | 2365010.24 | -31102.6686 | 63512.1852 | -11719.2893 | 51461.4351 | 71301.6547 | 363265.6 | -8413.334
441.32 | 11.1629 | 1.1728 |  | 28471.5978 | -255515.941 | 330008.176 | 9039976.67 | 2288925.32 | -40864.655 | 150487.198 | -43112.8825 | 199663.275 | 663013.591 | 2465055.52 | -27868.0501 | 67198.2996 | -13077.7845 | 49638.2434 | 77478.0435 | 375128.35 | -6613.1511
441.52 | 11.1938 | 1.1728 |  | 12373.0859 | -288432.909 | 358548.825 | 9738009.3 | 2271380.45 | -45073.3798 | 160148.939 | -45175.4218 | 206473.768 | 628594.987 | 2603662.29 | -29884.4691 | 69693.3134 | -10547.9018 | 50897.842 | 64426.6725 | 393511.436 | -9058.2063
441.72 | 11.2213 | 1.1728 |  | 11274.0591 | -321798.918 | 392800.065 | 10560738.1 | 2389068.62 | -52807.4037 | 174637.6 | -50200.0256 | 220340.202 | 679871.12 | 2656967.52 | -31169.9581 | 66138.8898 | -11117.9981 | 54717.0612 | 66638.7289 | 364920.369 | -7507.3098
441.92 | 11.2574 | 1.1728 |  | -18292.7969 | -327447.188 | 435610.453 | 10865922.7 | 1722327.79 | -59575.0107 | 174938.871 | -60675.4349 | 230198.699 | 827846.856 | 2830841.45 | -34562.5502 | 74964.4795 | -14072.7707 | 56728.0136 | 79500.6068 | 413679.767 | -9347.5219
442.12 | 11.286 | 1.1728 |  | -21606.3703 | -349303.306 | 474986.851 | 11337851.9 | 1428878.13 | -78549.8031 | 175834.26 | -69109.7649 | 240439.67 | 966428.063 | 2792303.05 | -44001.4543 | 73994.8571 | -17460.7557 | 58874.8219 | 100927.386 | 419987.547 | -12115.7945
442.32 | 11.2822 | 1.1728 |  | -34006.6677 | -339089.885 | 509014.712 | 10830569.3 | 990234.638 | -76644.3725 | 160421.75 | -68213.4773 | 244835.847 | 960155.761 | 2598096.8 | -43008.2593 | 71346.2344 | -17809.0798 | 58015.2701 | 105242.036 | 404039.079 | -11826.0878
442.52 | 11.2669 | 1.1728 |  | -41559.1504 | -278946.996 | 533749.331 | 9348074.8 | 696511.809 | -38996.9622 | 147153.978 | -63495.78 | 247375.176 | 890889.933 | 2409274.66 | -23174.3092 | 65773.018 | -16669.7763 | 58213.2801 | 99288.5798 | 378947.036 | -5828.2897
442.72 | 11.2692 | 1.1728 |  | -3547.1275 | -297961.493 | 576831.02 | 9417164.64 | 1495155 | -44783.9352 | 144622.205 | -52403.5131 | 258943.838 | 715070.3 | 2208729.24 | -17124.8845 | 56753.7373 | -12011.0667 | 59619.6882 | 75124.6939 | 328013.617 | -2623.452
442.92 | 11.2697 | 1.1728 |  | 34184.4659 | -314824.774 | 601671.459 | 9936071.73 | 2470125.34 | -49780.9555 | 158562.249 | -44076.679 | 267755.395 | 539053.177 | 2279706.2 | -21510.1108 | 54741.9976 | -6493.9573 | 62138.8872 | 41848.5224 | 291764.301 | -6588.3338
443.12 | 11.2596 | 1.1728 |  | 59479.1528 | -311583.603 | 622697.685 | 10213933.8 | 3118487.15 | -53685.9323 | 170317.439 | -39762.0996 | 275944.831 | 525224.464 | 2521190.45 | -30188.4872 | 58894.696 | -6471.8461 | 65106.1401 | 43473.7325 | 309997.908 | -9206.8515
443.32 | 11.284 | 1.1728 |  | 88424.1735 | -288480.532 | 631724.648 | 10137625.6 | 3519502.73 | -41046.7 | 178513.491 | -41353.9436 | 276464.432 | 608824.955 | 2710398.13 | -26599.949 | 68536.8923 | -10198.8126 | 65486.2348 | 61126.1148 | 363730.082 | -7964.3114
443.52 | 11.3369 | 1.1728 |  | 112199.579 | -273873.272 | 637801.743 | 10102294.3 | 4069789.22 | -41154.385 | 188461.758 | -36915.4502 | 273847.382 | 606620.602 | 2880572.09 | -33264.0912 | 72275.8461 | -10949.4729 | 63750.9138 | 70523.7554 | 393211.389 | -9566.2764
443.72 | 11.3609 | 1.1728 |  | 146908.253 | -254444.831 | 630139.851 | 9659635.23 | 4735130.05 | -41303.3088 | 185683.837 | -26648.8058 | 271102.183 | 491320.739 | 2839185.66 | -33964.5181 | 72789.2143 | -9205.2807 | 63032.71 | 63087.4896 | 398954.999 | -10609.7503
443.92 | 11.3759 | 1.1728 |  | 174124.526 | -225018.965 | 624120.206 | 8623493.41 | 5151198.24 | -35037.4702 | 167976.917 | -11014.3386 | 270810.603 | 320530.859 | 2627455.98 | -24959.296 | 68961.2602 | -7371.368 | 63041.1085 | 61208.2515 | 383486.857 | -5563.1881
444.12 | 11.4003 | 1.1728 |  | 189722.415 | -167160.837 | 609271.391 | 7107578.39 | 5362403.36 | -20897.2652 | 152386.572 | 2196.5879 | 266729.691 | 183354.754 | 2481339.09 | -20364.2839 | 67586.2475 | -5715.5766 | 61425.9187 | 56318.5313 | 387061.984 | -4548.9467
444.32 | 11.3965 | 1.1728 |  | 207416.146 | -140235.436 | 585452.02 | 6293752.01 | 5658418.66 | -25554.1046 | 143447.726 | 11000.2694 | 263015.451 | 39503.6897 | 2355320.26 | -24867.2354 | 64121.3969 | -1385.1639 | 60794.7068 | 33272.0599 | 378571.119 | -6826.2746
444.52 | 11.3694 | 1.1811 |  | 229437.116 | -117884.422 | 556732.717 | 5743710.96 | 6113306.84 | -28549.5601 | 142934.074 | 19324.8014 | 259115.232 | -47471.56 | 2265557.74 | -23791.7541 | 58878.0622 | -322.0604 | 61131.7183 | 26642.9767 | 329447.593 | -4982.645
444.72 | 11.3553 | 1.3141 |  | 235389.08 | -113487.778 | 516893 | 5632220.78 | 6202872.04 | -26327.1001 | 138976.531 | 21117.4154 | 251322.457 | -80884.2291 | 2226285.84 | -19896.2073 | 60708.4554 | -239.9127 | 59645.2612 | 25268.6956 | 347296.225 | -3049.3315
444.92 | 11.3926 | 1.4346 |  | 234906.527 | -95181.4563 | 476426.973 | 5510306.88 | 6243066.66 | -25978.2216 | 143476.161 | 19698.429 | 240611.596 | -34888.3271 | 2349201.82 | -26797.6112 | 62061.0756 | -538.4073 | 57760.6889 | 26883.2349 | 357232.894 | -8306.0976
445.12 | 11.4158 | 1.4055 |  | 231769.679 | -119879.121 | 442276.324 | 5926741.25 | 6331330.42 | -26759.157 | 146719.336 | 20532.3484 | 233947.593 | -84771.9273 | 2284568.3 | -23474.583 | 59251.9162 | 663.2313 | 56297.5711 | 21455.9826 | 338882.827 | -5813.8437
445.32 | 11.473 | 1.3445 |  | 215234.427 | -116329.547 | 411186.743 | 5904971.85 | 6081686.67 | -24343.6714 | 148952.808 | 17210.5998 | 228381.538 | -57979.4086 | 2335396.32 | -27473.8378 | 60500.6127 | 733.7516 | 56096.5055 | 19786.5101 | 352348.44 | -7850.6201
445.52 | 11.5356 | 1.3547 |  | 200646.56 | -131877.752 | 391591.522 | 6098537.62 | 5827547.26 | -29306.0882 | 146487.206 | 14303.0638 | 226012.36 | -34106.469 | 2286123.62 | -25159.2558 | 58274.264 | 848.4538 | 55656.0989 | 16539.1915 | 333016.223 | -7207.7965
445.72 | 11.5198 | 1.3991 |  | 155243.04 | -142863.62 | 378670.905 | 6152496.73 | 4804068.83 | -39852.9636 | 135741.241 | 4980.1787 | 225890.239 | 36192.9999 | 2212311.74 | -29663.5048 | 59952.2051 | 319.1174 | 56366.7804 | 16229.1117 | 344188.427 | -9540.3708
445.92 | 11.5173 | 1.4368 |  | 123755.148 | -163510.89 | 367254.885 | 6485465.44 | 3887793.03 | -35287.2312 | 128660.454 | -8961.2851 | 225038.335 | 224766.887 | 2006740.63 | -24936.1313 | 54023.4244 | -4221.0526 | 56278.8985 | 39877.0287 | 323735.565 | -6937.2237
446.12 | 11.5206 | 1.4569 |  | 85010.1129 | -196852.654 | 362602.036 | 7191550.84 | 3103839.1 | -27865.1922 | 132355.852 | -22418.3078 | 221934.809 | 345428.398 | 2029446.27 | -19831.9789 | 52507.7044 | -5239.3939 | 54697.2838 | 40931.3236 | 302171.978 | -5804.7409
446.32 | 11.4723 | 1.4806 |  | 62536.6304 | -229086.516 | 355537.402 | 8042473.38 | 2810016.92 | -38069.7879 | 141730.646 | -30765.5916 | 220010.075 | 455934.347 | 2173536.61 | -25446.2382 | 56456.8862 | -7651.3417 | 55242.4557 | 51410.7697 | 321904.15 | -6913.3562
446.52 | 11.4555 | 1.4881 |  | 41633.4693 | -252741.231 | 361050.434 | 8883056.24 | 2543835.47 | -34111.7875 | 155353.5 | -41087.751 | 217839.406 | 595803.19 | 2444255.63 | -21903.8345 | 63339.3598 | -10226.0717 | 54387.3995 | 56152.8511 | 331472.959 | -6746.5915
446.72 | 11.4798 | 1.5186 |  | 36115.6411 | -309591.57 | 376401.331 | 10575165.3 | 2745510.48 | -48746.6999 | 181598.479 | -50948.262 | 223243.822 | 703460.623 | 2722984.4 | -30734.6933 | 67392.0709 | -11824.494 | 56381.0894 | 66223.8524 | 354227.739 | -7608.1765
446.92 | 11.4888 | 1.5898 |  | 18624.4463 | -357602.515 | 398272.759 | 11770946.7 | 2560834.68 | -69167.5208 | 195801.762 | -59967.3107 | 227753.172 | 747282.126 | 2817549.09 | -40838.6544 | 67085.8304 | -10620.4887 | 56422.5838 | 66144.8693 | 381327.432 | -12435.7502
447.12 | 11.5001 | 1.6798 |  | -9093.3901 | -356913.931 | 427954.224 | 11850996.9 | 1902884.79 | -62024.5047 | 190681.402 | -68171.4712 | 234764.417 | 898214.727 | 2878444.25 | -33940.7331 | 73087.3131 | -15396.2633 | 58483.3803 | 86661.4683 | 403501.434 | -8972.8917
447.32 | 11.5401 | 1.7734 |  | -23956.116 | -365271.147 | 467823.137 | 11835044.9 | 1442648.28 | -71809.4352 | 181164.909 | -72414.3626 | 241264.79 | 959261.345 | 2819567.57 | -38122.3426 | 74534.8189 | -16275.5522 | 58713.9633 | 92534.6805 | 419676.658 | -11794.9029
447.52 | 11.5348 | 1.861 |  | -23521.1076 | -363811.01 | 510902.867 | 11399510.9 | 1317571.83 | -68996.1686 | 170757.185 | -68345.7078 | 250947.167 | 904947.987 | 2601447.94 | -36113.2621 | 66107.8929 | -15006.9059 | 59733.0096 | 90335.2007 | 382078.318 | -10450.5054
447.72 | 11.5347 | 1.9569 |  | -20510.1813 | -331300.252 | 552913.58 | 10323711.2 | 1274240.08 | -51505.9778 | 154996.032 | -59608.6542 | 260390.652 | 810192.175 | 2411444.44 | -25515.3871 | 63616.9828 | -14353.0638 | 61065.293 | 88130.9876 | 365910.447 | -5757.918
447.92 | 11.5264 | 2.1196 |  | -16482.3608 | -287784.79 | 586042.667 | 9212377.23 | 1316863.62 | -44469.3877 | 142700.594 | -51085.0312 | 266772.159 | 709315.148 | 2374533.93 | -23772.6723 | 65604.9584 | -12119.5294 | 62056.4434 | 76704.1455 | 383809.368 | -7295.6965
448.12 | 11.5154 | 2.3342 |  | 19431.4279 | -275862.558 | 620920.555 | 8884639.71 | 1950041.04 | -43168.2413 | 141482.021 | -43046.9965 | 276954.252 | 643548.305 | 2282931.08 | -21309.3409 | 62469.6977 | -11746.2245 | 64158.2108 | 75891.2839 | 366741.25 | -4483.6012
448.32 | 11.5278 | 2.602 |  | 44065.8437 | -254603.695 | 642482.258 | 8685135.56 | 2515055.39 | -44671.8463 | 149680.385 | -37058.1577 | 280343.135 | 563674.361 | 2459868.6 | -29026.511 | 66735.0946 | -9480.0483 | 65106.9897 | 61663.2196 | 370441.658 | -7644.4556
448.52 | 11.5287 | 2.8808 |  | 96850.255 | -264446.22 | 654399.785 | 8935679.9 | 3706667.62 | -56698.4855 | 160061.841 | -24230.5122 | 284582.507 | 421385.688 | 2437808.68 | -36939.4864 | 61261.8607 | -6989.1244 | 65779.7128 | 55960.4979 | 348022.852 | -9317.7892
448.72 | 11.5452 | 3.1071 |  | 119496.381 | -221694.844 | 661500.588 | 8045021.95 | 4115013.11 | -47968.1812 | 153209.874 | -14620.3503 | 285328.874 | 312757.707 | 2425088.14 | -34863.5691 | 63732.0544 | -5115.1668 | 65799.5256 | 45019.6272 | 358548.586 | -9941.3416
448.92 | 11.5785 | 3.2556 |  | 137163.024 | -179872.958 | 660649.541 | 6916067.67 | 4324759.75 | -38312.9176 | 139305.724 | -4647.7757 | 285970.122 | 211429.464 | 2309008.25 | -30629.6958 | 62503.5127 | -3567.9645 | 66149.1852 | 39056.8263 | 359652.93 | -9639.4333
449.12 | 11.5826 | 3.3636 |  | 165590.394 | -157264.397 | 655057.561 | 6030112 | 4669566.77 | -48646.7865 | 123407.19 | 6933.6794 | 286463.811 | 42666.4306 | 1915278.32 | -33951.7681 | 51782.6439 | -81.0993 | 65685.2606 | 26291.7823 | 317641.793 | -10191.0722
449.32 | 11.575 | 3.4594 |  | 167695.574 | -92558.2822 | 638718.434 | 4257464.77 | 4470391.1 | -34100.0482 | 103154.79 | 15934.3558 | 283720.687 | -59600.5788 | 1649772.96 | -20318.5312 | 43590.3251 | 1635.0691 | 65121.0503 | 15749.297 | 268943.074 | -4961.8999
449.52 | 11.5474 | 3.5391 |  | 168337.094 | -48864.2513 | 615358.744 | 3130896.62 | 4327043.31 | -32150.3029 | 85787.9894 | 22265.6273 | 278191.387 | -129651.831 | 1591947.44 | -18424.1723 | 47206.4785 | 2799.3815 | 64342.7369 | 6487.7725 | 279638.893 | -5679.1212
449.72 | 11.5197 | 3.6192 |  | 201767.366 | -53448.3112 | 590429.241 | 3205891.87 | 5046563.99 | -53433.7961 | 92366.4192 | 29292.4076 | 272796.596 | -200087.78 | 1508198.22 | -30795.8313 | 38391.3282 | 4142.1574 | 63449.4992 | 729.5152 | 218599.099 | -9198.6963
449.92 | 11.5004 | 3.6989 |  | 217198.786 | -61832.1523 | 551996.825 | 3369945.5 | 5466600.21 | -46667.1385 | 96991.2271 | 33369.8357 | 265699.216 | -292422.835 | 1440577.56 | -22040.119 | 35502.0827 | 6430.5735 | 62579.203 | -13416.9165 | 201301.029 | -3235.3247
450.12 | 11.4947 | 3.8415 |  | 209537.242 | -32914.3229 | 504156.773 | 3138694.85 | 5466686 | -38856.9051 | 103366.498 | 33134.5564 | 254103.93 | -270224.523 | 1674254.42 | -26690.6881 | 42200.9406 | 5945.527 | 60986.082 | -10806.7252 | 234973.116 | -9255.7497
450.32 | 11.4734 | 4.0623 |  | 216479.732 | -61007.385 | 474918.053 | 3679850.47 | 5609502.23 | -45853.4574 | 102715.137 | 32209.6572 | 248425.031 | -243020.456 | 1644605.3 | -28300.7439 | 44267.2565 | 4338.1146 | 60042.4004 | -91.3441 | 257137.868 | -6613.3062
450.52 | 11.4737 | 4.2325 |  | 184992.594 | -58508.1077 | 429784.436 | 3665444.18 | 4962589.07 | -48300.0201 | 99255.3323 | 25184.0968 | 236122.177 | -182941.288 | 1709241.35 | -35961.6137 | 47216.251 | 4332.5801 | 57253.0071 | -552.4662 | 286467.268 | -12657.174
450.72 | 11.5032 | 4.3771 |  | 177232.58 | -80798.6949 | 401366.218 | 3867912.35 | 4740411.3 | -45417.0864 | 94706.7811 | 22808.5568 | 229949.168 | -147573.137 | 1437043.1 | -27086.8605 | 37625.5574 | 2613.1051 | 55825.4701 | 6395.2665 | 222857.572 | -7339.3196
450.92 | 11.4781 | 4.5438 |  | 134014.258 | -99087.4895 | 386945.176 | 4005264.47 | 3825226.29 | -33481.8687 | 90174.4956 | 12614.2472 | 229480.639 | -122961.504 | 1364539.34 | -17316.2666 | 35566.8601 | 4540.2664 | 56326.5549 | -8469.9334 | 210242.669 | -3810.9039
451.12 | 11.4516 | 4.6331 |  | 98419.5202 | -117831.081 | 367196.779 | 4670611.31 | 3203705.19 | -29530.2872 | 101107.581 | -216.5023 | 226980.915 | 67199.4964 | 1476743.6 | -21755.9366 | 35060.064 | 320.3764 | 56644.2821 | 10695.5763 | 189823.244 | -6223.0383
451.32 | 11.4311 | 4.6668 |  | 78143.1159 | -169946.17 | 366818.744 | 6001699.93 | 2736764.31 | -36150.3847 | 114884.644 | -17624.7149 | 226471.311 | 266161.145 | 1649793.32 | -23119.9268 | 37940.0092 | -2588.2949 | 56754.6181 | 22298.0561 | 195872.898 | -7608.2242
451.52 | 11.3831 | 4.6942 |  | 50968.8162 | -212247.693 | 359356.513 | 7285069.7 | 2404318.27 | -43366.1236 | 129067.89 | -29655.2396 | 221592.042 | 419325.536 | 1900989.42 | -28190.1267 | 45186.3893 | -5548.3075 | 55557.2472 | 35530.7202 | 233230.881 | -9781.4631
451.72 | 11.3518 | 4.6822 |  | 30451.6953 | -243426.88 | 364583.415 | 8177974.61 | 2061763.71 | -40404.0771 | 138604.59 | -40893.1754 | 220302.249 | 545376.801 | 2059867.11 | -23597.5908 | 51165.214 | -8033.8897 | 55369.9654 | 47179.3421 | 276968.157 | -7545.6698
451.92 | 11.3556 | 4.6888 |  | 14168.9771 | -274956.712 | 378393.313 | 9275430.62 | 2102978.81 | -45358.1578 | 156749.982 | -46412.2684 | 220854.481 | 626009.858 | 2379780.93 | -30329.6751 | 59615.1727 | -9779.4039 | 54919.8405 | 56468.6459 | 313889.751 | -9597.5236
452.12 | 11.3374 | 4.6751 |  | 2073.0477 | -314924.017 | 394947.564 | 10368449.7 | 2066804.68 | -61745.8982 | 172700.592 | -53993.9582 | 225774.919 | 668545.416 | 2543075.56 | -38843.4443 | 61288.9397 | -8842.3241 | 56487.4449 | 48807.8479 | 321429.599 | -12249.4664
452.32 | 11.3366 | 4.5679 |  | -3154.429 | -321830.482 | 424579.078 | 10456080.2 | 1764785.12 | -63957.7435 | 169663.568 | -59972.5362 | 230864.147 | 797195.56 | 2472460.95 | -36970.471 | 58775.2606 | -12626.0403 | 56978.3463 | 70824.3261 | 310471.14 | -11913.5133
452.52 | 11.3758 | 4.4311 |  | -28805.5089 | -334201.391 | 460503.013 | 10302526.9 | 1123935.24 | -62695.9361 | 153315.863 | -62175.2626 | 238539.38 | 778634.692 | 2296268.35 | -30670.9276 | 57841.717 | -11436.0566 | 57496.6542 | 66761.4025 | 332138.289 | -9583.3198
452.72 | 11.3461 | 4.3172 |  | -44886.1111 | -306562.837 | 492584.874 | 9310658.95 | 603825.927 | -55881.4376 | 132662.463 | -58258.5246 | 244358.648 | 788882.888 | 2203587.97 | -29258.3174 | 59895.5979 | -13136.2495 | 58404.4992 | 79232.5457 | 353205.173 | -9548.8534
452.92 | 11.3169 | 4.1261 |  | -38577.9846 | -298321.21 | 534671.286 | 8714663.97 | 508654.097 | -63007.4257 | 116079.469 | -53232.4851 | 253321.059 | 736867.258 | 1933078.95 | -32255.0181 | 54896.3125 | -12624.002 | 59290.9396 | 78295.4185 | 327343.55 | -9368.7985
453.12 | 11.3094 | 3.9166 |  | -35807.9929 | -264832.718 | 564609.171 | 7792704.76 | 557093.103 | -42206.3957 | 107961.396 | -45174.985 | 259177.175 | 606146.293 | 1746595.42 | -23772.5655 | 47732.5108 | -9563.6986 | 59937.2003 | 60929.4824 | 274735.38 | -7323.2212
453.32 | 11.2635 | 3.7363 |  | -19893.0201 | -229924.739 | 595983.577 | 7095009.46 | 870491.909 | -29942.4582 | 108147.131 | -39339.4597 | 268106.316 | 523232.456 | 1727458.8 | -15695.6019 | 46217.0682 | -7504.1116 | 62052.3769 | 49902.9615 | 274130.897 | -4151.0756
453.52 | 11.247 | 3.57 |  | 22353.6996 | -240056.765 | 622042.308 | 7495558.72 | 1748015.95 | -51517.1896 | 119055.469 | -33422.7638 | 274206.063 | 477818.201 | 1846265.32 | -28279.7773 | 48205.7765 | -6990.8207 | 63510.7395 | 48639.724 | 272981.92 | -8505.6125
453.72 | 11.257 | 3.4978 |  | 74751.2737 | -241183.595 | 636264.646 | 7834276.57 | 2955537.79 | -56265.4691 | 136698.111 | -24017.3684 | 276340.151 | 358529.573 | 1900161.48 | -36791.6162 | 42277.2414 | -4065.3226 | 63233.9584 | 35398.7543 | 231228.591 | -11115.1007
453.92 | 11.2421 | 3.4274 |  | 93970.9153 | -190002.821 | 642180.73 | 6796449.46 | 3315301.44 | -42183.9075 | 131234.445 | -14742.0015 | 277178.739 | 249378.969 | 2005509.28 | -28958.3053 | 48157.3793 | -1597.2872 | 64161.8897 | 19553.0186 | 255310.087 | -9715.6725
454.12 | 11.2487 | 3.2734 |  | 120201.543 | -146875.624 | 640136.177 | 5742010.09 | 3713571.56 | -38761.544 | 117086.006 | -2917.4975 | 275497 | 176537.449 | 1943250.21 | -26371.5359 | 52102.1725 | -2510.5798 | 63298.2142 | 30714.1042 | 301061.811 | -9434.5509
454.32 | 11.2719 | 3.1163 |  | 154456.869 | -134147.757 | 630568.649 | 5305179.3 | 4339404.7 | -44541.4989 | 111644.426 | 8104.4328 | 273217.201 | 19397.1892 | 1769982.43 | -28500.7816 | 48235.942 | 462.2279 | 62299.093 | 19354.9507 | 291828.269 | -8803.3905
454.52 | 11.2607 | 3.0074 |  | 170794.582 | -97297.8933 | 614468.549 | 4448477.84 | 4705406.63 | -34218.9718 | 107272.406 | 18547.7335 | 271578.677 | -95270.4007 | 1754410.28 | -22152.8973 | 48466.2791 | 1904.6696 | 62859.7691 | 10649.9622 | 270292.351 | -5660.0933
454.72 | 11.2432 | 2.8851 |  | 189296.168 | -80037.2425 | 588422.387 | 4095648.54 | 4964505.05 | -40506.1273 | 103296.52 | 22369.6944 | 266230.754 | -140814.971 | 1743022.79 | -27342.8176 | 49589.4947 | 3016.9337 | 61854.9701 | 5940.4906 | 292126.401 | -8694.0172
454.92 | 11.2523 | 2.7491 |  | 214879.106 | -78905.1607 | 565639.588 | 4144622.77 | 5460027.17 | -47123.2496 | 106860.507 | 26469.7048 | 261061.905 | -160406.026 | 1672919.7 | -31238.0316 | 45485.6372 | 2510.6347 | 60674.4607 | 10640.8779 | 269902.408 | -9420.0545
455.12 | 11.2543 | 2.648 |  | 219742.263 | -90853.9616 | 534380.769 | 4178314.3 | 5566821.95 | -45477.1848 | 103724.417 | 29952.4946 | 254586.629 | -267285.363 | 1537428.06 | -26510.6718 | 40418.1892 | 5684.8828 | 59534.0385 | -6156.8721 | 238376.385 | -6501.9094
455.32 | 11.247 | 2.5634 |  | 217116.226 | -60167.9602 | 499856.157 | 3701903 | 5506724.47 | -34978.5716 | 104883.397 | 29495.8883 | 247875.312 | -225406.126 | 1629701.67 | -21512.2741 | 41363.6023 | 4485.2516 | 59113.9346 | -1311.537 | 241569.342 | -5880.5687
455.52 | 11.284 | 2.5265 |  | 218453.568 | -59785.3355 | 463729.615 | 3797321.7 | 5641638.02 | -36395.9227 | 108077.654 | 30268.8638 | 237963.751 | -220908.763 | 1729061.99 | -25303.594 | 45596.0048 | 3915.7787 | 56849.4892 | 763.1485 | 257614.098 | -6915.8769
455.72 | 11.317 | 2.5413 |  | 215192.381 | -59781.2997 | 431610.77 | 3866689.39 | 5760103.48 | -46145.2024 | 111443.288 | 32155.7606 | 230820.614 | -248258.895 | 1829916.76 | -30710.6905 | 48875.9572 | 4689.6531 | 55918.378 | -2099.8623 | 280098.413 | -8616.9503
455.92 | 11.3333 | 2.5662 |  | 198648.974 | -66611.9427 | 406896.877 | 3884661.85 | 5465675.67 | -42727.0983 | 108016.574 | 29843.6289 | 226965.99 | -239589.614 | 1812504.29 | -29408.6855 | 50432.5061 | 4852.0513 | 55164.1895 | -3318.7076 | 295661.859 | -9071.7602
456.12 | 11.3582 | 2.5821 |  | 171785.024 | -91610.0782 | 385118.132 | 4332079 | 4868682.4 | -41665.9112 | 103770.2 | 21440.6403 | 225976.701 | -132379.437 | 1720043.3 | -23019.8313 | 49652.6726 | 1820.9806 | 55660.5342 | 11568.7578 | 293694.427 | -5618.1894
456.32 | 11.3859 | 2.5832 |  | 140983.192 | -130927.574 | 368765.991 | 5192473.69 | 4142989.36 | -49026.8502 | 106601.981 | 6827.933 | 223211.306 | 21837.1577 | 1647650.64 | -30962.1879 | 46256.5595 | -275.7286 | 55087.5127 | 22211.1814 | 286961.74 | -8683.0536
456.52 | 11.3961 | 2.5796 |  | 100402.179 | -160278.436 | 361535.166 | 5827805.63 | 3216779.53 | -39162.4607 | 108481.612 | -9317.8175 | 221275.874 | 185578.286 | 1689689.55 | -22068.0501 | 44478.2934 | -2025.3142 | 54647.6959 | 25160.24 | 268916.957 | -7627.1905
456.72 | 11.4073 | 2.5656 |  | 70827.6248 | -199175.473 | 353508.714 | 7087558.25 | 2891058.55 | -30005.764 | 129810.728 | -22226.6638 | 219453.37 | 306032.596 | 1852785.85 | -20587.72 | 41198.7162 | -2811.6764 | 54420.9404 | 24924.3719 | 228189.788 | -6742.8975
456.92 | 11.4261 | 2.5688 |  | 57956.9227 | -259890.584 | 367047.584 | 8436816.15 | 2774546.11 | -53783.6506 | 142562.682 | -31248.2112 | 223405.409 | 403427.508 | 1973728.55 | -30766.0963 | 45554.233 | -4918.472 | 55962.2924 | 34292.8547 | 245755.135 | -9307.6494
457.12 | 11.4263 | 2.5996 |  | 21297.8765 | -270126.092 | 378759.362 | 8845454.65 | 2188667.45 | -45707.2269 | 148124.425 | -40482.9389 | 224395.396 | 497290.468 | 2121244.28 | -30035.1303 | 50517.7079 | -5980.7079 | 55330.7259 | 41458.0498 | 291255.299 | -10187.641
457.32 | 11.4327 | 2.6602 |  | -4850.5193 | -274158.251 | 405409.352 | 8971734.65 | 1587497.95 | -47783.1277 | 146339.9 | -49762.1193 | 230440.415 | 659075.272 | 2262824.08 | -25885.159 | 58402.825 | -10211.4391 | 57385.446 | 59217.6461 | 325696.234 | -9047.453
457.52 | 11.4456 | 2.7224 |  | -14209.8057 | -309243.147 | 432139.949 | 9873427.23 | 1454110.74 | -58332.0257 | 153883.447 | -56391.3243 | 235377.889 | 744961.661 | 2349322.73 | -30690.0037 | 61139.473 | -12219.5118 | 57252.4472 | 72118.3864 | 354467.229 | -8312.6833
457.72 | 11.444 | 2.7611 |  | -21636.4764 | -334515.286 | 462725.932 | 10548012.4 | 1389732.95 | -63333.8106 | 160588.509 | -60487.8742 | 242030.747 | 789885.421 | 2467878.75 | -32927.7274 | 64220.6319 | -12789.8844 | 58780.931 | 75256.7448 | 362753.218 | -9446.3262
457.92 | 11.4551 | 2.7655 |  | -23032.9815 | -339611.824 | 491444.987 | 10870925.1 | 1432118.75 | -68265.7291 | 168675.951 | -63425.1941 | 246614.037 | 836247.908 | 2588649.44 | -39418.7858 | 66616.7073 | -13458.6931 | 59409.764 | 78751.8627 | 372693.01 | -11976.8586
458.12 | 11.4856 | 2.8153 |  | -14240.2125 | -350281.119 | 528445.52 | 10863986.7 | 1558315.59 | -73235.9258 | 162503.238 | -59185.232 | 254918.331 | 758958.735 | 2456325.17 | -40872.7375 | 63963.885 | -11514.1007 | 60285.5045 | 71624.0243 | 371503.939 | -12892.0359
458.32 | 11.4913 | 2.888 |  | -10495.6523 | -319275.407 | 565581.462 | 9835551.88 | 1515464.96 | -57648.1268 | 148324.833 | -51450.7363 | 263949.155 | 682367.803 | 2252974.99 | -33633.6781 | 59154.3164 | -10761.8991 | 61648.7592 | 68107.5755 | 342077.222 | -10133.8257
458.52 | 11.5001 | 2.9059 |  | -16483.6563 | -262852.862 | 597019.117 | 8406092.46 | 1245802.58 | -44737.4778 | 132309.26 | -46074.3351 | 271521.373 | 631059.035 | 2100924.55 | -27423.1533 | 56216.3684 | -9921.6825 | 63241.1881 | 63951.8556 | 327547.938 | -8444.0348
458.72 | 11.5242 | 2.9213 |  | 3687.065 | -233363.977 | 625671.466 | 7505777.97 | 1439286.26 | -41915.4105 | 119655.283 | -37564.827 | 278767.439 | 537269.7 | 1896728.11 | -22338.1151 | 50557.1619 | -8523.2924 | 64314.7983 | 59825.4389 | 306065.514 | -6079.0251
458.92 | 11.4935 | 2.9267 |  | 29192.8668 | -216991.974 | 654572.229 | 7033706.56 | 1833342.62 | -39088.1535 | 113284.816 | -30039.2707 | 286271.872 | 441687.538 | 1806055.56 | -19796.0092 | 48963.0507 | -6573.8868 | 65586.0701 | 49262.3735 | 297089.939 | -4609.1741
459.12 | 11.4629 | 2.8743 |  | 66673.9975 | -205898.893 | 660205.554 | 6883175.28 | 2554313.37 | -52145.8848 | 116112.989 | -21853.0477 | 286926.562 | 361836.797 | 1874750.07 | -31473.0694 | 52628.4225 | -5347.2841 | 66048.7069 | 42560.3808 | 303194.62 | -8926.0528
459.32 | 11.4647 | 2.8044 |  | 102168.738 | -166384.22 | 655635.064 | 6229193.32 | 3387108.9 | -39906.5393 | 124537.954 | -10237.7391 | 282054.535 | 259998.435 | 1999084.38 | -27198.7119 | 50572.5971 | -3564.4974 | 64240.3214 | 36018.6427 | 286982.953 | -9719.3625
459.52 | 11.4388 | 2.7509 |  | 144492.697 | -170878.942 | 652074.172 | 6343944.28 | 4334472.02 | -43670.9926 | 129789.519 | 395.169 | 283973.139 | 77552.1647 | 1984637.53 | -27894.2931 | 49858.5426 | 743.8058 | 65488.8018 | 13801.0098 | 281017.349 | -8482.6928
459.72 | 11.4368 | 2.6558 |  | 180423.172 | -134738.654 | 632644.69 | 5644268.14 | 5028576.96 | -46855.6646 | 127756.105 | 11454.8868 | 278360.575 | 12302.2961 | 1988885.13 | -31941.6052 | 50438.407 | 243.6101 | 64325.4599 | 23335.5113 | 298986.756 | -12240.8299
459.92 | 11.4495 | 2.6049 |  | 195743.551 | -106347.149 | 608928.347 | 4974750.98 | 5258111.88 | -29043.71 | 121505.132 | 18227.5419 | 274590.448 | -105694.401 | 1867925.83 | -20211.2696 | 46864.2885 | 3146.9237 | 63729.396 | 4673.3447 | 267368.032 | -5153.0653
460.12 | 11.4642 | 2.5995 |  | 209402.267 | -68609.5693 | 580078.222 | 4189001.13 | 5487366.72 | -34984.9472 | 115523.306 | 25044.2958 | 268325.48 | -131825.422 | 1897897.62 | -27182.737 | 50487.5903 | 2122.0075 | 62908.9117 | 11099.7367 | 289355.214 | -7375.0868
460.32 | 11.4659 | 2.5979 |  | 217524.328 | -55611.8956 | 544962.449 | 3772609.88 | 5626899.51 | -41964.3722 | 109445.169 | 30031.6271 | 259235.513 | -220701.495 | 1788132.54 | -29237.7771 | 48215.2986 | 4502.6041 | 60621.4256 | -158.4876 | 284552.533 | -9596.1904
460.52 | 11.4545 | 2.5459 |  | 215937.072 | -45286.5852 | 514280.631 | 3262256.17 | 5547373.2 | -45601.6403 | 98846.2321 | 34815.6493 | 254613.925 | -263903.594 | 1675065.18 | -27332.9505 | 46863.2671 | 4397.9949 | 60444.8508 | 2415.4032 | 276352.248 | -7116.9319
460.72 | 11.4461 | 2.4497 |  | 200532.448 | -22968.9132 | 479022.924 | 2597145.01 | 5034939.56 | -50311.9667 | 84984.7253 | 32984.0381 | 246410.979 | -236247.652 | 1583729.67 | -27911.2755 | 47362.3986 | 3847.7744 | 59009.2301 | 4083.9824 | 283694.078 | -8120.6714
460.92 | 11.4233 | 2.3486 |  | 184117.659 | -28690.9566 | 447816.051 | 2615136.86 | 4678967.96 | -44985.1444 | 81383.3412 | 29396.5856 | 239090.44 | -207577.175 | 1477878.04 | -26456.6823 | 44585.9767 | 3467.8596 | 57073.4883 | 5485.1055 | 278749.182 | -7371.3401
461.12 | 11.4034 | 2.2504 |  | 176663.268 | -52520.8282 | 416943.324 | 3134333.94 | 4542970.2 | -47520.2299 | 87229.6817 | 23886.3737 | 232911.808 | -170392.774 | 1406333.57 | -28928.4066 | 39087.3929 | 3381.5015 | 56645.8924 | 3321.1525 | 239594.182 | -7235.691
461.32 | 11.3801 | 2.1722 |  | 150539.285 | -57669.0497 | 390660.539 | 3284066.24 | 4119381.81 | -38550.7948 | 86739.6848 | 19079.6342 | 225130.305 | -95827.8785 | 1510719.6 | -22115.7768 | 45313.2977 | 1161.5672 | 54726.2808 | 12615.6096 | 267384.972 | -6673.4142
461.52 | 11.3958 | 2.0898 |  | 144200.233 | -103476.948 | 371024.912 | 4608801.55 | 4231734.34 | -37373.2054 | 108838.577 | 10138.0756 | 222357.9 | -41931.621 | 1628126.83 | -25840.8569 | 40487.2793 | 2026.0976 | 54900.0571 | 6049.3289 | 233665.771 | -6860.5166
461.72 | 11.4222 | 2.0512 |  | 128575.985 | -142918.856 | 359349.028 | 5681564.99 | 4230631.14 | -45853.736 | 123580.241 | 4781.4331 | 220022.588 | 33798.4571 | 1816096.64 | -34059.4156 | 44658.5073 | 225.4398 | 54722.168 | 14282.659 | 242010.641 | -9026.9549
461.92 | 11.414 | 2.0148 |  | 81026.4165 | -155956.904 | 356774.265 | 6183985.28 | 3237779.43 | -29912.3401 | 124992.649 | -11958.2934 | 221683.627 | 207726.577 | 2074204.75 | -25226.4933 | 56106.4545 | -2001.9738 | 56261.4425 | 19821.2384 | 308717.925 | -8223.6933
462.12 | 11.4275 | 1.961 |  | 55695.8829 | -201105.075 | 360270.945 | 7347405.76 | 2715859.51 | -48958.6537 | 133356.904 | -26329.235 | 220650.34 | 444429.711 | 2158967.34 | -37098.0602 | 56970.3767 | -7658.605 | 55148.4704 | 52055.8155 | 322949.579 | -12021.5291
462.32 | 11.4336 | 1.9185 |  | 23386.6911 | -240314.253 | 376343.831 | 8057671.68 | 1959611.85 | -50832.4338 | 131758.557 | -38785.0687 | 223189.582 | 551450.796 | 2100331.8 | -31135.4879 | 56260.1739 | -8964.2901 | 55451.0694 | 57217.9016 | 320893.347 | -8890.4482
462.52 | 11.4083 | 1.8589 |  | -16089.7987 | -243976.214 | 391150.474 | 8150620.22 | 1279832.63 | -51371.0092 | 129325.607 | -44745.1502 | 224078.252 | 612744.992 | 2106095.22 | -34483.4746 | 59022.3664 | -10108.1904 | 54835.5822 | 64073.6744 | 343856.83 | -11138.4814
462.72 | 11.3984 | 1.7593 |  | -23530.1171 | -260936.024 | 425466.906 | 8269608.98 | 932091.44 | -51365.9902 | 124427.554 | -50304.8961 | 232704.096 | 691712.561 | 1992429.77 | -26777.8405 | 55947.8951 | -12191.6238 | 56532.8983 | 78155.7732 | 348367.375 | -7191.1686
462.92 | 11.4079 | 1.6695 |  | -42387.1505 | -275063.484 | 459436.458 | 8625122.77 | 720587.202 | -50104.7766 | 128137.808 | -52576.4776 | 238570.749 | 694697.608 | 2051859.69 | -28445.9046 | 55659.0253 | -11144.5523 | 56638.7183 | 70234.4424 | 331052.055 | -8596.7121
463.12 | 11.4039 | 1.6147 |  | -34488.0832 | -299593.533 | 497266.07 | 9210299.3 | 894822.071 | -52770.9509 | 137280.009 | -55674.3982 | 249801.62 | 693255.409 | 2085712.46 | -26929.2166 | 53328.7594 | -9834.5477 | 59772.7925 | 59825.24 | 312590.795 | -8285.8145
463.32 | 11.4186 | 1.5796 |  | -21550.9828 | -314648.888 | 535281.541 | 9855910.9 | 1332556.46 | -52993.6241 | 155451.445 | -55887.5475 | 258746.091 | 681667.046 | 2146585.88 | -30977.2303 | 49112.4655 | -9436.2324 | 60898.2702 | 59773.6589 | 279134.232 | -9170.8009
463.52 | 11.4361 | 1.5582 |  | -13735.4662 | -317830.602 | 567479.251 | 9888725.71 | 1456363.65 | -59011.8357 | 153907.893 | -54379.6309 | 267241.959 | 663035.426 | 2196851.68 | -32411.7922 | 52285.1675 | -8642.9914 | 63327.5759 | 52817.1195 | 289731.411 | -9992.3331
463.72 | 11.4663 | 1.5339 |  | 3736.8764 | -294991.115 | 599516.88 | 9265857.04 | 1644442.72 | -58864.9374 | 140875.998 | -47340.1212 | 272023.59 | 665040.038 | 2192558.3 | -31659.164 | 58525.1269 | -11087.9025 | 63592.8502 | 68640.5398 | 327713.564 | -9904.8029
463.92 | 11.4852 | 1.4975 |  | 14398.2639 | -266513.888 | 622990.005 | 8610010.29 | 1874830.69 | -48324.4804 | 135321.69 | -39237.5427 | 275699.717 | 552381.599 | 2161193.83 | -29503.6093 | 59829.2103 | -8849.0737 | 63425.2311 | 61299.9092 | 351250.287 | -9933.913
464.12 | 11.4723 | 1.4395 |  | 43665.8379 | -257906.749 | 644049.334 | 8267213.46 | 2411556.02 | -50797.3156 | 133625.043 | -30915.1218 | 283047.759 | 454057.376 | 2055716 | -30462.3671 | 55195.4393 | -6955.0532 | 65315.0315 | 52741.3494 | 327587.595 | -8196.9813
464.32 | 11.4737 | 1.3619 |  | 67729.6254 | -223078.912 | 658792.86 | 7584056.02 | 2762207.11 | -37256.7254 | 133006.055 | -25780.1085 | 286185.866 | 413853.564 | 2088583.8 | -22530.3741 | 53811.53 | -6085.3142 | 65866.9426 | 47137.9255 | 308096.747 | -6671.6455
464.52 | 11.4892 | 1.2819 |  | 100996.466 | -201090.474 | 660107.356 | 7253475.91 | 3490529.26 | -37401.056 | 138065.03 | -16896.4664 | 285698.673 | 332797.897 | 2127119.81 | -25735.223 | 52843.0723 | -4905.3303 | 65788.5232 | 41766.6394 | 297349.104 | -7544.9615
464.72 | 11.4847 | 1.2082 |  | 128659.939 | -176010.911 | 656790.813 | 6872484.63 | 4066095.12 | -39234.0886 | 140157.501 | -8931.4607 | 284280.846 | 230022.401 | 2248845.31 | -27817.6262 | 56713.1632 | -2468.9438 | 65784.5249 | 27168.6716 | 308758.518 | -8296.5464
464.92 | 11.4851 | 1.1744 |  | 170551.514 | -163839.156 | 643533.246 | 6590597.95 | 4942193.88 | -39034.4054 | 139092.01 | 3556.5809 | 281775.638 | 128634.039 | 2197333.06 | -28940.8159 | 57690.0145 | -2785.617 | 65228.7703 | 38644.4441 | 331314.957 | -8229.2475
465.12 | 11.5123 | 1.1716 |  | 189845.968 | -118918.69 | 620871.26 | 5764773.7 | 5296961.66 | -25843.1527 | 138867.162 | 10039.1325 | 275280.383 | 32488.7998 | 2225309 | -26433.9419 | 58694.4574 | -300.0331 | 63616.208 | 22612.8525 | 335384.867 | -7877.0372
465.32 | 11.5403 | 1.1726 |  | 222195.712 | -112642.908 | 594805.214 | 5440988.24 | 5971289.07 | -33360.5533 | 133578.445 | 22176.08 | 270663.436 | -94602.0904 | 2134324.92 | -26154.4339 | 56963.84 | 1139.6742 | 62877.319 | 20256.4413 | 336242.897 | -7535.4048
465.52 | 11.5611 | 1.1728 |  | 235614.826 | -101669.839 | 563640.805 | 5217358.15 | 6291730.11 | -32681.6118 | 135083.256 | 26676.1006 | 266031.811 | -162607.837 | 2172914.79 | -23127.5732 | 56586.9883 | 3015.1592 | 62601.6138 | 6409.5077 | 317067.322 | -5992.6164
465.72 | 11.5854 | 1.1728 |  | 240645.837 | -97129.9291 | 522759.026 | 5147823.71 | 6417558.23 | -38525.7594 | 135573.295 | 28673.5694 | 258753.916 | -196338.924 | 2120738.68 | -32729.7701 | 54856.5151 | 3815.0118 | 61850.0788 | 5157.3565 | 318023.654 | -9970.4207
465.92 | 11.5832 | 1.1728 |  | 227200.434 | -80148.9412 | 488862.554 | 4584267.99 | 5970800.18 | -35923.4782 | 122592.21 | 27448.3376 | 251726.504 | -174386.5 | 1976767.04 | -26044.1666 | 54716.4516 | 2423.4868 | 60442.3312 | 12795.911 | 322483.504 | -7032.6524
466.12 | 11.5936 | 1.1728 |  | 201794.734 | -71194.3885 | 452876.464 | 4392432.22 | 5383532.07 | -25745.148 | 120852.639 | 19811.4394 | 243500.657 | -71351.6019 | 2009228.98 | -17977.1124 | 55451.9965 | 185.0848 | 58970.0516 | 23223.0368 | 329973.205 | -4804.0031
466.32 | 11.627 | 1.1728 |  | 201679.136 | -112818.73 | 423117.785 | 5303335.1 | 5482749.88 | -47319.273 | 127896.871 | 16476.1423 | 236269.257 | -57067.7893 | 1980174.21 | -32365.8491 | 51911.6323 | 1002.1625 | 57391.3747 | 18368.1412 | 313140.09 | -9070.5226
466.52 | 11.61 | 1.1728 |  | 176433.449 | -118730.503 | 399255.062 | 5338721.04 | 5093979.81 | -42470.6684 | 126804.01 | 14264.3033 | 230752.801 | -64347.6436 | 1966025.85 | -30470.4181 | 51054.3181 | 1862.7579 | 56535.1435 | 10927.7563 | 292547.312 | -8537.1946
466.72 | 11.6161 | 1.1728 |  | 151229.385 | -138671.205 | 382523.242 | 5738633.35 | 4554768.46 | -41667.247 | 124107.238 | 5913.9694 | 229222.994 | 12688.6282 | 1919029.9 | -26526.1167 | 52442.1615 | 385.3034 | 56717.6451 | 18822.2097 | 316994.368 | -7665.8704
466.92 | 11.674 | 1.1728 |  | 123451.078 | -158838.541 | 376907.823 | 6249445.79 | 4141972.99 | -32176.401 | 131434.883 | -1713.8701 | 228647.295 | 142137.378 | 2005643.46 | -25303.2707 | 51229.489 | -2758.1559 | 56513.7259 | 34374.6325 | 299170.109 | -6991.7116
467.12 | 11.6615 | 1.1728 |  | 85203.532 | -194482.735 | 372911.055 | 7117680.79 | 3357141.48 | -45841.0865 | 134030.931 | -16033.591 | 229940.978 | 240585.673 | 2099324.96 | -32686.5051 | 54155.5178 | -1950.22 | 57858.4469 | 22590.0848 | 309484.698 | -9523.668
467.32 | 11.6819 | 1.1728 |  | 59553.8801 | -198158.447 | 376720.356 | 7144305.35 | 2724922.94 | -46442.7758 | 124728.077 | -22950.9895 | 227551.054 | 450491.87 | 2164361.77 | -32126.3771 | 61368.0799 | -9431.3183 | 56836.7682 | 64814.3856 | 356098 | -9921.8014
467.52 | 11.6906 | 1.1728 |  | 13593.0355 | -212635.959 | 388266.781 | 7427610.55 | 1877048.77 | -49644.1054 | 121932.918 | -32195.7443 | 228660.02 | 481334.508 | 2197619.44 | -35044.8656 | 63547.6245 | -7755.401 | 56283.2483 | 55615.5902 | 374765.275 | -10001.8433
467.72 | 11.6728 | 1.1728 |  | -8381.7515 | -221077.591 | 412903.647 | 7516786.79 | 1411122.26 | -47898.7028 | 120873.944 | -37860.6301 | 235389.339 | 594783.497 | 2140837.45 | -33125.6325 | 63337.0534 | -11508.8825 | 57638.6433 | 76517.5497 | 379288.752 | -9696.0074
467.92 | 11.7068 | 1.1728 |  | -21653.6567 | -259450.991 | 447224.744 | 8279312.01 | 1138569.24 | -52306.835 | 128405.081 | -46138.4174 | 243780.939 | 638368.018 | 2073126.81 | -30177.3506 | 56669.5745 | -10684.0436 | 58789.4401 | 69734.9508 | 339860.043 | -8068.7572
468.12 | 11.7345 | 1.1728 |  | -33017.9097 | -280130.265 | 480435.601 | 8812833 | 1060457.78 | -56717.4465 | 133349.274 | -48437.7222 | 252330.455 | 639432.988 | 2118974.11 | -34202.9617 | 56414.1793 | -9690.2415 | 60618.0982 | 61731.3611 | 328976.172 | -10183.468
468.32 | 11.7102 | 1.1728 |  | -41887.9859 | -289846.652 | 522354.738 | 8934888.14 | 803863.278 | -55846.7794 | 132142.985 | -51995.8949 | 263969.077 | 667787.595 | 2078829.5 | -32264.4324 | 55332.7468 | -9806.0947 | 63284.1616 | 61476.5677 | 319980.747 | -9948.8796
468.52 | 11.7461 | 1.1728 |  | -34363.7031 | -293692.974 | 566207.719 | 8989724.42 | 806677.907 | -59710.7023 | 131375.733 | -54002.1515 | 273362.977 | 725103.649 | 2029221.42 | -31886.6035 | 52993.7203 | -11548.6932 | 64724.341 | 70463.6806 | 307225.317 | -9790.0346
468.72 | 11.7722 | 1.1728 |  | -18895.8737 | -290366.994 | 600980.457 | 8783728.91 | 1088569.58 | -60557.7435 | 125379.383 | -47383.0106 | 279350.853 | 645151.183 | 2001173.47 | -31767.3441 | 53768.6926 | -9912.0092 | 65221.9172 | 63480.4033 | 311123.149 | -9414.1784
468.92 | 11.7364 | 1.1728 |  | -6503.805 | -258336.474 | 632476.25 | 8178563.38 | 1389809.17 | -47121.8008 | 124693.807 | -40594.1277 | 285154.257 | 576221.64 | 2112114.18 | -29352.192 | 60154.1751 | -8969.1038 | 66156.7857 | 58310.0163 | 341423.404 | -9886.4917
469.12 | 11.7393 | 1.1728 |  | 42063.1821 | -273111.805 | 661283.477 | 8500747.33 | 2348075.04 | -61861.2168 | 134206.893 | -33289.4797 | 293449.393 | 493023.805 | 2065044.41 | -33062.5087 | 53844.5373 | -7304.2695 | 67725.4142 | 55210.5321 | 322668.386 | -10455.3067
469.32 | 11.7292 | 1.1728 |  | 65272.2496 | -265072.669 | 676343.176 | 8424840.64 | 2820705.65 | -51424.5483 | 139344.118 | -27653.7093 | 298036.565 | 400339.538 | 2070168.46 | -27418.7008 | 49347.1639 | -4683.4651 | 68921.0952 | 37629.7087 | 264965.334 | -7558.0821
469.52 | 11.7131 | 1.1728 |  | 90840.9252 | -227243.61 | 684602.974 | 7870570.91 | 3209525.75 | -38707.7681 | 144098.831 | -25586.5911 | 300050.367 | 399291.321 | 2099994.1 | -24558.3303 | 48281.1456 | -4909.6086 | 69725.9615 | 40015.7149 | 269684.13 | -7527.0811
469.72 | 11.7153 | 1.1728 |  | 119230.999 | -208694.078 | 680568.812 | 7553173.25 | 3824031.43 | -39211.4759 | 144728.759 | -16679.4555 | 295611.137 | 303929.944 | 2108658.42 | -27522.7107 | 51033.2202 | -4026.4763 | 67811.2668 | 37413.1255 | 286254.98 | -8402.8283
469.92 | 11.7198 | 1.1723 |  | 149060.014 | -182729.026 | 669283.744 | 6943421.84 | 4477612.41 | -39369.394 | 141252.331 | -4007.2798 | 292621.719 | 147498.631 | 2124979.92 | -30290.3472 | 52798.2134 | -877.4015 | 67856.706 | 23482.6079 | 294993.516 | -9838.0295
470.12 | 11.7086 | 1.1717 |  | 172920.149 | -119608.598 | 657041.748 | 5596697.21 | 4945735.95 | -32324.4657 | 134243.126 | 8910.4932 | 288818.426 | 57450.1198 | 2128185.45 | -29123.277 | 55026.912 | -945.4047 | 66597.7941 | 28503.6565 | 319599.152 | -8935.9976
470.32 | 11.7248 | 1.1714 |  | 187974.609 | -95127.2085 | 640799.931 | 4637714.11 | 5135646.05 | -45898.721 | 113858.516 | 21184.7646 | 285810.08 | -97962.3675 | 1939893.23 | -30280.0913 | 54745.9017 | 1910.5607 | 65720.5664 | 17988.2322 | 339424.89 | -9508.9975
470.52 | 11.7107 | 1.1712 |  | 202636.774 | -69239.243 | 615116.058 | 3796918.79 | 5251868.63 | -42861.7208 | 99869.4431 | 28851.7244 | 283210.564 | -178648.952 | 1731415.05 | -22527.4071 | 49434.3082 | 2671.4445 | 66146.2962 | 14116.2699 | 295821.193 | -4503.2867
470.72 | 11.6972 | 1.1711 |  | 208638.696 | -59186.284 | 574878.289 | 3641497.12 | 5281191.92 | -43444.1477 | 96777.5074 | 28678.974 | 273510.75 | -188226.442 | 1706628.21 | -25328.9244 | 50174.6616 | 3334.649 | 63824.7724 | 8592.6089 | 312397.378 | -7577.6791
470.92 | 11.6642 | 1.1701 |  | 216414.275 | -65090.9711 | 538736.691 | 3750801.87 | 5425734.58 | -50053.7074 | 102832.514 | 28362.2376 | 266353.955 | -197787.06 | 1664410.87 | -30971.67 | 44327.184 | 3981.3687 | 63058.1697 | 4563.3718 | 272106.111 | -7859.279
471.12 | 11.6423 | 1.1688 |  | 208644.523 | -52794.3231 | 490883.833 | 3531509.48 | 5292448.77 | -37929.5483 | 99739.6522 | 27900.9872 | 253518.829 | -160211.024 | 1724231.61 | -20635.1022 | 49118.4552 | 1906.4993 | 60715.3206 | 12130.8213 | 283988.695 | -5205.003
471.32 | 11.6495 | 1.1683 |  | 201924.636 | -74912.159 | 452820.164 | 4181636.89 | 5381496.33 | -40676.8083 | 113184.077 | 24537.5341 | 243852.671 | -161626.459 | 1842858.26 | -27680.8574 | 49634.4436 | 3237.4466 | 58650.4257 | 6160.981 | 296890.135 | -7884.3894
471.52 | 11.6372 | 1.1689 |  | 203260.778 | -110890.729 | 421198.954 | 5155641.13 | 5631393.76 | -44758.3845 | 131433.982 | 19946.1223 | 239070.871 | -129683.098 | 1926321.81 | -30713.9909 | 46106.3061 | 3341.6204 | 58608.4631 | 2953.4575 | 262235.032 | -8023.8816
471.72 | 11.6276 | 1.17 |  | 163097.581 | -134143.46 | 396679.838 | 5789811.29 | 4895166.19 | -41486.1019 | 131257.188 | 8964.0621 | 234173.382 | -32275.5107 | 2057412.48 | -30371.7764 | 53351.499 | 2341.2446 | 58111.5938 | 5799.6635 | 300652.829 | -10055.583
471.92 | 11.6575 | 1.1715 |  | 147442.566 | -182694.67 | 382918.491 | 6848574.45 | 4519545.8 | -41559.5885 | 133607.688 | -1737.9623 | 233358.644 | 153962.416 | 1981903.41 | -27611.3728 | 52053.5004 | -3694.8942 | 58159.394 | 40871.3898 | 311299.982 | -7080.7977
472.12 | 11.6692 | 1.1727 |  | 92293.7507 | -202086.373 | 375796.434 | 7502569.62 | 3419878.71 | -32925.8047 | 142796.714 | -21326.3708 | 229350.874 | 295309.423 | 2144740.85 | -26067.0236 | 52048.1696 | -2564.5148 | 56740.2127 | 25106.2836 | 296194.294 | -8775.9697
472.32 | 11.6627 | 1.1729 |  | 71516.2021 | -227305.251 | 373127.376 | 8226878.15 | 3047252.51 | -34454.581 | 149114.155 | -31863.8793 | 229266.93 | 497901.926 | 2304208.53 | -26013.8009 | 58757.5997 | -8672.6964 | 58252.3425 | 54241.9428 | 314874.592 | -8155.7392
472.52 | 11.665 | 1.1728 |  | 43446.6811 | -255296.72 | 378790.153 | 8858650.67 | 2610433.82 | -51251.0445 | 153024.526 | -38576.8442 | 225842.926 | 542378.893 | 2359320.89 | -34205.5255 | 61544.0548 | -8657.4436 | 55583.5353 | 57573.7522 | 352755.755 | -9832.5569
472.72 | 11.6559 | 1.1728 |  | 15291.2437 | -257552.423 | 396488.315 | 8892665.03 | 2158567.47 | -46256.5762 | 152490.823 | -42990.1971 | 229395.734 | 629291.619 | 2490308.67 | -29564.643 | 67529.0072 | -11244.4523 | 57046.0271 | 71081.5971 | 388094.36 | -8963.4421
472.92 | 11.6681 | 1.1728 |  | -668.796 | -285507.269 | 419719.4 | 9542727.8 | 1883422.68 | -59485.5739 | 156184.404 | -49016.6192 | 235921.517 | 698046.516 | 2501812.74 | -35741.738 | 66161.1035 | -12089.8346 | 57951.9451 | 78029.2312 | 386412.26 | -9619.6938
473.12 | 11.6698 | 1.1728 |  | -22076.6073 | -292234.502 | 451268.019 | 9781024.73 | 1381504.45 | -53544.3703 | 158348.635 | -57830.6781 | 243759.174 | 802691.814 | 2561214.35 | -31824.6051 | 66856.0845 | -13690.2752 | 59794.9408 | 81304.7275 | 379294.164 | -7574.868
473.32 | 11.685 | 1.1728 |  | -33800.434 | -307157.814 | 483623.423 | 10014211.9 | 1112349.03 | -59788.7426 | 154319.019 | -60935.1534 | 249360.277 | 857261.33 | 2546047.98 | -34030.7865 | 69835.2377 | -15384.8001 | 60199.753 | 92148.0368 | 403512.405 | -10070.5782
473.52 | 11.7004 | 1.1728 |  | -38266.5066 | -314332.536 | 517393.08 | 10189462.8 | 1048002.61 | -56658.0011 | 159655.135 | -63172.4477 | 256963.193 | 858967.713 | 2540366.5 | -32349.455 | 65093.1701 | -14201.1725 | 61363.128 | 83784.5439 | 369192.214 | -9090.2163
473.72 | 11.7043 | 1.1728 |  | -24704.5831 | -320605.518 | 554896.322 | 10308479.4 | 1342464.47 | -60207.888 | 163350.682 | -60665.0622 | 266487.86 | 808595.104 | 2499025.21 | -32758.041 | 61179.943 | -12477.1339 | 63373.4493 | 73393.6069 | 341867.169 | -8181.1114
473.92 | 11.7003 | 1.1728 |  | -13181.0562 | -299391.888 | 592316.863 | 9749133.07 | 1514209.25 | -61047.5095 | 154714.275 | -53825.9747 | 273241.779 | 761187.019 | 2533024.37 | -35808.5844 | 67753.7992 | -12732.1368 | 64421.307 | 78549.3984 | 387755.962 | -10079.7779
474.12 | 11.687 | 1.1728 |  | 4890.0148 | -272484.465 | 625139.216 | 9082717.19 | 1776129.83 | -56909.3251 | 149183.617 | -47218.4156 | 280010.63 | 685381.058 | 2448491.82 | -34175.3725 | 67155.747 | -11564.443 | 65031.6654 | 73892.9687 | 386888.798 | -10836.7396
474.32 | 11.6737 | 1.1728 |  | 31248.2093 | -254727.684 | 653185.308 | 8601389.72 | 2186682.22 | -49049.3252 | 142289.293 | -38918.3807 | 288112.94 | 618811.67 | 2343765.61 | -26670.2351 | 63713.0715 | -11560.7854 | 66903.5339 | 77174.3864 | 365376.624 | -6065.1685
474.52 | 11.6669 | 1.1728 |  | 59977.4545 | -238806.681 | 668346.43 | 8286838.58 | 2662922.04 | -43791.0392 | 141890.535 | -32505.9501 | 290403.263 | 512456.069 | 2268247.53 | -29120.5006 | 61371.7303 | -8883.4349 | 66655.1344 | 65733.3607 | 356432.363 | -8220.1497
474.72 | 11.6698 | 1.1728 |  | 105131.327 | -216386.25 | 672441.16 | 7725304.39 | 3590538.8 | -44836.0953 | 143386.406 | -18807.9854 | 290542.463 | 360711.267 | 2160353.03 | -31424.1814 | 54744.2321 | -6125.8237 | 66601.5158 | 52542.6896 | 320100.973 | -8044.0193
474.92 | 11.6715 | 1.1728 |  | 131602.891 | -165242.664 | 666086.534 | 6524811.8 | 4160216.35 | -28477.595 | 133352.85 | -3697.9712 | 287242.028 | 180537.616 | 2196844.83 | -20653.8923 | 61229.4347 | -3225.4155 | 65751.5316 | 36113.1139 | 349738.931 | -6262.8972
475.12 | 11.6787 | 1.1728 |  | 171502.852 | -145403.825 | 658172.96 | 6218405.52 | 5049358.92 | -27937.7885 | 143465.241 | 5564.4901 | 288439.133 | 65625.1399 | 2271025.96 | -22991.0003 | 58756.7715 | -317.4498 | 66520.9091 | 26570.7842 | 350693.36 | -7489.9043
475.32 | 11.6793 | 1.1728 |  | 216615.457 | -168205.164 | 644938.767 | 6615599.27 | 5930796.16 | -56984.2697 | 145030.497 | 15060.5522 | 289602.034 | -49525.8375 | 2104308.32 | -40826.0572 | 53182.7821 | 1535.2798 | 67166.4695 | 18298.5513 | 314811.429 | -10597.1549
475.52 | 11.6597 | 1.1728 |  | 201255.294 | -104637.961 | 612235.352 | 5114030.83 | 5396430.86 | -42492.1019 | 125980.775 | 18483.4951 | 280665.449 | -76281.2335 | 2025718.05 | -34163.1096 | 54547.5576 | 1748.5249 | 65525.7299 | 17605.1711 | 327073.762 | -10734.1779
475.72 | 11.6327 | 1.1728 |  | 205427.388 | -77269.8441 | 590001.794 | 4127781.03 | 5117749.26 | -39049.2054 | 101621.201 | 21597.0774 | 275247.261 | -61275.1889 | 1801733.98 | -23771.3852 | 54265.9688 | -416.931 | 64176.431 | 30850.9645 | 343756.864 | -6285.8259
475.92 | 11.6292 | 1.1728 |  | 203750.049 | -51695.5731 | 547069.544 | 3575572.53 | 5136364.59 | -37773.171 | 98228.5312 | 26112.6501 | 262114.249 | -130333.875 | 1760507.83 | -25868.1557 | 52428.8225 | 1323.8212 | 61094.8058 | 20377.7493 | 316301.7 | -7401.7249
476.12 | 11.6009 | 1.1728 |  | 216113.834 | -56202.7995 | 512943.52 | 3553484.86 | 5489269.25 | -40184.0253 | 99654.7489 | 31570.6545 | 255727.756 | -228719.47 | 1695521.71 | -21790.0525 | 47912.7665 | 3821.1839 | 60460.9865 | 6302.6237 | 291333.604 | -4776.8111
476.32 | 11.5885 | 1.1728 |  | 221718.491 | -63100.6138 | 475015.246 | 3890960.59 | 5830718.35 | -39093.4215 | 112761.316 | 32497.133 | 248010.251 | -259528.26 | 1759472.89 | -25571.3326 | 44908.2023 | 5130.0643 | 59261.5075 | -2745.5078 | 262613.864 | -6869.0918
476.52 | 11.6153 | 1.1728 |  | 223901.874 | -99629.7123 | 449359.853 | 4888672.11 | 6060261.63 | -40110.5821 | 130509.52 | 26984.857 | 245991.158 | -252548.951 | 1831103.35 | -31078.8602 | 41785.2196 | 6675.5089 | 59949.2382 | -14212.4421 | 235238.65 | -9077.8791
476.72 | 11.6114 | 1.1728 |  | 189917.504 | -99590.4163 | 418275.703 | 5103410.15 | 5442085.93 | -35000.2458 | 134899.147 | 17242.6642 | 239809 | -121340.648 | 1984132.93 | -31045.1183 | 46416.2495 | 4126.9706 | 59228.1027 | -3936.2677 | 256746.166 | -10079.6648
476.92 | 11.5986 | 1.1728 |  | 150483.12 | -127520.183 | 395138.873 | 5616996.01 | 4443729.27 | -36871.687 | 126883.369 | 2395.9282 | 235147.979 | 62026.2653 | 1972181.21 | -26501.0869 | 49877.8197 | 369.3399 | 58794.6302 | 14995.8228 | 289275.52 | -8966.1348
477.12 | 11.6074 | 1.1728 |  | 125993.43 | -151272.381 | 376549.073 | 6211982.18 | 3895704.12 | -33193.118 | 131305.622 | -9155.9232 | 227725.643 | 259110.756 | 1994078.99 | -24636.8329 | 48434.2871 | -4754.2798 | 56662.9485 | 39925.4636 | 269919.359 | -7445.7713
477.32 | 11.5954 | 1.1728 |  | 89030.7101 | -203311.49 | 369282.261 | 7343880.52 | 3320174.49 | -38141.631 | 139238.627 | -20736.2693 | 224961.529 | 282646.482 | 2051423.14 | -25067.1917 | 48151.9799 | -2061.8311 | 55640.9156 | 21761.6186 | 269911.798 | -8250.4495
477.52 | 11.5676 | 1.1728 |  | 69680.1648 | -245386.855 | 370123.008 | 8325578.96 | 3086472.46 | -42474.3399 | 146208.606 | -27631.9531 | 227084.891 | 390715 | 2087972.71 | -25617.0435 | 49625.6046 | -5562.5617 | 56729.4372 | 40595.5223 | 276001.107 | -7699.1848
477.72 | 11.5639 | 1.1728 |  | 29189.1943 | -273301.306 | 384115.02 | 9046834.04 | 2317208.7 | -47784.6184 | 149515.293 | -40241.706 | 229519.219 | 517300.125 | 2216121.14 | -30292.36 | 54933.8863 | -6913.4778 | 57011.8773 | 44991.1683 | 309080.124 | -9712.2247
477.92 | 11.5645 | 1.1728 |  | 7772.5332 | -297328.877 | 402101.047 | 9727705.87 | 1920162.92 | -52277.2503 | 155711.144 | -50191.05 | 233280.636 | 674034.479 | 2322877.59 | -29241.6905 | 59016.2429 | -11118.1846 | 57985.7663 | 68635.3235 | 336148.985 | -8221.4934
478.12 | 11.5742 | 1.1728 |  | -14641.7379 | -316830.256 | 426306.954 | 10473485.5 | 1501290.17 | -47385.7795 | 165521.096 | -62737.5746 | 235453.51 | 808953.402 | 2564704.82 | -25063.0704 | 68698.3378 | -13617.7788 | 57715.7102 | 75985.756 | 375657.291 | -8181.5515
478.32 | 11.5886 | 1.1728 |  | -10473.1082 | -378699.61 | 456883.565 | 12018962.3 | 1863376.44 | -77659.0433 | 186551.919 | -65916.9463 | 244858.917 | 805513.961 | 2634696.62 | -41225.278 | 63106.9117 | -11779.2743 | 59898.929 | 70781.1123 | 353099.927 | -10668.6327
478.52 | 11.5919 | 1.1728 |  | -13849.8166 | -354748.611 | 488410.157 | 11412190.7 | 1696658.52 | -66222.4542 | 178390.223 | -64080.2844 | 248823.726 | 861424.852 | 2687230.72 | -39800.7503 | 68784.8722 | -14890.7167 | 60118.2813 | 89996.772 | 389375.319 | -12069.511
478.72 | 11.5987 | 1.1728 |  | -40766.7559 | -320569.667 | 524283.588 | 10443430.5 | 1025606.44 | -54934.0438 | 162376.096 | -64943.5729 | 254910.826 | 856793.519 | 2642713.19 | -32809.0118 | 70070.2529 | -13714.1875 | 60693.2073 | 80403.6862 | 402527.777 | -9852.445
478.92 | 11.5995 | 1.1728 |  | -18564.7816 | -321697.012 | 558609.46 | 10140367.2 | 1276408.15 | -57629.1363 | 153844.216 | -59924.2241 | 264444.35 | 833045.459 | 2399405.98 | -27388.4833 | 62929.7575 | -14644.2966 | 62343.0799 | 89380.0745 | 370772.127 | -5918.0803
479.12 | 11.5858 | 1.1728 |  | -14915.9953 | -312048.594 | 590921.266 | 9997737.49 | 1423733.79 | -47471.8446 | 154366.18 | -56457.4654 | 271052.683 | 774162.372 | 2473279.27 | -23754.7458 | 66960.1466 | -13428.3769 | 63168.0451 | 77300.3523 | 374116.509 | -5492.5541
479.32 | 11.5676 | 1.1728 |  | 27274.9514 | -328931.191 | 618070.027 | 10406508.7 | 2250292.03 | -67854.9001 | 163180.928 | -50764.4759 | 279059.625 | 718051.264 | 2482811.2 | -36539.6555 | 62854.2766 | -11769.7136 | 65766.0169 | 72912.9796 | 350343.688 | -9846.9882
479.52 | 11.5612 | 1.1728 |  | 40220.335 | -288869.748 | 638623.2 | 9610724.62 | 2531825.2 | -52161.5079 | 159274.115 | -42536.337 | 280147.489 | 643595.836 | 2476411.28 | -31507.0426 | 64262.6511 | -11531.5181 | 64438.1251 | 76762.0186 | 369095.397 | -8598.2087
479.72 | 11.5587 | 1.1728 |  | 62606.5269 | -264631.308 | 650957.524 | 8962643.78 | 2866953.42 | -40879.855 | 151006.082 | -33812.7607 | 283989.184 | 538449.802 | 2444991.85 | -23191.2702 | 64221.1979 | -9486.7304 | 66099.0112 | 67178.6021 | 364720.049 | -5881.1391
479.92 | 11.5883 | 1.1728 |  | 111053.097 | -240414.572 | 663733.301 | 8602647.45 | 3774547.03 | -40685.8793 | 156020.013 | -25300.6062 | 285474.851 | 464030.753 | 2412836.17 | -27794.2912 | 61742.0676 | -8339.2512 | 65376.0345 | 61128.6523 | 353306.166 | -8110.5835
480.12 | 11.613 | 1.1728 |  | 147177.656 | -228469.012 | 657698.719 | 8295721.61 | 4632193.74 | -36160.4672 | 157466.862 | -11311.6797 | 285027.533 | 227236.942 | 2366935.07 | -27266.6209 | 60898.9733 | -2781.5889 | 65465.3612 | 34919.4946 | 351451.901 | -7778.2807
480.32 | 11.6222 | 1.1728 |  | 182490.052 | -185354.905 | 651260.419 | 7180616.42 | 5309264.78 | -31780.8085 | 146893.208 | 4933.3017 | 284771.434 | 96485.4306 | 2308982.46 | -26781.5851 | 62430.2147 | -2498.834 | 65493.4212 | 43026.2684 | 372258.811 | -8784.0549
480.52 | 11.6233 | 1.1728 |  | 203463.806 | -156244.172 | 629669.361 | 6361831.76 | 5563280.77 | -40905.9232 | 134761.874 | 13996.6493 | 282053.262 | -21846.855 | 2153282.63 | -29717.6087 | 59598.2269 | 134.7864 | 65380.7771 | 27036.849 | 351827.913 | -7992.1189
480.72 | 11.617 | 1.1728 |  | 207077.75 | -106766.009 | 600773.23 | 5055544.97 | 5460999.69 | -41734.4146 | 117652.722 | 21392.1615 | 275233.772 | -59715.2992 | 2030951.45 | -27730.7602 | 58438.0254 | -252.255 | 64105.1732 | 27486.8497 | 340661.293 | -8140.7791
480.92 | 11.5803 | 1.1728 |  | 209688.219 | -83400.3445 | 568019.099 | 4322467.02 | 5316482.67 | -40021.2403 | 106395.965 | 23607.5777 | 268443.841 | -102680.986 | 1872364.6 | -22748.1971 | 54040.6455 | 899.5256 | 62961.6024 | 21408.0039 | 326810.574 | -5852.6148
481.12 | 11.5743 | 1.1728 |  | 214482.254 | -69444.7977 | 525087.196 | 4168027.15 | 5505612.72 | -31216.6818 | 114067.306 | 25064.4473 | 257441.353 | -128320.528 | 1869790.8 | -20287.4518 | 49067.6511 | 1735.2913 | 60541.6923 | 15628.5491 | 291954.121 | -4699.6781
481.32 | 11.5573 | 1.1728 |  | 228559.472 | -95470.3358 | 493380.877 | 4832209.34 | 5941909.46 | -35809.0777 | 125455.53 | 24820.5753 | 251647.986 | -176584.654 | 1934890.69 | -20432.9985 | 47456.5663 | 4382.8443 | 60147.9221 | -982.7285 | 275742.115 | -5719.1629
481.52 | 11.5545 | 1.1713 |  | 236323.174 | -122296.917 | 460438.607 | 5621669.31 | 6340656.52 | -42690.8811 | 137812.748 | 25692.2201 | 244844.084 | -192491.286 | 2043529.63 | -33661.9419 | 52774.7421 | 3872.5055 | 59181.2289 | 2009.4334 | 297824.086 | -8959.0273
481.72 | 11.5828 | 1.1667 |  | 212066.122 | -94876.8072 | 423604.269 | 5456384.98 | 5989274.46 | -18579.1492 | 144554.237 | 19687.2644 | 236580.224 | -63363.0929 | 2337267.88 | -24417.9343 | 62273.675 | -39.9275 | 58843.9078 | 12876.9712 | 318798.92 | -7183.9277
481.92 | 11.6391 | 1.1614 |  | 192237.518 | -139899.81 | 406607.574 | 6365932.41 | 5608952.81 | -36656.3283 | 148023.165 | 10352.4999 | 233032.94 | -536.897 | 2362203.65 | -32488.2383 | 60998.1237 | 897.4575 | 57522.488 | 12003.243 | 332943.21 | -9695.9458
482.12 | 11.6612 | 1.1561 |  | 171493.565 | -156628.258 | 386144.059 | 6742993.46 | 5212694.59 | -33867.4806 | 150689.566 | 3440.0138 | 229704.984 | 119490.531 | 2346392.58 | -29548.1252 | 59142.6224 | -2680.6152 | 57402.6296 | 33887.9558 | 330445.352 | -8254.6647
482.32 | 11.6759 | 1.1509 |  | 131381.839 | -185765.772 | 373922.783 | 7331197.61 | 4325863.76 | -33059.0738 | 147808.772 | -10524.0503 | 227473.326 | 189821.867 | 2283733.32 | -26024.7418 | 57842.9327 | -1206.2812 | 56630.041 | 19866.5393 | 328345.287 | -8065.0556
482.52 | 11.6722 | 1.1455 |  | 106158.642 | -210990.613 | 373807.856 | 7739604.91 | 3731655.75 | -41142.769 | 146144.643 | -19885.186 | 228578.869 | 360921.726 | 2258384.01 | -29957.087 | 57293.158 | -6013.053 | 57473.7013 | 45494.0087 | 327448.097 | -9031.1433
482.72 | 11.6604 | 1.1545 |  | 64526.3725 | -233782.551 | 371827.392 | 8113965.82 | 2917277.99 | -44110.4329 | 142783.716 | -29051.3211 | 226608.02 | 429196.791 | 2159827.89 | -27086.6707 | 54274.1445 | -6503.3484 | 56087.1569 | 46611.3017 | 309076.552 | -7097.2604
482.92 | 11.6427 | 1.3916 |  | 29091.9389 | -256370.702 | 388160.012 | 8468455.4 | 2175994.85 | -46264.8761 | 138236.837 | -38218.2477 | 230400.169 | 531227.339 | 2221246.31 | -25863.6974 | 58208.3801 | -7900.1802 | 57714.0209 | 45514.3107 | 311450.367 | -7446.5383
483.12 | 11.6405 | 1.7421 |  | 16460.5657 | -289370.945 | 408599.023 | 9462518.42 | 2143825.27 | -49105.1279 | 155503.238 | -46284.4986 | 234810.875 | 622148.663 | 2329432.75 | -27236.1804 | 58025.4495 | -9458.6245 | 57929.7122 | 55133.2343 | 313508.773 | -8078.0716
483.32 | 11.6542 | 2.0861 |  | -6705.5268 | -317468.829 | 439543.444 | 10317710 | 1837010.61 | -55097.545 | 168963.203 | -55317.6561 | 243031.156 | 679823.48 | 2510563.57 | -31705.9828 | 61729.0992 | -9032.586 | 60225.0456 | 49665.2083 | 324847.8 | -9244.7476
483.52 | 11.689 | 2.4113 |  | -3401.2525 | -350467.01 | 479583.873 | 11056089.9 | 1899719.6 | -65707.8292 | 171367.038 | -58441.5798 | 253696.82 | 760686.673 | 2480861.12 | -37200.1245 | 62084.7053 | -12260.8981 | 61980.3215 | 73225.0455 | 349989.067 | -10122.3642
483.72 | 11.7308 | 2.701 |  | -26418.3902 | -329821.553 | 515425.93 | 10443873.3 | 1326701.4 | -66653.7683 | 159194.868 | -59284.7963 | 258626.404 | 781190.977 | 2497603.62 | -40613.4656 | 66752.6557 | -12423.1083 | 62112.2604 | 73330.765 | 373118.45 | -12561.276
483.92 | 11.7504 | 2.9706 |  | -29716.016 | -291847.549 | 560220.411 | 9154232.21 | 994053.068 | -57995.9018 | 136128.555 | -53704.1015 | 267460.826 | 780178.958 | 2343067.69 | -33374.9618 | 67222.2481 | -14249.0164 | 63577.9586 | 85112.5599 | 385478.266 | -9577.1856
484.12 | 11.7766 | 3.21 |  | -26650.1979 | -264904.91 | 596333.799 | 8354326.87 | 1013158.99 | -44930.7221 | 125976.755 | -46670.5852 | 274706.179 | 675207.815 | 2204572.38 | -24484.4132 | 61785.0914 | -11472.9695 | 63615.3407 | 73512.3561 | 363716.05 | -6225.8733
484.32 | 11.7937 | 3.4572 |  | 5423.4586 | -270596.132 | 634410.376 | 8268249.03 | 1673268.58 | -57407.7039 | 123177.116 | -35780.7567 | 287121.441 | 512869.67 | 1993143.49 | -32308.1059 | 55100.3781 | -7898.0483 | 66414.028 | 58178.0324 | 333033.902 | -8678.8303
484.52 | 11.7722 | 3.6768 |  | 27638.7572 | -254998.481 | 666254.141 | 7646117.87 | 1901437.19 | -59046.8086 | 112948.008 | -29219.5552 | 296701.891 | 429181.07 | 1819719.25 | -28363.9133 | 51210.9357 | -6292.6448 | 68412.7825 | 48549.432 | 303861.494 | -7442.4699
484.72 | 11.778 | 3.8381 |  | 35300.7824 | -215786.978 | 681626.494 | 6964885.73 | 1961305.52 | -35706.2955 | 112338.188 | -26994.8436 | 300001.375 | 404787.311 | 1817744.39 | -21255.359 | 50176.1975 | -5928.9873 | 69028.3792 | 46960.7095 | 294723.775 | -6920.0756
484.92 | 11.8141 | 4.0292 |  | 80829.2904 | -225875.769 | 694393.145 | 7514640.19 | 3056714.48 | -34023.4672 | 134868.011 | -21159.5614 | 304259.486 | 314783.582 | 1876482.35 | -22265.695 | 43862.5329 | -3623.0428 | 69494.5638 | 35539.7143 | 252065.502 | -5809.4502
485.12 | 11.7834 | 4.2551 |  | 117668.064 | -222187.008 | 694185.868 | 7571149.42 | 3878432.64 | -52832.9435 | 143343.073 | -12459.4124 | 304394.404 | 210783.593 | 2018311.09 | -34770.9188 | 44961.202 | -654.2279 | 70649.8604 | 18840.6564 | 241041.783 | -10778.2372
485.32 | 11.8064 | 4.3825 |  | 152018.551 | -172084.377 | 687143.541 | 6540918.73 | 4416776.17 | -45110.7188 | 131824.844 | -1562.5707 | 299797.208 | 173459.955 | 2016223.22 | -32301.4654 | 51455.0422 | -2796.0347 | 69462.8693 | 33923.1155 | 287607.094 | -10889.508
485.52 | 11.8437 | 4.5454 |  | 167378.929 | -132577.811 | 670515.555 | 5464373.6 | 4714802.94 | -41276.9087 | 118699.321 | 11542.7273 | 293812.01 | -27335.5189 | 1893508.84 | -27885.794 | 50879.8439 | 1843.3406 | 67020.2882 | 12985.0519 | 298371.826 | -9964.0551
485.72 | 11.8158 | 4.6824 |  | 194389.318 | -118263.837 | 658497.523 | 4955533.63 | 5233722.7 | -36022.5012 | 116554.132 | 21419.7223 | 296633.422 | -156782.084 | 1727997.34 | -22279.1543 | 43419.3766 | 3954.2084 | 68698.5966 | 4244.511 | 254406.264 | -4923.1278
485.92 | 11.8091 | 4.7487 |  | 216089.779 | -106891.534 | 623453.039 | 4789497.25 | 5550507.65 | -42949.2272 | 117119.753 | 23506.6319 | 290122.5 | -165053.359 | 1672658.21 | -26730.2791 | 39318.3359 | 4107.3965 | 68007.7841 | 370.6837 | 219302.063 | -6662.3758
486.12 | 11.81 | 4.8571 |  | 210840.438 | -77862.063 | 578820.477 | 4295908.69 | 5445632.09 | -36729.6887 | 114477.787 | 24624.8172 | 277765.62 | -177867.242 | 1735929.78 | -24735.5982 | 42377.3747 | 4570.0174 | 65337.1487 | -2985.759 | 239483.443 | -8487.2923
486.32 | 11.7758 | 4.9969 |  | 220127.076 | -91838.1232 | 541552.844 | 4392053.55 | 5569615.32 | -41282.5938 | 110040.838 | 26319.5888 | 270465.544 | -216719.163 | 1610296.48 | -21191.4041 | 39291.9806 | 5343.5405 | 64432.1405 | -6055.1913 | 228878.396 | -5263.2469
486.52 | 11.7677 | 5.1084 |  | 218170.907 | -82701.952 | 494469.36 | 4531257.6 | 5678619.82 | -32212.6452 | 118783.101 | 24689.1183 | 258841.334 | -160611.001 | 1796417.53 | -20859.3591 | 45189.0636 | 3070.345 | 62736.8256 | 3592.499 | 246508.882 | -5188.1589
486.72 | 11.7679 | 5.2544 |  | 210666.855 | -101136.25 | 455851.848 | 5063369.46 | 5772308.49 | -38443.5655 | 130003.484 | 22463.4175 | 247925.354 | -188707.386 | 1933120.73 | -33111.0713 | 48486.3505 | 5204.3238 | 59826.5953 | -6058.9924 | 280620.189 | -11934.5299
486.92 | 11.7233 | 5.4026 |  | 191782.433 | -121189.054 | 429227.376 | 5412262.38 | 5442245.97 | -40060.1892 | 129409.933 | 17790.9184 | 244635.983 | -121037.175 | 1947655.43 | -26495.2393 | 48810.35 | 3530.5446 | 60223.1484 | 731.3742 | 280409.426 | -8107.1954
487.12 | 11.7235 | 5.5063 |  | 153126.802 | -126637.022 | 402179.674 | 5622231.47 | 4525241.59 | -40634.3202 | 125757.955 | 4615.7148 | 237798.218 | 47483.7838 | 1980749.2 | -31048.4981 | 51598.9045 | 291.2278 | 59324.5072 | 14813.5761 | 288194.995 | -11725.8628
487.32 | 11.7419 | 5.7046 |  | 132444.051 | -159317.798 | 391288.933 | 5992114.05 | 3930245.71 | -38298.2399 | 114086.006 | -1723.4331 | 234022.975 | 129289.759 | 1723848.37 | -25183.5789 | 47247.4712 | -2580.9475 | 57446.6401 | 33977.9357 | 290429.8 | -6202.8626
487.52 | 11.7048 | 5.9603 |  | 77757.2254 | -158130.887 | 380081.885 | 5908459.92 | 2937096.5 | -26699.7532 | 109508.673 | -10283.1117 | 230421.444 | 197447.568 | 1825336.9 | -20835.0259 | 52315.6441 | -2753.7677 | 56964.296 | 28661.825 | 303107.975 | -6139.3421
487.72 | 11.6854 | 6.1227 |  | 66911.9868 | -193604.886 | 375612.475 | 6568583.5 | 2711637.24 | -50858.0636 | 113516.781 | -16904.159 | 229089.367 | 282957.713 | 1716074.59 | -36832.7756 | 43975.0831 | -3811.4589 | 56701.083 | 33992.532 | 256979.303 | -12987.1675
487.92 | 11.6868 | 6.2995 |  | 43855.6142 | -202547.917 | 388270.609 | 6297113.88 | 2082092.19 | -51965.2669 | 100279.799 | -20477.032 | 230458.418 | 303743.993 | 1469290.75 | -30727.9211 | 36913.5785 | -3849.7828 | 56313.1071 | 31544.5981 | 213825.791 | -8618.7642
488.12 | 11.6356 | 6.4896 |  | -19313.9231 | -174896.169 | 398710.946 | 5465917.33 | 827149.145 | -36883.9585 | 82337.5459 | -25044.1254 | 233472.806 | 315474.447 | 1420165.09 | -24018.3999 | 40240.4271 | -2972.4781 | 57397.1751 | 25404.525 | 236109.571 | -8892.9312
488.32 | 11.6258 | 6.6062 |  | -18746.4111 | -210185.52 | 433803.783 | 6029802.78 | 638036.79 | -38091.6299 | 79799.6782 | -32426.7111 | 244734.738 | 452613.037 | 1301269.09 | -20218.2893 | 38806.829 | -7330.1857 | 59687.1056 | 48133.7073 | 231197.4 | -5688.687
488.52 | 11.6369 | 6.7835 |  | -38398.9423 | -232523.034 | 461668.402 | 6849566.33 | 490428.093 | -48519.004 | 100950.914 | -40349.8559 | 249367.111 | 495559.876 | 1418375.98 | -35157.8608 | 33946.5108 | -6064.5591 | 59607.8963 | 39797.5274 | 190216.416 | -11071.3577
488.72 | 11.591 | 6.9491 |  | -61615.8841 | -226349.9 | 494408.494 | 6535952.97 | -167237.078 | -58276.2206 | 89791.6814 | -45550.0419 | 257012.669 | 564659.073 | 1456204.94 | -41178.6852 | 38879.0057 | -6898.788 | 62178.7614 | 41786.4871 | 215903.341 | -15677.2401
488.92 | 11.5716 | 6.9554 |  | -73677.4406 | -201555.918 | 529979.991 | 5629498.65 | -724161.775 | -46181.347 | 70194.2623 | -45646.6967 | 260947.324 | 626804.431 | 1201778.18 | -31153.8935 | 34227.1177 | -10012.3904 | 61482.516 | 60657.9322 | 197303.647 | -11820.8433
489.12 | 11.6013 | 6.9664 |  | -78061.3191 | -171111.684 | 567866.193 | 4665256.06 | -949986.944 | -35035.8012 | 57090.1686 | -40826.4305 | 267578.032 | 527848.37 | 1018958.27 | -23822.7904 | 29793.2697 | -7097.1286 | 62061.8371 | 44611.178 | 185263.82 | -8091.2058
489.32 | 11.5534 | 7.0682 |  | -55305.9441 | -164896.865 | 606837.651 | 4403405.34 | -364918.887 | -33134.8019 | 57551.0246 | -29857.406 | 277810.224 | 364186.292 | 896091.406 | -18412.576 | 25423.2036 | -3725.0804 | 63648.098 | 30287.1932 | 164984.382 | -4939.3836
489.52 | 11.4903 | 6.9948 |  | -24811.4136 | -171134.682 | 638797.118 | 4755521.75 | 307743.263 | -54790.8383 | 68305.7278 | -25545.3067 | 287844.413 | 329961.228 | 994469.786 | -37130.065 | 23982.811 | -3051.0667 | 66460.8621 | 26944.7994 | 123381.811 | -13179.809
489.72 | 11.4816 | 6.8327 |  | 11208.6006 | -169737.567 | 657037.843 | 4594690.15 | 743889.717 | -60318.8773 | 60019.8371 | -21370.0311 | 289782.039 | 337740.686 | 848186.982 | -33515.1131 | 20050.2838 | -4763.859 | 66614.5473 | 37888.4487 | 115613.515 | -11117.3361
489.92 | 11.4364 | 6.7705 |  | 4372.1632 | -115055.787 | 666217.963 | 3480375.83 | 515191.168 | -31410.4784 | 49172.0613 | -16993.0225 | 289195.29 | 252301.589 | 917593.253 | -21144.8083 | 27633.8922 | -2049.5694 | 66034.9093 | 22504.7446 | 160837.316 | -9639.3406
490.12 | 11.3777 | 6.656 |  | 56928.2319 | -114296.48 | 664589.814 | 3596611.76 | 1724325.96 | -45922.2047 | 61821.0104 | -5342.4218 | 287072.445 | 154920.856 | 902421.496 | -27339.7257 | 22869.8368 | -1646.5332 | 65168.4551 | 23984.8022 | 133552.695 | -8503.2395
490.32 | 11.3693 | 6.5119 |  | 97687.5661 | -93845.9751 | 661325.98 | 3377996.03 | 2661919.23 | -53504.4846 | 70008.0132 | 5383.2932 | 285281.548 | 3341.8719 | 1025646.36 | -26473.5908 | 23690.5264 | 2211.6168 | 65068.9367 | 3439.6798 | 122015.905 | -8060.5472
490.52 | 11.3482 | 6.467 |  | 135096.972 | -87939.1181 | 650489.836 | 3315104.17 | 3669906.52 | -63056.6314 | 78530.6236 | 19086.3276 | 282890.425 | -163978.888 | 1053517.95 | -35792.815 | 23652.2733 | 5043.5472 | 64377.8195 | -7764.908 | 131322.956 | -10474.7711
490.72 | 11.3449 | 6.4217 |  | 156568.454 | -64374.4847 | 637753.743 | 3008901.81 | 4070253.67 | -50343.2117 | 75734.0412 | 24349.7264 | 283794.704 | -215898.096 | 1151836.82 | -26155.1725 | 30420.9152 | 5609.0862 | 65961.9684 | -10555.507 | 173385.933 | -7914.8045
490.92 | 11.3521 | 6.3845 |  | 179013.459 | -67534.54 | 614439.527 | 3221121.88 | 4528579.73 | -56885.6488 | 80593.4971 | 26876.9343 | 277734.441 | -215149.883 | 1251180.21 | -32194.6745 | 33443.0926 | 5068.1102 | 64029.1007 | -5689.5461 | 201362.695 | -10857.6631
491.12 | 11.3351 | 6.3439 |  | 193073.602 | -59345.3422 | 586253.365 | 3327873.88 | 4789902.32 | -47828.0208 | 90619.9442 | 25236.0638 | 272133.937 | -193253.338 | 1331677.46 | -25645.7628 | 31477.6177 | 4727.1077 | 63938.7531 | -5950.5331 | 172653.038 | -6513.5043
491.32 | 11.3183 | 6.2344 |  | 204530.718 | -64423.7454 | 541127.261 | 3618503.05 | 5124737.2 | -49112.0963 | 99985.0756 | 26168.0839 | 258563.784 | -212138.873 | 1430736.93 | -30809.1435 | 32781.5496 | 5359.7944 | 60480.1671 | -9279.3035 | 180657.005 | -9640.3054
491.52 | 11.2832 | 6.0874 |  | 211773.38 | -67796.5778 | 504869.365 | 3734087.13 | 5293038.93 | -41346.1633 | 101988.057 | 27055.78 | 250597.896 | -239544.05 | 1469972.66 | -21255.3237 | 34649.0827 | 5945.1066 | 59586.2492 | -11881.7733 | 194520.837 | -6127.2049
491.72 | 11.254 | 5.8822 |  | 215665.54 | -85007.9419 | 464430.195 | 4303009.65 | 5551234.3 | -41194.8002 | 112890.661 | 25893.1923 | 241368.225 | -204624.925 | 1671031.17 | -22583.2936 | 40683.5627 | 4607.7886 | 58328.8419 | -6627.8236 | 216513.824 | -6181.2476
491.92 | 11.2449 | 5.6713 |  | 214709.975 | -111437.59 | 421696.957 | 5223501.37 | 5767965.07 | -46325.2583 | 128258.213 | 21892.0383 | 230343.501 | -166676.012 | 1863532.08 | -32231.1962 | 44858.1997 | 4209.3769 | 56184.7768 | -2826.6093 | 249873.746 | -10530.5517
492.12 | 11.2159 | 5.5226 |  | 189392.34 | -123498.842 | 383115.012 | 5692885.45 | 5434489.69 | -37130.8677 | 136204.865 | 15232.6091 | 220759.639 | -98534.3413 | 1987075.49 | -29835.174 | 47133.0628 | 3215.1166 | 54486.3271 | 802.0892 | 258586.446 | -10001.8192
492.32 | 11.1934 | 5.3207 |  | 159676.893 | -145834.308 | 362396.089 | 6201574.27 | 4659320.78 | -30656.1803 | 134724.292 | 394.1016 | 217613.449 | 83387.104 | 2036959.71 | -22590.2653 | 51006.2683 | -492.8717 | 54704.2934 | 14722.8606 | 278088.4 | -7624.9172
492.52 | 11.2276 | 5.1272 |  | 139389.339 | -177796.553 | 341025.633 | 7115814.82 | 4297773.72 | -24641.9763 | 143505.362 | -10533.4337 | 210866.975 | 236075.395 | 2073171.02 | -21113.0476 | 49966.4069 | -4428.6177 | 52630.4724 | 37931.6158 | 274638.456 | -4485.4821
492.72 | 11.2522 | 5.0635 |  | 100953.858 | -203212.503 | 332248.387 | 7780977.1 | 3740543.14 | -26349.3525 | 153648.401 | -20966.428 | 206266.183 | 280416.609 | 2283999.45 | -28061.4713 | 53866.808 | -2098.7738 | 51724.7297 | 21542.2466 | 290609.903 | -11161.4252
492.92 | 11.2376 | 4.9736 |  | 82815.0037 | -221839.752 | 327483.225 | 8172053.56 | 3509971.19 | -39374.0044 | 154613.932 | -24412.1276 | 207317.944 | 380517.114 | 2306754.81 | -31191.8253 | 57110.8914 | -6070.3564 | 52951.8995 | 41990.906 | 311556.081 | -8954.4367
493.12 | 11.258 | 4.8105 |  | 40666.1179 | -213585.654 | 342222.661 | 7690855.65 | 2445695 | -42581.6904 | 137066.211 | -32205.4348 | 207775.666 | 481924.392 | 2250245.23 | -33250.6002 | 58966.1129 | -7293.1636 | 51949.3387 | 46793.6892 | 326755.158 | -12003.861
493.32 | 11.2571 | 4.7149 |  | 3448.3384 | -214036.668 | 358868.943 | 7190441.49 | 1565219.79 | -49492.2304 | 116434.739 | -34339.6806 | 211259.039 | 505496.134 | 1980427.9 | -33153.9988 | 54432.4475 | -8033.4848 | 51849.2359 | 52937.4967 | 314655.922 | -11542.287
493.52 | 11.2387 | 4.5947 |  | -24293.1311 | -209029.329 | 388558.845 | 6646948.23 | 777278.11 | -31800.4136 | 103822.645 | -39317.4746 | 220606.05 | 538753.318 | 1719271.26 | -18153.4477 | 46526.9404 | -8523.3077 | 54010.0286 | 54720.7016 | 273928.041 | -4554.9862
493.72 | 11.228 | 4.4324 |  | -44271.6031 | -211016.359 | 410846.33 | 6692113.42 | 393756.981 | -39538.7467 | 104552.092 | -43306.7121 | 224949.85 | 570420.022 | 1684053.76 | -27370.5216 | 44353.3342 | -8459.7214 | 54297.5839 | 51821.8376 | 255559.868 | -8303.6182
493.92 | 11.2212 | 4.2821 |  | -48911.6156 | -229814.1 | 444534.707 | 6816300.82 | 270127.843 | -53168.0619 | 98740.4291 | -43339.3028 | 233424.212 | 565639.163 | 1611557.89 | -32925.7233 | 43219.997 | -8070.2567 | 56127.6271 | 49837.7181 | 252145.376 | -10369.6232
494.12 | 11.2179 | 4.1359 |  | -65555.9826 | -206005.082 | 477231.381 | 6203069.33 | -127017.983 | -44517.8291 | 87124.7435 | -42468.1725 | 240121.125 | 561321.407 | 1535846.52 | -31719.0069 | 44904.9388 | -8221.7857 | 57028.8091 | 51386.721 | 261094.304 | -11319.0647
494.32 | 11.2402 | 4.0028 |  | -72135.7444 | -185540.533 | 511933.668 | 5565802.26 | -398009.491 | -33794.5381 | 75470.9872 | -40945.1199 | 248549.069 | 565856.211 | 1465970.09 | -22698.8376 | 45768.6846 | -9094.2426 | 58638.8291 | 56698.8631 | 272990.311 | -7675.1061
494.52 | 11.266 | 3.9307 |  | -60345.5088 | -186241.95 | 555893.22 | 5555119.81 | -179572.497 | -38942.9188 | 75804.6587 | -37822.8975 | 258798.125 | 507208.651 | 1379274.36 | -26357.2622 | 41763.7492 | -7238.4982 | 59867.5421 | 49558.105 | 261002.202 | -9316.6264
494.72 | 11.2711 | 3.8717 |  | -35572.3326 | -186848.633 | 591214.616 | 5614828.26 | 353173.623 | -41510.2877 | 86458.3768 | -33280.6774 | 268746.2 | 455093.451 | 1369417.36 | -27955.5583 | 34774.4071 | -6105.2572 | 62166.6455 | 43639.8334 | 209939.167 | -8481.9195
494.92 | 11.2821 | 3.7671 |  | -12469.4741 | -175898.523 | 618985.975 | 5486491.15 | 758279.909 | -47803.1425 | 89433.647 | -29593.9071 | 275019.254 | 400074.872 | 1401618.06 | -31567.3541 | 34062.5351 | -4336.6712 | 63497.0158 | 33135.4569 | 196253.903 | -11038.859
495.12 | 11.2623 | 3.6865 |  | 17634.5595 | -159162.017 | 638594.85 | 4989039.39 | 1240973.59 | -49893.8872 | 80521.3478 | -20408.7398 | 278563.819 | 321520.995 | 1301541.62 | -31073.6088 | 35139.8026 | -4038.0443 | 63798.0044 | 34876.0352 | 209082.022 | -10174.4521
495.32 | 11.2706 | 3.5701 |  | 34807.5841 | -110568.421 | 647915.984 | 3901993.77 | 1513364.88 | -39143.4601 | 70140.1492 | -10288.1464 | 278775.449 | 220843.854 | 1285680.53 | -24352.9604 | 38559.5568 | -2764.9432 | 63607.1067 | 29832.7766 | 230309.043 | -9362.4055
495.52 | 11.2677 | 3.4725 |  | 77261.9598 | -99919.533 | 649243.223 | 3660324.72 | 2410970.47 | -42962.8 | 73889.7217 | 1285.2372 | 279501.431 | 69602.8596 | 1207565.8 | -24303.008 | 32933.0945 | 247.4907 | 63545.2776 | 16450.3114 | 201617.391 | -7087.6455
495.72 | 11.2722 | 3.3766 |  | 132546.684 | -107836.879 | 647718.822 | 3961905.53 | 3588721.77 | -56868.5428 | 83723.1489 | 12078.9681 | 280693.081 | -64016.9185 | 1187296.42 | -25778.2526 | 27442.6855 | 2973.0955 | 63909.344 | 1529.6586 | 151936.287 | -7016.5076
495.92 | 11.2867 | 3.2936 |  | 164014.367 | -103551.065 | 634408.397 | 4140570.25 | 4409164.97 | -47427.1956 | 98715.7409 | 18710.2105 | 280101.216 | -174683.395 | 1299387.2 | -26175.1881 | 27165.2814 | 5698.1898 | 64403.5807 | -11276.6233 | 136775.952 | -7501.6095
496.12 | 11.3247 | 3.2437 |  | 189778.121 | -99867.3263 | 620328.062 | 4332284.39 | 4975140.38 | -43931.0705 | 106085.519 | 22579.8024 | 279013.694 | -200811.843 | 1440595.35 | -26921.3682 | 31614.3977 | 5720.2747 | 64779.8996 | -11101.8037 | 166277.003 | -8753.7632
496.32 | 11.3641 | 3.245 |  | 216777.741 | -109429.065 | 592360.033 | 4799756.14 | 5580813.23 | -43333.0607 | 117660.957 | 24208.7333 | 273359.184 | -208339.931 | 1563117.89 | -29016.5352 | 33842.1657 | 5589.2516 | 63869.6273 | -10178.3794 | 178415.105 | -8353.6465
496.52 | 11.3985 | 3.2673 |  | 222420.114 | -96532.3508 | 561455.944 | 4779552.55 | 5792890.7 | -34543.1789 | 125390.515 | 24323.0738 | 266105.1 | -196069.813 | 1784560.41 | -26901.7608 | 40553.8428 | 5374.6929 | 63034.4092 | -10250.3479 | 208317.38 | -8447.4958
496.72 | 11.4247 | 3.282 |  | 231262.759 | -96670.6938 | 526735.729 | 4822112.04 | 5986300.3 | -38433.6179 | 124585.624 | 26604.8605 | 256933.831 | -205370.498 | 1813922.84 | -26549.714 | 42903.9024 | 4943.3426 | 60774.9559 | -3937.9084 | 245155.437 | -9374.0397
496.92 | 11.4139 | 3.2814 |  | 222638.809 | -94130.5839 | 492974.317 | 4827247.19 | 5834294.46 | -29437.0889 | 125885.848 | 24099.1572 | 250872.182 | -162029.879 | 1939936.97 | -17296.4045 | 47488.4052 | 3834.7381 | 60504.3325 | -3235.4925 | 255812.212 | -4443.4377
497.12 | 11.411 | 3.2147 |  | 229231.419 | -128358.148 | 460199.458 | 5709393.39 | 5991830.95 | -42973.5463 | 133268.88 | 19768.9924 | 242925.767 | -105503.469 | 2001190.49 | -26203.7649 | 50702.8696 | 2115.0049 | 58810.4636 | 10147.0333 | 292507.856 | -7894.1009
497.32 | 11.4199 | 3.1615 |  | 217786.533 | -139805.98 | 422889.67 | 6349966.58 | 5971234.15 | -28977.3907 | 150650.745 | 12817.8603 | 233858.558 | -12165.0802 | 2237673.46 | -20199.0361 | 56246.0366 | -568.6676 | 57240.9972 | 20348.5203 | 301782.449 | -5028.9174
497.52 | 11.4362 | 3.1478 |  | 199596.304 | -174649.108 | 388352.673 | 7532867.69 | 5827880.88 | -31741.7671 | 167440.896 | 2007.0213 | 225261.869 | 68938.8886 | 2485970.75 | -30621.8915 | 61204.6386 | 3.9768 | 56398.7021 | 16126.1409 | 338388.175 | -10260.0859
497.72 | 11.4299 | 3.1517 |  | 180305.286 | -207738.267 | 366093.3 | 8256199.64 | 5479504.12 | -34458.6824 | 171599.513 | -5797.0371 | 220399.886 | 182242.95 | 2505698.5 | -28486.7857 | 60963.4332 | -2989.3233 | 55236.3607 | 33833.2436 | 338585.642 | -7984.9853
497.92 | 11.4691 | 3.1547 |  | 139889.162 | -216796.667 | 349329.934 | 8579450.4 | 4612743.29 | -34391.6915 | 167325.221 | -18477.4824 | 216042.249 | 354017.849 | 2633896.94 | -28449.5828 | 67649.6891 | -6400.6395 | 55074.2379 | 45615.9028 | 367483.091 | -7846.2505
498.12 | 11.5312 | 3.2699 |  | 100974.275 | -230165.547 | 347383.087 | 8750678.72 | 3846637.15 | -25660.2455 | 160468.272 | -26401.417 | 213618.094 | 474997.002 | 2608033.41 | -21508.9375 | 72120.775 | -10568.6775 | 53257.2941 | 70969.9537 | 417080.541 | -6718.8921
498.32 | 11.5661 | 3.438 |  | 68375.467 | -255748.796 | 358774.37 | 9366456.13 | 3257527.55 | -37988.8678 | 168437.132 | -37582.8349 | 219657.382 | 587852.991 | 2639134.77 | -29236.0799 | 69769.4456 | -11647.1359 | 55417.4626 | 75407.2092 | 397392.892 | -5436.7947
498.52 | 11.5921 | 3.5357 |  | 29058.0454 | -260077.993 | 371717.371 | 9248679.18 | 2462994.25 | -54519.3676 | 159176.421 | -42506.0565 | 219254.904 | 633760.321 | 2599404.02 | -43674.9952 | 70572.0209 | -11107.3725 | 54350.8079 | 73321.9835 | 404576.588 | -14352.2502
498.72 | 11.5914 | 3.5797 |  | 317.739 | -256046.331 | 403342.52 | 8372246.04 | 1634343.06 | -55332.7073 | 133150.825 | -42053.7864 | 228447.364 | 608873.534 | 2204389.53 | -36069.7319 | 62709.0304 | -10753.5502 | 56162.2719 | 71314.2249 | 367455.009 | -10544.3535
498.92 | 11.5976 | 3.5812 |  | -35115.2451 | -228326.795 | 436119.674 | 7211988.23 | 717758.188 | -38090.3812 | 110106.96 | -41811.1407 | 235915.128 | 574057.106 | 1867642.06 | -24903.5429 | 53459.3039 | -9336.774 | 56382.7464 | 63226.5766 | 328221.785 | -7347.0568
499.12 | 11.593 | 3.6077 |  | -45239.1277 | -229776.178 | 479663.35 | 6799370.24 | 326458.732 | -40589.6341 | 97963.0445 | -42468.4811 | 249995.043 | 563358.473 | 1656775.43 | -23832.6304 | 46255.703 | -8367.7598 | 59897.6092 | 54005.3693 | 278166.333 | -5769.8525
499.32 | 11.5891 | 3.6195 |  | -61347.8913 | -214306.564 | 510597.861 | 6594184.5 | 91334.5796 | -34688.7186 | 101659.391 | -44047.2264 | 257601.17 | 584870.152 | 1683930.4 | -25254.4064 | 44329.8856 | -8488.8534 | 61236.0598 | 52100.5994 | 251214.131 | -7016.062
499.52 | 11.6067 | 3.6569 |  | -59257.0356 | -220965.036 | 546319.611 | 6554118.93 | 1945.6028 | -54219.34 | 93712.2508 | -43658.1873 | 266665.067 | 573668.568 | 1595567.04 | -35610.2361 | 44350.6762 | -7940.5788 | 63159.0807 | 52195.3045 | 269816.257 | -11074.4212
499.72 | 11.634 | 3.7503 |  | -60909.1885 | -184929.047 | 576856.771 | 5699763.6 | -162266.964 | -35563.9735 | 82613.1608 | -40375.5369 | 271587.928 | 585830.542 | 1543756.32 | -23076.1518 | 47725.6908 | -9988.4248 | 63421.1425 | 65005.9563 | 288847.217 | -8037.2584
499.92 | 11.6948 | 3.914 |  | -30315.0187 | -208452.46 | 617881.888 | 6142526.64 | 552211.404 | -45737.9098 | 90024.6897 | -33965.8628 | 282096.015 | 446871.108 | 1424458.61 | -27270.6198 | 38523.049 | -5546.9733 | 64645.6282 | 43134.401 | 246999.788 | -8643.6991
500.12 | 11.7247 | 4.1526 |  | 3915.5704 | -202658.428 | 648665.194 | 6043769.59 | 1380183.36 | -53343.5559 | 99487.7395 | -23430.2456 | 291412.206 | 324430.9 | 1432423.57 | -32898.7909 | 33107.8041 | -3192.4619 | 67037.9238 | 30339.2821 | 190831.65 | -10470.1388
500.32 | 11.7296 | 4.3155 |  | 21699.0464 | -183945.211 | 680881.292 | 5454938.31 | 1510119.17 | -54697.9075 | 88370.1479 | -18145.9272 | 302054.29 | 245176.731 | 1268976.04 | -31897.2938 | 30815.8648 | -1302.477 | 69880.5273 | 20291.5836 | 175260.847 | -10147.8754
500.52 | 11.7427 | 4.403 |  | 32526.2969 | -132769.708 | 691084.889 | 4356325.26 | 1453176.18 | -35040.2007 | 75342.6925 | -14257.645 | 303559.65 | 264118.255 | 1261118.06 | -22452.5024 | 35643.2958 | -3330.9105 | 69839.6691 | 32202.9925 | 213766.106 | -8038.3953
500.72 | 11.7646 | 4.5067 |  | 71123.983 | -120571.811 | 694628.306 | 4216242.53 | 2227282.98 | -43866.2011 | 79329.1986 | -5474.395 | 301746.579 | 164727.609 | 1262132.32 | -27377.8085 | 33675.4588 | -1568.6205 | 68753.3782 | 25207.5738 | 199373.852 | -8634.264
500.92 | 11.7692 | 4.6236 |  | 134843.58 | -139727.398 | 690592.569 | 4758171.76 | 3702749.32 | -48329.9763 | 96204.1001 | 7484.4446 | 301900.879 | -22416.2082 | 1261930.11 | -25329.7909 | 27764.7255 | 2380.0858 | 68667.9658 | 5838.7898 | 151973.485 | -5403.2156
501.12 | 11.7696 | 4.6872 |  | 170459.843 | -125780.718 | 672599.303 | 4740952.6 | 4638285.24 | -52158.8651 | 110068.326 | 17102.4105 | 299238.32 | -162651.722 | 1420921.51 | -33663.5723 | 29444.6381 | 5935.9363 | 69013.388 | -11688.9342 | 156368.124 | -11302.0116
501.32 | 11.8061 | 4.756 |  | 204068.514 | -108324.068 | 652339.749 | 4451439.41 | 5280022.45 | -51743.0076 | 106358.015 | 26059.7186 | 296422.451 | -220902.601 | 1455745.6 | -30036.484 | 34145.1452 | 5493.8846 | 68971.687 | -6845.9673 | 192069.679 | -9175.4634
501.52 | 11.8512 | 4.8919 |  | 211464.762 | -79660.1859 | 624620.589 | 4011588.55 | 5489402.27 | -45654.6813 | 107843.402 | 30371.2757 | 289794.642 | -283635.431 | 1528330.8 | -29156.2467 | 37205.2805 | 6891.416 | 67408.123 | -13366.5486 | 212228.939 | -10857.0917
501.72 | 11.8539 | 5.042 |  | 227923.993 | -91271.4797 | 595622.492 | 4097268.43 | 5704036.42 | -55952.8727 | 102628.606 | 32846.4839 | 286463.408 | -306072.323 | 1416747.09 | -28479.0836 | 34063.6932 | 6983.9333 | 67642.1742 | -13978.8681 | 196086.607 | -7910.0499
501.92 | 11.8626 | 5.0995 |  | 213754.353 | -56879.6613 | 552239.819 | 3606808.58 | 5391571.21 | -35255.4613 | 101872.781 | 29896.215 | 275482.704 | -246199.14 | 1513073.19 | -23343.8362 | 37646.7845 | 5339.3049 | 65526.739 | -6535.7113 | 213185.129 | -7102.2826
502.12 | 11.8604 | 5.1494 |  | 207375.583 | -75256.1169 | 516295.317 | 4068792.76 | 5345382.62 | -30668.1761 | 110351.604 | 25535.5863 | 267662.811 | -232648.882 | 1581707.73 | -18914.5455 | 36825.0028 | 6137.745 | 63755.7458 | -10717.1137 | 216623.631 | -5494.0163
502.32 | 11.8551 | 5.1683 |  | 222149.828 | -117916.097 | 485661.756 | 5240130.72 | 5794408.27 | -43616.9917 | 127627.335 | 21589.8912 | 261914.65 | -177086.564 | 1701940.61 | -26403.7761 | 37950.109 | 4670.2787 | 63504.1463 | -5596.4549 | 208947.212 | -6910.616
502.52 | 11.8527 | 5.1493 |  | 197900.095 | -129661.387 | 447394.257 | 5888511.15 | 5591862.18 | -35366.6597 | 143366.785 | 14101.293 | 252106.307 | -91131.7643 | 2036567.66 | -26919.9185 | 46649.2958 | 3619.0208 | 62292.3423 | -3335.0082 | 239814.724 | -8568.9246
502.72 | 11.8946 | 5.152 |  | 197245.451 | -160904.108 | 428189.811 | 6836621.66 | 5605213.95 | -33869.5125 | 151716.979 | 5944.2181 | 247701.892 | 28830.0711 | 2215282.21 | -28172.1413 | 53879.7529 | 634.8244 | 61829.7986 | 12182.6867 | 287601.267 | -10116.7954
502.92 | 11.9227 | 5.2534 |  | 160755.603 | -185152.905 | 405878.948 | 7481652.33 | 5091537.89 | -26461.8894 | 158000.409 | -1829.3287 | 240637.548 | 88475.6234 | 2309190.64 | -29632.9471 | 55917.1471 | 355.1189 | 59307.8377 | 14294.9739 | 303819.926 | -10571.2489
503.12 | 11.9514 | 5.3474 |  | 137491.15 | -216960.534 | 400268.251 | 8122052.03 | 4571800.24 | -29669.2324 | 159269.742 | -12521.6023 | 244000.349 | 243950.516 | 2320102.12 | -23283.8471 | 55318.8676 | -3215.2787 | 61449.4796 | 30148.2685 | 308770.973 | -6044.3661
503.32 | 11.9833 | 5.432 |  | 96518.195 | -231591.242 | 398443.348 | 8435987.87 | 3736338.75 | -41270.6868 | 157094.674 | -23643.6219 | 240088.246 | 398082.522 | 2445024.87 | -33601.0014 | 63019.7061 | -6456.4055 | 59959.8951 | 45951.8336 | 347148.783 | -10665.7716
503.52 | 11.995 | 5.5369 |  | 60864.2141 | -241912.39 | 406192.076 | 8445820.15 | 2972867.77 | -56417.2812 | 150009.26 | -31117.5281 | 240651.103 | 469961.078 | 2379330.07 | -40238.7978 | 63076.1951 | -7149.3805 | 59862.3285 | 50360.3576 | 358837.679 | -14213.5187
503.72 | 11.9793 | 5.5909 |  | 21450.7845 | -243549.239 | 426968.485 | 8031430.18 | 2046617.81 | -52743.5178 | 133637.697 | -35689.8835 | 245315.601 | 499134.099 | 2112410.88 | -34867.4326 | 57125.4416 | -7461.6906 | 59905.1105 | 51265.5997 | 327279.693 | -11249.0875
503.92 | 11.9701 | 5.575 |  | -15542.9026 | -233271.573 | 461292.841 | 7378762.78 | 1084740.53 | -50218.0647 | 114728.99 | -40324.8153 | 253758.872 | 559506.903 | 1909096.19 | -29888.0102 | 53814.1715 | -8696.273 | 61466.6844 | 57008.6229 | 319473.547 | -10469.3389
504.12 | 11.977 | 5.5496 |  | -33288.2534 | -246279.769 | 497128.614 | 7427783.01 | 678531.956 | -45179.8756 | 111879.118 | -44010.161 | 264119.187 | 575473.836 | 1729785.68 | -22959.0059 | 44511.0348 | -8298.224 | 63390.7588 | 52689.3603 | 257815.771 | -4582.561
504.32 | 11.9908 | 5.561 |  | -46478.7376 | -237698.603 | 539015.455 | 7303509.14 | 478522.613 | -53598.4017 | 113861.603 | -45286.1685 | 272906.862 | 601588.61 | 1856324.86 | -35900.1803 | 47358.2469 | -8060.5095 | 65168.9639 | 50295.6573 | 266522.005 | -12461.8049
504.52 | 12.0151 | 5.6236 |  | -38430.0735 | -255660.44 | 581457.148 | 7488743.91 | 623973.888 | -57838.6904 | 111267.128 | -42994.551 | 283606.006 | 539675.8 | 1668520 | -33935.5963 | 40499.8022 | -6233.0263 | 66596.1641 | 43751.4008 | 242492.15 | -11391.9164
504.72 | 12.0508 | 5.7326 |  | -31412.2092 | -243598.234 | 619521.498 | 7186283.81 | 723648.318 | -49682.9909 | 105621.958 | -38648.3599 | 294066.098 | 513118.184 | 1590028.76 | -27770.917 | 41359.2723 | -7185.8388 | 69065.5919 | 49249.7238 | 239251.3 | -8014.0882
504.92 | 12.0938 | 5.8797 |  | -15169.6783 | -241555.454 | 660513.145 | 6926233.25 | 956574.769 | -62371.7416 | 98272.5028 | -32783.4268 | 303214.863 | 435951.953 | 1465269.64 | -38268.1333 | 37581.4685 | -5038.8792 | 70155.1436 | 39988.961 | 227691.628 | -13940.0198
505.12 | 12.1028 | 6.0337 |  | 2472.4523 | -212111.776 | 691721.017 | 6070172.26 | 1080534.65 | -50978.5308 | 84148.7617 | -25760.9281 | 311777.026 | 370877.75 | 1302712.81 | -28189.8694 | 35901.2181 | -4652.9586 | 72269.2426 | 37543.2846 | 208909.978 | -8822.8553
505.32 | 12.0889 | 6.1117 |  | 11283.3339 | -160763.197 | 713090.577 | 5024100.52 | 1111339.66 | -46420.6138 | 79642.0691 | -21718.5642 | 315733.425 | 327997.519 | 1346781.67 | -33998.1451 | 37445.8987 | -3303.5928 | 72808.6748 | 29987.9408 | 208244.398 | -12122.2151
505.52 | 12.0887 | 6.1425 |  | 40679.7019 | -143251.154 | 723384.552 | 4512590.29 | 1658290.39 | -47274.4949 | 75020.0199 | -11800.0881 | 317190.815 | 222590.476 | 1200461.61 | -27521.3873 | 33968.3781 | -2147.9646 | 72349.2417 | 27560.7042 | 211796.142 | -8234.0012
505.72 | 12.0564 | 6.178 |  | 70454.8964 | -124465.832 | 725896.322 | 4332951.36 | 2314832.19 | -44084.6885 | 84181.071 | -4613.3355 | 318617.732 | 115086.989 | 1304774.41 | -25728.6533 | 33194.1659 | 629.7748 | 72980.7829 | 12735.1456 | 187439.165 | -8068.1337
505.92 | 12.0297 | 6.1192 |  | 124431.254 | -139181.282 | 722156.7 | 4926023.29 | 3535080.52 | -53798.5965 | 98982.3952 | 3992.6816 | 318533.56 | 59436.4882 | 1445128.24 | -29245.63 | 35157.7338 | 310.5791 | 73382.0891 | 16964.5785 | 198884.307 | -7643.4217
506.12 | 12.0519 | 6.0592 |  | 162458.699 | -130264.15 | 704477.561 | 5193324.64 | 4515905.38 | -54795.3141 | 117882.443 | 10491.35 | 312679.529 | -31012.1649 | 1704302.05 | -40652.0853 | 39909.7376 | 2999.5731 | 72202.0761 | 2567.4624 | 209870.536 | -13236.3332
506.32 | 12.064 | 6.1132 |  | 194129.889 | -109274.683 | 683364.285 | 4727859.65 | 5268797.55 | -54648.241 | 117136.684 | 23035.4297 | 306161.565 | -149131.036 | 1729223.73 | -39879.7185 | 41986.0052 | 4123.0965 | 70737.3134 | 903.5427 | 233708.719 | -13393.7084
506.52 | 12.0804 | 6.2026 |  | 205693.222 | -74977.1579 | 654568.78 | 3845813.38 | 5397310.98 | -51869.8437 | 103346.756 | 31016.7978 | 301258.169 | -262789.034 | 1595713.79 | -33599.9209 | 41847.0425 | 6310.4257 | 70330.2381 | -9058.6498 | 244179.066 | -10940.8588
506.72 | 12.0924 | 6.307 |  | 210705.488 | -42950.0893 | 610164.852 | 2996642.1 | 5345618.46 | -49666.3266 | 90140.3749 | 36677.9583 | 291948.998 | -308882.614 | 1415989.1 | -29773.9568 | 37246.0996 | 6283.1376 | 68264.3353 | -8098.4047 | 220772.797 | -8428.8276
506.92 | 12.0934 | 6.4114 |  | 208455.849 | -25553.2623 | 583044.245 | 2476889.57 | 5160207.22 | -42560.2559 | 82060.9314 | 36569.2476 | 288073.343 | -305397.258 | 1333341.18 | -18926.242 | 36452.0959 | 5974.6878 | 68372.6606 | -9385.1021 | 210457.042 | -4141.3432
507.12 | 12.0597 | 6.4596 |  | 201347.735 | -44934.9592 | 538332.436 | 3054670.12 | 5143458.86 | -47617.6674 | 94296.9055 | 31618.0541 | 278701.471 | -278740.3 | 1448020.82 | -27255.7711 | 36463.9419 | 6527.2544 | 66639.5952 | -13525.7052 | 205055.783 | -7408.9308
507.32 | 12.027 | 6.4154 |  | 208434.824 | -80578.8495 | 498862.717 | 3932260.91 | 5261181.72 | -61442.5396 | 100152.954 | 26385.6395 | 269837.836 | -199466.343 | 1419499.42 | -35159.6477 | 34277.6715 | 4401.3743 | 65648.8988 | -2386.3572 | 191271.557 | -9459.7059
507.52 | 12.0165 | 6.3723 |  | 171166.241 | -87253.6949 | 457283.098 | 4224761.88 | 4716742.23 | -36851.8361 | 104502.259 | 20185.3643 | 256850.542 | -149261.461 | 1564653.38 | -27850.5453 | 38260.9915 | 4133.3433 | 62049.189 | -3455.8056 | 207061.372 | -9374.1092
507.72 | 11.9899 | 6.3637 |  | 154813.132 | -120728.722 | 435715.313 | 4926188.28 | 4358166.59 | -42336.6895 | 106650.409 | 10759.9001 | 254902.574 | -53718.6516 | 1612536.21 | -26776.1224 | 41370.9333 | 2606.0446 | 63497.138 | 1050.7138 | 227985.881 | -7887.9742
507.92 | 11.9881 | 6.3097 |  | 128524.945 | -136035.733 | 415034.92 | 5512302.83 | 3952985.66 | -35439.4849 | 115416.051 | 1145.0065 | 247507.723 | 90613.7998 | 1757405.92 | -26765.4216 | 45766.8448 | -1105.798 | 61142.4155 | 23606.3837 | 260928.656 | -7539.6583
508.12 | 12.0192 | 6.3155 |  | 102055.905 | -172654.752 | 408573.454 | 6390956.54 | 3605543.24 | -42154.1987 | 126317.086 | -8081.1561 | 245006.559 | 158434.282 | 1900886.53 | -33264.0868 | 46906.4834 | -502.6322 | 60418.7594 | 16141.6843 | 258320.825 | -11934.1139
508.32 | 12.0072 | 6.384 |  | 83117.2184 | -204679.464 | 408729.409 | 7045891.97 | 3270401.98 | -53033.6787 | 128047.347 | -15033.2916 | 246306.655 | 238816.077 | 1905930.56 | -34156.6865 | 47929.1712 | -2137.7343 | 61186.5656 | 23069.9247 | 264123.945 | -11676.5744
508.52 | 11.9786 | 6.3588 |  | 34453.305 | -214282.139 | 419110.871 | 6988250.28 | 2107890.68 | -55669.2867 | 119299.267 | -27260.7603 | 248593.993 | 349322.037 | 1786200.02 | -34737.1273 | 45690.0152 | -3432.1094 | 61405.9302 | 29848.4986 | 265071.803 | -12644.5812
508.72 | 11.9561 | 6.2816 |  | 3068.5194 | -225101.029 | 435304.143 | 7058501.2 | 1262332.81 | -44436.4595 | 111829.762 | -37823.8487 | 251816.558 | 518211.663 | 1687144.95 | -27214.0451 | 42660.8921 | -7695.9414 | 61818.7263 | 49764.7091 | 245512.149 | -9009.8182
508.92 | 11.9263 | 6.2214 |  | -20869.6116 | -247794.978 | 456187.022 | 7493212.14 | 832510.384 | -54151.0284 | 112921.94 | -43838.704 | 253864.388 | 570913.463 | 1685399.33 | -29481.8912 | 42050.0434 | -8038.0847 | 61481.6097 | 49941.0885 | 236946.482 | -9550.2635
509.12 | 11.8772 | 6.142 |  | -32485.7736 | -263144.799 | 483742.338 | 7905652 | 716706.958 | -52048.3935 | 120100.816 | -47612.4686 | 260248.58 | 600606.173 | 1781555.45 | -28196.5423 | 41609.6057 | -7755.861 | 63343.1852 | 45197.1771 | 216032.62 | -8426.7553
509.32 | 11.8536 | 6.0122 |  | -35001.0905 | -277605.989 | 517349.662 | 8169651.57 | 708006.087 | -66592.2057 | 118235.755 | -47534.9162 | 265968.996 | 622584.396 | 1834555.68 | -40128.4097 | 47394.5684 | -8775.0443 | 64047.9588 | 53983.9163 | 265171.413 | -12958.7682
509.52 | 11.846 | 5.9325 |  | -47556.5099 | -249835.114 | 549903.299 | 7811148.08 | 548665.994 | -47133.2372 | 125009.417 | -49099.6434 | 271906.248 | 635441.05 | 1936488.72 | -28821.061 | 46687.1391 | -8347.9548 | 64583.1129 | 51767.899 | 260613.994 | -9974.933
509.72 | 11.8591 | 5.8932 |  | -25065.8366 | -273683.657 | 598118.815 | 8373949.93 | 981448.902 | -56159.5048 | 130425.401 | -48535.9602 | 284756.038 | 621744.385 | 1926201.54 | -32001.4483 | 45274.1947 | -7913.124 | 67097.4629 | 49148.9797 | 252425.06 | -10015.2495
509.92 | 11.8466 | 5.8955 |  | -6578.5383 | -275842.425 | 633958.826 | 8441443.18 | 1344130.46 | -66912.2645 | 129006.176 | -43499.5185 | 291647.332 | 579658.496 | 1959956.43 | -39039.8068 | 50097.6745 | -7745.733 | 68161.2803 | 50258.5326 | 279106.168 | -13136.5762
510.12 | 11.8199 | 5.8185 |  | 12861.4518 | -254327.789 | 660152.67 | 7776907.07 | 1547484.73 | -65033.1226 | 120905.31 | -37135.936 | 296442.262 | 509467.074 | 1784994.81 | -41185.4843 | 44813.4604 | -6678.7045 | 69014.803 | 47090.4852 | 243468.541 | -13552.7769
510.32 | 11.8175 | 5.6923 |  | 26023.6595 | -193326.936 | 681618.881 | 6222775.47 | 1563499.55 | -44566.6498 | 101129.685 | -27403.4683 | 298157.502 | 412326.506 | 1591203.07 | -29747.3199 | 43945.2701 | -5758.8849 | 68061.3085 | 44547.8846 | 262789.242 | -9519.287
510.52 | 11.7727 | 5.6203 |  | 40884.2554 | -134321.526 | 687505.581 | 4757586.84 | 1863878.23 | -34143.682 | 88246.747 | -12664.1442 | 297990.25 | 248193.742 | 1553941.98 | -21581.5915 | 45126.4886 | -3099.5687 | 67836.2139 | 33708.2016 | 277350.661 | -6831.0759
510.72 | 11.705 | 5.4735 |  | 83865.4071 | -124082.364 | 694942.609 | 4707946.32 | 2731460.34 | -37339.4397 | 96775.6025 | -4886.1001 | 302469.29 | 150133.627 | 1600521.43 | -22385.7934 | 41773.2501 | -706.1315 | 69453.4081 | 19883.7898 | 236387.488 | -6102.4254
510.92 | 11.7033 | 5.2886 |  | 140551.72 | -147751.961 | 685391.276 | 5519215.55 | 4014212.81 | -46909.0315 | 115295.308 | 2049.3342 | 301205.805 | 101846.126 | 1711753.47 | -25773.2266 | 40809.3294 | -655.4757 | 69477.4548 | 20300.7876 | 218117.289 | -6355.3543
511.12 | 11.6698 | 5.2068 |  | 157089.603 | -132310.312 | 664632.24 | 5435336.41 | 4456012.83 | -55321.9553 | 121240.551 | 7482.5548 | 293957.379 | 13812.8234 | 1926775.98 | -40999.9106 | 48421.0973 | 2143.4365 | 68479.3757 | 5275.861 | 252202.261 | -14266.6998
511.32 | 11.6365 | 5.072 |  | 181078.615 | -96288.4017 | 640474.905 | 4611995.04 | 4823137.17 | -45226.1117 | 113444.878 | 15354.6244 | 286492.657 | -14267.1778 | 1836366.71 | -32026.0598 | 47512.2582 | 609.1017 | 66623.341 | 17624.2973 | 266305.448 | -10888.0807
511.52 | 11.6503 | 4.961 |  | 185592.244 | -58229.686 | 612481.633 | 3625823.22 | 4840337.86 | -44343.0731 | 98222.4483 | 23736.3538 | 278089.565 | -135991.491 | 1703328.61 | -31409.244 | 47226.7372 | 2961.0928 | 64322.2951 | 7569.1324 | 277777.792 | -8549.2541
511.72 | 11.6265 | 4.9138 |  | 190866.275 | -18406.562 | 577005.452 | 2459818.1 | 4849071.44 | -49247.1977 | 82479.0937 | 33033.2798 | 269799.728 | -251909.405 | 1505563.46 | -29150.1296 | 42986.3393 | 5240.817 | 62666.2576 | -4622.0155 | 256596.196 | -10502.7808
511.92 | 11.5868 | 4.8001 |  | 206135.479 | -23959.406 | 559271.192 | 2144882.59 | 4970234.81 | -45646.185 | 70927.7802 | 37642.9985 | 269910.898 | -324047.504 | 1203535.03 | -16997.0665 | 35990.7064 | 5827.8212 | 63437.8533 | -6305.9193 | 222612.988 | -1310.4733
512.12 | 11.5933 | 4.6732 |  | 199371.829 | -13584.9627 | 510465.906 | 2261186.19 | 5005009.62 | -44816.9306 | 85059.9954 | 35339.8032 | 258511.634 | -314349.564 | 1305218.08 | -28566.4829 | 31657.1852 | 6803.4163 | 61186.3719 | -13501.0179 | 182711.765 | -8178.4861
512.32 | 11.5353 | 4.6113 |  | 198189.392 | -41787.8223 | 478749.57 | 2738735.29 | 4938689.63 | -62497.9054 | 84848.5542 | 32070.959 | 252252.739 | -291049.473 | 1266669.79 | -34721.7269 | 29889.9666 | 6813.7579 | 60681.93 | -16167.6023 | 166241.922 | -9300.6691
512.52 | 11.4818 | 4.4556 |  | 171140.643 | -38246.9091 | 435119.789 | 2753823.97 | 4386918.71 | -48474.1002 | 81585.6986 | 25198.2682 | 240922.672 | -177201.319 | 1333425.89 | -30594.5343 | 36100.8827 | 3569.4982 | 58921.3217 | -619.499 | 200176.909 | -8836.1969
512.72 | 11.4823 | 4.2943 |  | 139474.174 | -46681.9034 | 397811.622 | 2943020.49 | 3768266.19 | -41426.7987 | 81001.5702 | 16863.8378 | 229480.503 | -104589.714 | 1380491.29 | -30056.9938 | 38853.6563 | 2967.334 | 56038.3457 | 2041.3972 | 231649.998 | -10659.0478
512.92 | 11.4471 | 4.2161 |  | 128337.692 | -74315.3705 | 379806.642 | 3603229.68 | 3659251.11 | -34313.37 | 89824.9896 | 11094.4092 | 226338.863 | -23276.4745 | 1423404.25 | -18352.1537 | 35325.2921 | 1067.1549 | 55880.0314 | 9868.0791 | 196474.38 | -3510.4256
513.12 | 11.4294 | 4.0769 |  | 104091.293 | -122616.007 | 366111.152 | 4917356.08 | 3496802.4 | -43389.8473 | 105441.217 | 1965.0635 | 222968.932 | 65390.6761 | 1703485.39 | -30987.3445 | 45422.2453 | -99.5548 | 55497.2438 | 13362.4459 | 244680.992 | -9829.0062
513.32 | 11.4268 | 3.9344 |  | 77501.3505 | -159506.429 | 359227.817 | 6009879.93 | 3074517.2 | -47236.911 | 119447.082 | -11380.7246 | 222374.679 | 205274.502 | 1886396.63 | -35192.5444 | 48185.5396 | -1788.6883 | 56000.6604 | 20666.2904 | 266436.525 | -11307.3826
513.52 | 11.3939 | 3.8296 |  | 37640.9554 | -188829.368 | 364105.338 | 6564305.89 | 2165922.9 | -55997.4242 | 115340.216 | -24427.0448 | 221546.969 | 370218.929 | 1847546.17 | -38717.6504 | 50080.7568 | -5303.0055 | 54897.2046 | 40182.3484 | 289503.067 | -13923.5113
513.72 | 11.3664 | 3.6992 |  | 2964.1371 | -221175.594 | 376453.554 | 7008461.09 | 1182746.47 | -37214.4268 | 103066.293 | -37859.4569 | 224762.784 | 516286.644 | 1641597.42 | -18113.9877 | 46885.1163 | -8797.721 | 55533.3576 | 58614.3997 | 286391.131 | -5531.399
513.92 | 11.3875 | 3.5966 |  | -16377.519 | -251195.1 | 389074.401 | 7884073.33 | 922935.416 | -37963.6502 | 111734.158 | -45592.9695 | 224109.683 | 619026.207 | 1776692.59 | -21931.5591 | 49732.9766 | -10536.918 | 54426.5904 | 62166.1678 | 284207.921 | -7105.0906
514.12 | 11.3382 | 3.5629 |  | -20762.6743 | -287417.338 | 415605.166 | 8786336.6 | 1118870.21 | -52672.0326 | 129707.428 | -48624.5003 | 230697.317 | 617084.832 | 1973939.16 | -29486.092 | 50721.6867 | -8969.5831 | 56562.4308 | 52339.7623 | 279288.501 | -8052.7546
514.32 | 11.328 | 3.4065 |  | -22216.77 | -283009.821 | 436128.335 | 9107813.23 | 1313127.57 | -54481.977 | 146820.992 | -51879.8556 | 233183.4 | 690581.928 | 2219241.21 | -34681.1445 | 54933.8231 | -10630.6697 | 56831.4433 | 62007.2099 | 300993.215 | -10724.7592
514.52 | 11.3599 | 3.3193 |  | -27331.1065 | -293752.079 | 473390.198 | 9344997.29 | 1265404.29 | -57096.1304 | 148945.713 | -53048.069 | 241313.961 | 692626.509 | 2335153.47 | -32321.4354 | 60700.0245 | -10539.8269 | 58086.8617 | 62759.7562 | 339563.76 | -9831.8673
514.72 | 11.3366 | 3.3054 |  | -30726.2941 | -298255.178 | 507665.214 | 9581478.94 | 1238847.93 | -58029.1338 | 155987.151 | -55655.3178 | 250799.548 | 746803.256 | 2424159.86 | -35147.698 | 60256.8635 | -11550.192 | 60282.8974 | 69197.379 | 338299.581 | -9973.3773
514.92 | 11.3201 | 3.1836 |  | -29178.7173 | -307775.712 | 542248.723 | 9762852.64 | 998728.093 | -67170.5396 | 149882.714 | -61296.5052 | 258884.271 | 823364.362 | 2352391.62 | -35328.6342 | 60908.705 | -13192.3678 | 61855.9448 | 77336.1324 | 349769.997 | -9794.7811
515.12 | 11.3191 | 3.0509 |  | -26040.9334 | -265342.493 | 563905.943 | 8928943.66 | 909743.841 | -53622.0282 | 141587.148 | -58499.4768 | 256997.791 | 862910.194 | 2370417.31 | -32537.6115 | 64785.1397 | -15964.682 | 59908.1177 | 96631.3691 | 381481.493 | -10208.5986
515.32 | 11.2896 | 2.9348 |  | -8092.057 | -263701.184 | 594743.446 | 8689735.62 | 1344325.25 | -53437.9978 | 138565.801 | -48676.8065 | 262723.517 | 692036.293 | 2293066.51 | -31688.6718 | 63020.0057 | -11846.2171 | 60469.1172 | 75583.0615 | 364022.045 | -8786.4886
515.52 | 11.2733 | 2.7719 |  | 39203.7062 | -253725.801 | 615915.525 | 8296122.13 | 2324479.6 | -53300.2612 | 138599.593 | -34075.9572 | 268329.845 | 539628.701 | 2170671.93 | -30744.8014 | 56422.0078 | -9582.0747 | 61639.7891 | 67097.5841 | 327336.106 | -7672.8864
515.72 | 11.2706 | 2.665 |  | 57392.6209 | -219279.53 | 633756.772 | 7325954.29 | 2686652.12 | -49183.8519 | 126021.385 | -20777.1401 | 271704.082 | 353009.778 | 2127170.64 | -30567.6921 | 57546.8481 | -4894.4487 | 62204.7485 | 40389.8014 | 326399.011 | -9580.6582
515.92 | 11.253 | 2.6177 |  | 93022.1774 | -173014.316 | 643502.583 | 6330788.94 | 3245681.79 | -33538.145 | 121863.416 | -11044.7038 | 277673.026 | 274709.731 | 1999122.06 | -22782.6666 | 53109.0773 | -4787.2648 | 64268.9738 | 43026.8168 | 305804.874 | -6342.7765
516.12 | 11.2724 | 2.5699 |  | 123651.887 | -167563.132 | 642886.074 | 6265808.9 | 3735122.13 | -29726.1951 | 121915.288 | -6640.4591 | 277745.792 | 180036.979 | 1902287.22 | -18472.9739 | 49199.0019 | -1909.6799 | 63232.8082 | 26545.8402 | 281977.803 | -5786.7656
516.32 | 11.2901 | 2.5989 |  | 162208.444 | -150905.576 | 630154.705 | 5902823.18 | 4539886.79 | -46241.9118 | 124254.602 | 5035.1801 | 275060.386 | 69459.2982 | 1890364.78 | -31120.1982 | 46454.0596 | -264.5483 | 63564.2936 | 19674.8083 | 260648.921 | -10233.3039
516.52 | 11.2834 | 2.6113 |  | 185140.302 | -114856.16 | 604202.249 | 4903839.57 | 4966903.01 | -42890.3756 | 116711.328 | 16845.4517 | 268187.473 | -106198.889 | 1696853.36 | -30032.7343 | 40294.0319 | 3613.7424 | 61578.0892 | 2027.7504 | 231935.091 | -8909.82
516.72 | 11.2927 | 2.567 |  | 189755.302 | -51581.0592 | 583327.221 | 3080575.76 | 4837967.72 | -40644.5376 | 84884.4076 | 30031.9282 | 264339.361 | -211934.751 | 1513600.37 | -21892.2153 | 44282.9191 | 3731.5444 | 61494.0656 | 2957.5483 | 259641.593 | -6937.04
516.92 | 11.2869 | 2.5321 |  | 193738.742 | -27452.3108 | 554095.306 | 2208549.19 | 4824919.17 | -52139.9286 | 72357.0995 | 37223.39 | 258782.975 | -315762.967 | 1345232.93 | -24484.4607 | 39349.8152 | 6112.8078 | 60052.204 | -7418.4919 | 239195.355 | -6358.2477
517.12 | 11.2711 | 2.4601 |  | 204146.954 | -26750.9594 | 528151.065 | 2137191.83 | 4911934.45 | -56180.659 | 69783.811 | 37548.2889 | 256166.595 | -326558.944 | 1212291.8 | -26768.7177 | 34819.6677 | 6340.2487 | 60452.6288 | -10032.9205 | 216852.768 | -6845.4843
517.32 | 11.2871 | 2.3587 |  | 203926.165 | -21687.594 | 492534.409 | 2139724.61 | 4904097.46 | -56291.0544 | 74614.2737 | 35655.6594 | 246970.963 | -296551.221 | 1197828.6 | -29377.3863 | 30571.9169 | 5828.6862 | 58361.4594 | -9132.057 | 180484.043 | -8958.9199
517.52 | 11.2817 | 2.3268 |  | 200684.714 | -34372.0431 | 463450.283 | 2391689.54 | 4886650.24 | -59512.4726 | 75316.6646 | 34705.9825 | 240753.723 | -324191.869 | 1161003.72 | -31122.8185 | 29044.9915 | 7171.3741 | 57491.6355 | -17780.495 | 168931.505 | -7693.4021
517.72 | 11.2814 | 2.2705 |  | 180333.733 | -10648.7861 | 427354.137 | 1925850.22 | 4505731.47 | -52158.829 | 69146.3315 | 33359.3209 | 231542.236 | -277387.893 | 1240290.77 | -30727.8394 | 35284.4741 | 5548.4201 | 55919.6345 | -9339.8185 | 202671.624 | -10250.6988
517.92 | 11.3381 | 2.2444 |  | 171525.617 | -25402.3975 | 402600.716 | 2075046.87 | 4401137.41 | -49501.9415 | 66335.0589 | 32970.5583 | 225902.449 | -276570.732 | 1202652.41 | -26251.8504 | 36760.292 | 5197.7552 | 54532.0487 | -5519.8257 | 227467.797 | -7496.8896
518.12 | 11.3467 | 2.3272 |  | 143996.614 | -39436.8445 | 381238.459 | 2457386.64 | 4064510.11 | -50978.5422 | 73224.8422 | 28562.5142 | 223478.861 | -263182.948 | 1277345.32 | -31526.0536 | 35307.5155 | 6108.5041 | 54575.0274 | -12951.6586 | 205089.007 | -9379.2894
518.32 | 11.3295 | 2.306 |  | 111331.266 | -73003.465 | 368184.264 | 3209752.55 | 3357363.82 | -44879.5156 | 77973.0429 | 14318.8247 | 224790.834 | -103926.472 | 1252276.06 | -26665.139 | 33548.405 | 3200.6814 | 56035.7684 | -147.1974 | 203195.087 | -7720.8968
518.52 | 11.3645 | 2.2166 |  | 84052.3368 | -107840.761 | 361396.398 | 4206358.11 | 2649460.99 | -37489.5181 | 85023.5219 | -4048.1508 | 222926.527 | 133020.252 | 1303257.84 | -27470.2478 | 34295.0813 | -1498.0936 | 55570.2338 | 20959.9516 | 202486.457 | -9240.0637
518.72 | 11.3658 | 2.2486 |  | 50981.1258 | -163387.263 | 360123.473 | 5360350.93 | 2077594.01 | -48775.2726 | 93061.2426 | -16101.282 | 220333.16 | 233440.867 | 1327124.01 | -29498.5151 | 31457.5307 | -2102.8884 | 54163.7661 | 22325.9207 | 188065.28 | -8255.2733
518.92 | 11.3342 | 2.2309 |  | 17394.1185 | -187987.318 | 365183.653 | 6001486.11 | 1490766.15 | -43184.2387 | 96537.8202 | -26486.7693 | 220839.289 | 349639.837 | 1435787.01 | -23642.3595 | 36323.3426 | -4289.6974 | 54633.6463 | 31963.4201 | 206465.932 | -9475.1506
519.12 | 11.3464 | 2.1451 |  | -110.8306 | -236480.1 | 384996.987 | 7276357.23 | 1323679.92 | -37388.1647 | 112536.329 | -36581.7986 | 225984.084 | 440330.143 | 1577748.21 | -21815.2321 | 36716.7886 | -5072.1999 | 55436.5735 | 33854.8856 | 200060.049 | -7931.3202
519.32 | 11.3531 | 2.1335 |  | -8297.5163 | -283762.373 | 407531.829 | 8524200.61 | 1364005.64 | -58378.7383 | 125376.221 | -41972.0673 | 231350.49 | 520951.628 | 1747540.72 | -30485.1982 | 41481.4434 | -7092.7489 | 56727.4021 | 46339.3115 | 235665.496 | -10657.0785
519.52 | 11.3477 | 2.1093 |  | -33596.8541 | -289408.585 | 437913.024 | 9057790.92 | 938239.781 | -35225.7451 | 138887.841 | -54361.8699 | 239557.417 | 661803.519 | 2032107.54 | -18503.3946 | 49640.209 | -9083.218 | 59030.2689 | 52298.9396 | 266534.482 | -5835.7896
519.72 | 11.3665 | 2.0562 |  | -34629.2997 | -314168.237 | 468607.402 | 10051160.8 | 1009486.07 | -58227.377 | 155752.238 | -63046.3989 | 243384.802 | 835099.438 | 2398683.15 | -33525.3751 | 60387.7829 | -13583.851 | 59689.4079 | 75319.8813 | 320962.417 | -10784.0641
519.92 | 11.3837 | 2.0532 |  | -16889.644 | -352515.217 | 499541.733 | 11063183.3 | 1494750.42 | -65583.8737 | 172405.255 | -65165.3183 | 247857.335 | 836156.154 | 2505572.68 | -32905.0127 | 59299.0087 | -12561.6786 | 59135.6381 | 74830.9838 | 336848.908 | -9810.072
520.12 | 11.3869 | 2.0564 |  | -16255.548 | -352510.347 | 531710.834 | 11298615.3 | 1658067.01 | -60607.5173 | 180199.011 | -64927.6857 | 255139.758 | 831001.015 | 2718493.08 | -31310.2193 | 66512.2653 | -12374.1784 | 61159.3089 | 71066.2036 | 364057.095 | -8820.8033
520.32 | 11.4051 | 2.0304 |  | -751.354 | -333219.563 | 555590.118 | 11064073.7 | 1930155.89 | -63058.3728 | 179365.199 | -61386.9962 | 258237.646 | 905029.803 | 2915585.45 | -38222.2606 | 76567.4853 | -16824.5113 | 62253.3342 | 98467.6513 | 425896.978 | -9491.5074
520.52 | 11.4277 | 2.04 |  | 11418.5299 | -319076.685 | 584689.906 | 10693033.3 | 2078695.37 | -69817.811 | 173924.97 | -57122.6124 | 260649.493 | 859657.307 | 2907586.36 | -43738.4524 | 80115.8122 | -16057.2061 | 60946.6928 | 97068.881 | 449279.831 | -13209.0339
520.72 | 11.4418 | 2.0739 |  | 43537.0542 | -320865.01 | 614397.251 | 10442931.6 | 2581585.49 | -57816.2556 | 167657.928 | -49140.4076 | 271372.724 | 736218.639 | 2629077.13 | -29084.9277 | 70158.7158 | -14074.758 | 63167.0444 | 90744.2779 | 402336.65 | -5840.747
520.92 | 11.4632 | 2.1029 |  | 56260.4741 | -286133.571 | 635439.125 | 9625499.99 | 2836220.49 | -49127.2316 | 163829.432 | -40780.8316 | 275368.486 | 572849.114 | 2523320.17 | -33434.8068 | 64543.716 | -8386.8148 | 63043.4118 | 58531.139 | 370222.859 | -9969.941
521.12 | 11.4782 | 2.1363 |  | 92109.2632 | -240697.531 | 646657.452 | 8270517.19 | 3482987.56 | -47434.383 | 148622.093 | -22255.7952 | 279473.139 | 397065.292 | 2275449.54 | -32684.6728 | 58250.112 | -6582.6173 | 64452.3766 | 52236.4638 | 335951.184 | -9310.2936
521.32 | 11.5044 | 2.1684 |  | 106010.186 | -173596.902 | 659977.045 | 6315942.11 | 3581581.43 | -33426.6695 | 119832.929 | -4689.8709 | 282601.784 | 194658.304 | 2029099.94 | -21794.7492 | 57925.8435 | -3749.8018 | 64201.6506 | 41417.4212 | 340899.237 | -6200.4071
521.52 | 11.5613 | 2.2406 |  | 140687.765 | -133404.86 | 657850.53 | 5119809.37 | 4122862.41 | -36465.2389 | 106009.838 | 9854.6233 | 285263.975 | 14581.6676 | 1770187.56 | -21890.9266 | 50942.3824 | -293.2271 | 65168.0456 | 25605.029 | 310556.485 | -7066.857
521.72 | 11.5881 | 2.3911 |  | 172989.695 | -106215.568 | 647966.592 | 4436528.78 | 4702309.54 | -39475.2765 | 105882.258 | 19693.4146 | 287111.415 | -151183.353 | 1574539.63 | -21981.6851 | 38884.5033 | 4392.2633 | 65826.6863 | 423.3019 | 238484.975 | -4486.2271
521.92 | 11.5985 | 2.5014 |  | 188903.675 | -67231.1187 | 620504.978 | 3551925.43 | 4919590.71 | -39867.5429 | 98346.4291 | 26735.3173 | 282618.849 | -201528.265 | 1549379.78 | -20566.2938 | 40541.8276 | 4387.9855 | 65622.8152 | 308.8018 | 240889.319 | -6544.3316
522.12 | 11.6318 | 2.5719 |  | 215387.145 | -78321.6506 | 598496.889 | 3629865.13 | 5341061.86 | -59980.3369 | 96239.4428 | 30714.0826 | 279160.305 | -266137.78 | 1401228.66 | -31751.4632 | 35052.3469 | 6138.7899 | 65028.3311 | -9246.227 | 211952.283 | -9267.2514
522.32 | 11.6564 | 2.6849 |  | 222436.143 | -57129.9473 | 556438.266 | 3205406.84 | 5507421.82 | -51356.6058 | 94469.1025 | 35403.3863 | 269744.834 | -316700.081 | 1333254.55 | -27033.7154 | 31711.9298 | 6611.1018 | 63250.6917 | -11602.5601 | 182749.645 | -7026.8556
522.52 | 11.6787 | 2.7929 |  | 220467.02 | -48684.7604 | 526592.42 | 3028526.63 | 5482980.12 | -51779.9172 | 92588.9547 | 36304.9034 | 264301.754 | -352338.987 | 1338451.08 | -28055.2508 | 30964.2072 | 8291.5742 | 62737.7126 | -22221.5263 | 175434.734 | -8581.4922
522.72 | 11.7015 | 2.9079 |  | 217185.545 | -46540.2261 | 492366.913 | 3011835.73 | 5533740.67 | -55147.7976 | 95746.667 | 37249.0584 | 257381.173 | -341653.79 | 1347280.93 | -31715.7611 | 29993.8919 | 7422.6753 | 61495.3891 | -17652.4812 | 162826.191 | -9269.7137
522.92 | 11.7344 | 3.0165 |  | 198364.203 | -51033.1801 | 462663.1 | 3192273.58 | 5156900.88 | -43533.4913 | 98390.8229 | 30442.3966 | 253068.203 | -312799.487 | 1353028.9 | -28026.1479 | 29911.4571 | 8135.3654 | 61426.7212 | -24436.3206 | 161223.355 | -8218.9761
523.12 | 11.7877 | 3.1518 |  | 196433.733 | -70009.9554 | 446414.402 | 3556443.33 | 5053736.88 | -42743.6679 | 97321.2345 | 26226.203 | 250480.457 | -207557.008 | 1374169 | -23677.7654 | 31770.7238 | 4772.2469 | 61106.9739 | -6679.7422 | 171702.241 | -7118.5874
523.32 | 11.8202 | 3.3547 |  | 156694.529 | -92530.6792 | 422598.738 | 4259866.86 | 4542336.14 | -36854.1558 | 110248.454 | 17098.5333 | 246053.252 | -166969.475 | 1572878.89 | -26378.4197 | 35806.6195 | 5798.1276 | 60262.6178 | -15044.7505 | 181845.543 | -7160.9465
523.52 | 11.8446 | 3.5061 |  | 131633.878 | -107828.899 | 405077.123 | 4751402.57 | 4064164.5 | -39614.038 | 115015.233 | 7070.3866 | 244199.562 | 14747.1329 | 1703389.08 | -31459.7323 | 39578.9806 | 1018.2738 | 61374.1347 | 9004.8968 | 202276.659 | -9757.6918
523.72 | 11.8797 | 3.6337 |  | 98423.2612 | -129297.409 | 399695.387 | 4983170.71 | 3170125.2 | -48262.3452 | 100768.692 | -3733.5406 | 239870.936 | 144269.385 | 1671647.28 | -29782.1966 | 45893.4756 | -1346.2585 | 59125.7351 | 21101.4839 | 270621.976 | -10100.0338
523.92 | 11.91 | 3.798 |  | 65937.2492 | -150177.251 | 398757.515 | 5470814.19 | 2682666.21 | -34338.909 | 105040.147 | -10764.8986 | 239427.219 | 213324.022 | 1692899.07 | -20831.8656 | 45749.7654 | -2709.4336 | 58831.8944 | 29016.2395 | 271949.184 | -7115.2344
524.12 | 11.9398 | 3.9732 |  | 58888.0893 | -228926.642 | 418853.756 | 7279659.47 | 2781365.44 | -45904.6505 | 125777.548 | -20265.4422 | 248430.607 | 249104.521 | 1770734.78 | -24002.6084 | 41826.2594 | -1317.1675 | 60669.7374 | 17891.0042 | 234534.676 | -6962.6435
524.32 | 11.9862 | 4.1509 |  | 48052.3435 | -289970.108 | 440106.752 | 8958494.63 | 2806485.33 | -62622.6377 | 146203.709 | -29611.1053 | 256912.323 | 369331.705 | 1946921.33 | -33002.799 | 43719.3849 | -3937.0059 | 63692.6965 | 30947.5943 | 227130.214 | -10874.5631
524.52 | 12.0371 | 4.379 |  | 6887.7785 | -318396.341 | 470277.975 | 9913728.62 | 1973583.23 | -54188.3612 | 156669.304 | -47324.5213 | 266751.412 | 530811.002 | 2149751.88 | -28473.8496 | 49548.8336 | -5325.3152 | 66124.6765 | 35153.3263 | 269711.166 | -8958.142
524.72 | 12.0734 | 4.6113 |  | -8068.225 | -346167.254 | 505167.617 | 10757615.4 | 1553944.17 | -63153.3848 | 160957.229 | -60350.9746 | 272952.946 | 783790.261 | 2358262.67 | -30497.6013 | 59719.7953 | -12433.0389 | 67089.3832 | 72901.1332 | 342416.689 | -9820.1041
524.92 | 12.1357 | 4.8357 |  | -6608.1885 | -384104.98 | 538162.133 | 11985236.2 | 1752660.65 | -70228.8447 | 185621.302 | -68960.1301 | 276807.923 | 845767.988 | 2577419.75 | -38496.4182 | 58143.7051 | -11408.6289 | 66382.0421 | 66630.0676 | 320231.221 | -11407.5494
525.12 | 12.1801 | 5.1265 |  | 22258.9925 | -406761.872 | 583440.071 | 12347072.2 | 2480846.92 | -84174.9891 | 190286.937 | -60428.7761 | 285613.697 | 755328.438 | 2581199.67 | -43447.1642 | 59260.6294 | -10437.1376 | 67942.9823 | 64694.7526 | 328884.973 | -12787.464
525.32 | 12.198 | 5.3756 |  | 19891.1278 | -371448.385 | 624964.751 | 11450384.3 | 2484311.41 | -72504.9722 | 181221.245 | -52599.9834 | 294461.61 | 664895.085 | 2665925.35 | -39405.8143 | 67680.3785 | -9267.5448 | 69741.4319 | 59952.7938 | 377929.044 | -11850.9153
525.52 | 12.243 | 5.5723 |  | 30239.3559 | -330871.288 | 659617.009 | 10391137.5 | 2532398.09 | -67586.2274 | 165423.628 | -44199.6753 | 302659.276 | 641142.74 | 2594315.22 | -40645.7808 | 68485.9916 | -10329.5056 | 71341.1954 | 67863.3345 | 383045.59 | -12363.1594
525.72 | 12.2767 | 5.838 |  | 47481.6738 | -296386.38 | 699814.752 | 9376806.76 | 2587550.65 | -53623.0426 | 152387.531 | -38631.6679 | 312733.975 | 572837.646 | 2387712.36 | -28016.9779 | 63993.8168 | -9456.8636 | 72328.0823 | 64151.6297 | 369025.142 | -6776.0248
525.92 | 12.3129 | 6.106 |  | 61937.5557 | -262310.653 | 717644.601 | 8637429.82 | 2910132.8 | -53858.0308 | 148537.36 | -29336.7005 | 316128.985 | 452359.164 | 2327311.9 | -37166.1296 | 61953.3675 | -6454.1248 | 72448.67 | 51055.0869 | 361604.406 | -11226.8961
526.12 | 12.3543 | 6.4124 |  | 108479.883 | -231516.941 | 735280.599 | 7689641.6 | 3756653.2 | -57709.1554 | 140552.838 | -12888.7751 | 321936.451 | 273051.899 | 2067722.05 | -40133.4135 | 50339.3541 | -3217.0563 | 74087.7538 | 36509.5523 | 286444.027 | -10943.1943
526.32 | 12.4017 | 6.7375 |  | 120361.431 | -166497.873 | 745978.617 | 5729858.57 | 3774796.76 | -58103.3403 | 112853.744 | 2533.7424 | 324550.955 | 33000.1426 | 1703649.95 | -39321.4357 | 43244.7052 | 2706.1152 | 73710.5033 | 5388.8733 | 250721.154 | -14887.3983
526.52 | 12.4325 | 7.0785 |  | 136539.251 | -100274.58 | 749752.127 | 3664970.79 | 3762559.72 | -46049.5358 | 82651.7994 | 17785.044 | 331383.167 | -124448.889 | 1203036.58 | -22415.6405 | 29758.1799 | 4079.0494 | 76206.4702 | 118.7451 | 177677.636 | -4619.7799
526.72 | 12.453 | 7.3945 |  | 141223.083 | -49882.9661 | 741102.492 | 2209623.52 | 3456222.35 | -48182.2046 | 55604.6716 | 24272.5166 | 332013.067 | -202643.87 | 932863.6 | -21046.5549 | 26314.5477 | 5663.0053 | 76239.2495 | -8543.5138 | 162297.822 | -4677.8527
526.92 | 12.4491 | 7.6801 |  | 163182.708 | -27585.0747 | 715583.04 | 1787774.13 | 3803435.48 | -54818.8477 | 55624.3599 | 28706.5329 | 327728.372 | -227965.454 | 830619.01 | -27818.4684 | 20614.8994 | 5360.2901 | 75705.4896 | -5966.0718 | 126298.457 | -6573.5858
527.12 | 12.4417 | 7.9028 |  | 182942.298 | -20789.8741 | 678348.255 | 1558112.37 | 4125055.96 | -70519.9806 | 52729.5482 | 33658.5895 | 317047.318 | -287068.648 | 735667.233 | -35956.9626 | 17986.3485 | 6325.7327 | 73473.0163 | -10678.9978 | 106874.246 | -10085.8022
527.32 | 12.4247 | 8.0861 |  | 187413.736 | 6847.3801 | 638936.765 | 956251.414 | 4239546.74 | -70272.2928 | 47664.9463 | 39114.7432 | 307537.887 | -351365.98 | 726597.755 | -34281.7527 | 19820.9205 | 7333.5162 | 72051.6603 | -15302.6035 | 106419.398 | -10142.4898
527.52 | 12.4286 | 8.2443 |  | 197328.851 | 7459.4344 | 597462.526 | 846402.816 | 4545848.77 | -74479.8971 | 47737.3726 | 44466.1252 | 297746.246 | -434291.118 | 666215.365 | -34529.1351 | 17199.9357 | 9105.9162 | 69647.9373 | -23804.8417 | 97363.157 | -9856.389
527.72 | 12.4064 | 8.4462 |  | 192398.473 | -8641.1986 | 559285.7 | 1221192.28 | 4594269.45 | -79864.0653 | 53693.4363 | 44489.7393 | 292236.258 | -470417.886 | 650915.828 | -39514.7334 | 12096.9694 | 10460.0011 | 69313.3698 | -31681.1086 | 67828.4735 | -10419.8727
527.92 | 12.3746 | 8.5851 |  | 169749.216 | -19959.907 | 520443.732 | 1521909.59 | 4131684 | -72264.9664 | 51504.3371 | 36990.1103 | 286018.978 | -338490.917 | 717710.887 | -36851.4935 | 16806.2327 | 6910.1383 | 69463.4008 | -14392.9489 | 90242.9399 | -11028.5775
528.12 | 12.3849 | 8.6861 |  | 140951.133 | -47585.7739 | 492954.216 | 2255468.22 | 3444937.78 | -63154.1674 | 54468.7186 | 22119.4657 | 279188.251 | -192978.702 | 758010.548 | -34684.9082 | 18575.4471 | 5247.3501 | 68080.1996 | -9982.6643 | 109784.224 | -11682.1254
528.32 | 12.3613 | 8.9033 |  | 108024.463 | -74080.2346 | 468480.587 | 2941459.82 | 2913015.11 | -46881.1204 | 67825.7168 | 11056.0279 | 272518.746 | -61234.9456 | 880344.453 | -29257.6097 | 16567.5579 | 2745.7441 | 66354.0286 | 2424.2429 | 86534.4599 | -7942.8157
528.52 | 12.3092 | 9.0244 |  | 74901.3761 | -110126.082 | 450794.827 | 3680290.88 | 2245754.42 | -59841.268 | 67109.5279 | -425.4611 | 266526.447 | 64961.5697 | 964933.161 | -37004.691 | 22955.5389 | 827.4192 | 65747.2867 | 9627.8238 | 121192.248 | -13727.5228
528.72 | 12.2972 | 9.0537 |  | 45262.6454 | -124103.165 | 443341.062 | 4046499.07 | 1701406.94 | -41943.7323 | 73123.6812 | -9842.1416 | 262624.36 | 186226.422 | 1044904.61 | -26790.9774 | 22770.8094 | -1468.9128 | 64259.9966 | 20219.7701 | 117733.49 | -9044.3147
528.92 | 12.2745 | 9.1731 |  | 29691.1485 | -174682.514 | 453659.537 | 5175577.57 | 1609739.68 | -47194.5189 | 85446.4356 | -16430.4236 | 264770.878 | 213576.227 | 1144663.32 | -28182.4742 | 23603.3982 | -712.0333 | 64174.0361 | 15434.7962 | 120567.06 | -10200.6906
529.12 | 12.2361 | 9.2609 |  | 21002.0778 | -222642.206 | 464969.855 | 6471265.75 | 1645730.46 | -60206.7319 | 107555.284 | -25723.5654 | 269544.536 | 294699.765 | 1209076.4 | -38835.9956 | 19885.0325 | -1891.7477 | 65859.1929 | 20756.7224 | 101279.633 | -12446.9502
529.32 | 12.1942 | 9.2746 |  | -19400.609 | -225228.207 | 489154.388 | 6531276.35 | 674779.926 | -51470.7805 | 99840.2723 | -37824.1171 | 275361.881 | 485461.5 | 1414935.18 | -29181.3904 | 32532.2701 | -6037.1313 | 68291.5433 | 38995.9584 | 167886.821 | -10397.0387
529.52 | 12.1612 | 9.2506 |  | -37543.8821 | -249950.301 | 507545.434 | 7275530.96 | 309468.991 | -58876.8545 | 101689.84 | -46813.2872 | 274893.445 | 605110.701 | 1519783.08 | -34972.239 | 39500.3092 | -8561.764 | 66543.2337 | 52656.0905 | 222033.986 | -12497.0684
529.72 | 12.128 | 9.2337 |  | -25154.8173 | -294285.822 | 535882.786 | 8401173.87 | 730248.727 | -63750.1765 | 122986.663 | -50707.2391 | 279251.461 | 629846.148 | 1632944.16 | -34763.1973 | 34549.216 | -8162.2358 | 66366.6858 | 50959.0183 | 191068.454 | -11804.9625
529.92 | 12.0654 | 9.1974 |  | -18479.4395 | -318148.691 | 572379.956 | 8949044.88 | 1005002.79 | -78027.7616 | 130214.48 | -50405.453 | 287223.663 | 605200.08 | 1743643.69 | -39336.6366 | 37942.6812 | -6834.6431 | 69082.525 | 42192.2525 | 200843.362 | -12316.377
530.12 | 12.0149 | 9.0925 |  | -37999.9171 | -264672.933 | 595015.182 | 8073467.05 | 650783.347 | -59556.4272 | 122843.568 | -48582.4103 | 287022.917 | 645601.528 | 1985464.7 | -39348.1709 | 52396.5434 | -8991.9861 | 68375.5601 | 55080.2361 | 289563.842 | -15427.5104
530.32 | 12.0232 | 9.0416 |  | -7624.6298 | -284847.719 | 638767.815 | 8384252.28 | 1169729.04 | -65812.7089 | 124364.45 | -45174.9252 | 295644.462 | 583018.365 | 1792018.27 | -38208.7122 | 45338.8729 | -7729.2716 | 68064.1553 | 53246.0499 | 276152.799 | -13610.8831
530.52 | 12.0193 | 9.1345 |  | 24191.1896 | -282902.571 | 671081.103 | 8129905.64 | 1784255.12 | -69750.9111 | 121327.265 | -34367.5933 | 303165.473 | 453794.155 | 1598302.27 | -36531.0923 | 35502.9799 | -5476.3271 | 69719.0487 | 41055.5673 | 195678.023 | -9810.7568
530.72 | 11.9878 | 9.1982 |  | 22986.111 | -219734.774 | 691983.751 | 6633406.25 | 1618981.25 | -52765.2043 | 104453.453 | -26320.3594 | 307209.791 | 339977.641 | 1568197.68 | -34244.9727 | 40971.5376 | -2729.7167 | 71114.7817 | 26824.1696 | 236059.266 | -12455.0102
530.92 | 11.9836 | 9.184 |  | 57426.8486 | -166068.986 | 707144.435 | 5179034.4 | 2044386.15 | -59818.51 | 84741.5053 | -12615.1293 | 307957.607 | 262270.058 | 1309620.84 | -39010.1756 | 34819.3941 | -3313.2846 | 70030.7339 | 34593.7556 | 209545.795 | -14832.9307
531.12 | 11.9546 | 9.2076 |  | 64864.5639 | -101908.39 | 708965.782 | 3436296.37 | 1985389.68 | -45542.7528 | 67874.7771 | -1134.5883 | 307514.534 | 71169.0005 | 1008057.44 | -28871.1651 | 23114.8436 | 1445.4848 | 69707.336 | 8326.0029 | 127359.015 | -8787.3659
531.32 | 11.8935 | 9.1467 |  | 84622.0187 | -44607.4617 | 702954.838 | 1940679.21 | 2152757.69 | -43702.505 | 46536.7883 | 10686.3495 | 307913.604 | -37548.6332 | 802835.107 | -21098.253 | 21478.1485 | 2329.2825 | 70518.9869 | 4998.3206 | 121843.027 | -7527.8239
531.52 | 11.8635 | 8.9538 |  | 122811.038 | -25891.8997 | 685855.686 | 1621823.82 | 2907017.3 | -56729.408 | 49760.9496 | 19883.2148 | 303201.796 | -143124.275 | 692222.766 | -28676.454 | 14992.651 | 3955.3286 | 69095.5207 | -1283.8106 | 80205.0694 | -8021.8597
531.72 | 11.8496 | 8.8303 |  | 146901.671 | -7369.6105 | 664967.682 | 1161805.21 | 3439881.84 | -65462.9871 | 50035.051 | 29592.3029 | 297973.925 | -262879.981 | 646381.625 | -35621.8326 | 11986.5708 | 6122.7547 | 68003.0521 | -10206.0341 | 52559.8617 | -11571.6523
531.92 | 11.8237 | 8.7653 |  | 168050.494 | 3979.1351 | 635771.6 | 808407.95 | 3814778.54 | -69268.7799 | 45816.8288 | 36087.8654 | 292268.182 | -347267.178 | 506861.935 | -34301.6485 | 8209.2657 | 7527.4346 | 67395.9554 | -17062.1019 | 40743.7728 | -9343.3909
532.12 | 11.8357 | 8.6987 |  | 174778.114 | 23981.2335 | 600618.871 | 355697.882 | 3893633.31 | -66246.1838 | 39471.9491 | 39804.6665 | 285381.38 | -373103.254 | 511206.482 | -31109.1544 | 9977.3918 | 7594.0207 | 66737.6485 | -18350.0572 | 49524.0464 | -8536.1907
532.32 | 11.8356 | 8.729 |  | 180525.411 | 28654.4622 | 572346.949 | 202467.137 | 3996473.48 | -73351.3444 | 35511.3795 | 42567.4285 | 278470.233 | -410079.586 | 500624.669 | -34823.0263 | 11454.3892 | 8387.9632 | 64953.9104 | -21752.8223 | 62671.9439 | -10617.9529
532.52 | 11.7989 | 8.7415 |  | 181229.359 | 12734.3681 | 537019.603 | 518319.79 | 4082228.06 | -74062.4808 | 36473.3447 | 42829.6089 | 271981.456 | -423798.638 | 510433.447 | -33223.4325 | 12821.4735 | 8642.3719 | 64499.5591 | -23155.1915 | 73334.6298 | -8827.7974
532.72 | 11.7642 | 8.6434 |  | 176995.705 | -2158.2897 | 498502.061 | 1003374.07 | 3990318.44 | -73924.0882 | 44855.677 | 36344.5667 | 263204.159 | -346330.246 | 577089.037 | -38708.7424 | 10594.2909 | 7403.0389 | 62968.1216 | -18549.5158 | 52690.2475 | -11540.0487
532.92 | 11.7224 | 8.5298 |  | 161143.493 | -20255.9416 | 462811.021 | 1373185.8 | 3648720.97 | -67982.9006 | 44604.3162 | 29941.6157 | 253055.55 | -260686.884 | 614984.469 | -35592.6148 | 14191.9549 | 5471.4201 | 60805.4267 | -9740.7991 | 79173.7026 | -10929.9413
533.12 | 11.6848 | 8.3954 |  | 137369.756 | -37719.8961 | 429983.95 | 1863152.3 | 3315487.01 | -55740.7877 | 48700.8581 | 23569.1933 | 245268.321 | -203980.22 | 738147.957 | -25598.5273 | 19827.8944 | 4824.5031 | 60036.0161 | -9545.9591 | 104963.031 | -6329.8651
533.32 | 11.6753 | 8.2828 |  | 118389.887 | -56583.6013 | 402485.895 | 2774927 | 3372963.95 | -47801.8155 | 71029.0995 | 17744.9455 | 238113.996 | -126985.843 | 1120758.35 | -29855.5717 | 29674.5831 | 3324.1219 | 58635.1379 | -1334.6872 | 165198.054 | -10568.2968
533.52 | 11.6946 | 8.2673 |  | 113998.873 | -120804.793 | 392511.527 | 4448593.66 | 3650331.77 | -53281.9268 | 99377.2174 | 9453.5022 | 237061.825 | -84558.1561 | 1306975.17 | -34150.6958 | 27279.1016 | 4163.231 | 58216.394 | -6364.8662 | 140972.106 | -11244.8822
533.72 | 11.7288 | 8.3542 |  | 88452.2287 | -158334.911 | 392338.038 | 5463804.08 | 3266652.2 | -51436.5972 | 111177.574 | -2177.1173 | 239801.862 | 56883.7316 | 1474868.46 | -36029.525 | 30738.8846 | 1686.8854 | 59884.4847 | 3728.0189 | 149544.45 | -11887.3879
533.92 | 11.7696 | 8.5198 |  | 40414.6549 | -181165.838 | 404578.863 | 5897361.86 | 2145041.34 | -47710.7022 | 103258.961 | -17543.9809 | 243585.809 | 252364.913 | 1564685.87 | -30802.9474 | 39898.3007 | -2205.7101 | 61199.7675 | 21421.9216 | 222637.513 | -10808.1164
534.12 | 11.7872 | 8.6998 |  | 7814.111 | -210864.318 | 420973.419 | 6592157.24 | 1398556.67 | -50123.3215 | 107732.948 | -31675.885 | 245304.191 | 426512.948 | 1594838.39 | -33924.1057 | 39054.8026 | -5407.1508 | 60112.354 | 39071.1059 | 223283.533 | -13425.7213
534.32 | 11.7637 | 8.7924 |  | -11480.7852 | -243904.507 | 443162.906 | 7155406.12 | 874322.078 | -53444.6234 | 106064.938 | -41116.0651 | 250445.913 | 537990.077 | 1536201.83 | -27328.0707 | 37645.2793 | -7697.6222 | 61602.4953 | 48257.2402 | 209238.571 | -6844.6573
534.52 | 11.736 | 8.7301 |  | -34229.3708 | -247260.192 | 465499.949 | 7379524.96 | 516232.946 | -48578.58 | 107486.09 | -46072.4063 | 251573.281 | 603741.018 | 1693889.85 | -27456.524 | 44687.9961 | -8790.2029 | 60794.8443 | 53303.7382 | 255295.154 | -10026.3869
534.72 | 11.7175 | 8.6328 |  | -22182.6618 | -291734.594 | 498189.287 | 8441784.69 | 977292.549 | -62206.7444 | 124785.815 | -46915.2971 | 259481.546 | 580429.451 | 1784531.35 | -33063.9043 | 42124.9997 | -7301.8838 | 61972.2429 | 44927.5873 | 231870.293 | -9384.693
534.92 | 11.6773 | 8.5193 |  | -10289.4935 | -322564.653 | 532675.315 | 9389998.29 | 1409473.76 | -67792.0334 | 141235.566 | -48705.5655 | 268766.469 | 601979.022 | 1988204.97 | -35635.5872 | 46038.3851 | -7603.6753 | 64567.5614 | 46495.77 | 249967.983 | -10991.1295
535.12 | 11.6597 | 8.3388 |  | -10024.0377 | -332997.41 | 562115.728 | 9977429.94 | 1526070.55 | -74935.8804 | 153427.854 | -52870.7547 | 275464.7 | 670081.167 | 2185846.26 | -40898.0016 | 52331.6221 | -9240.1445 | 66683.914 | 55763.7023 | 280087.154 | -12136.8192
535.32 | 11.6817 | 8.2351 |  | -10236.5705 | -307855.518 | 585169.74 | 9707754.01 | 1468729.52 | -68511.1322 | 155205.838 | -54384.3169 | 274181.501 | 727062.06 | 2346914.71 | -44717.3462 | 60942.5847 | -11092.6646 | 64602.8361 | 68438.5967 | 348808.665 | -16530.9777
535.52 | 11.6938 | 8.2619 |  | 14110.853 | -313594.021 | 624991.179 | 9484908.65 | 1800643.38 | -74194.9655 | 150562.808 | -48547.6142 | 282793.678 | 616085.403 | 2101739.72 | -41893.5004 | 48645.1445 | -7746.6886 | 65503.9341 | 52110.2609 | 275029.81 | -13334.9517
535.72 | 11.6893 | 8.2643 |  | 21800.7798 | -254289.981 | 645564.639 | 7868175.22 | 1894561.49 | -58433.511 | 130758.037 | -33826.2138 | 285537.928 | 467594.03 | 1849243.74 | -39148.314 | 41301.6035 | -5824.3148 | 65626.3206 | 43315.3434 | 228054.998 | -12282.0932
535.92 | 11.6903 | 8.2015 |  | 22907.1151 | -170300.638 | 663418.07 | 5357967.06 | 1537857.13 | -44985.6975 | 85886.0983 | -17558.9909 | 288705.471 | 272039.158 | 1438680.93 | -30343.8417 | 40573.3125 | -2620.7631 | 65951.3224 | 28947.9195 | 245080.8 | -12373.604
536.12 | 11.6733 | 8.1385 |  | 38127.0916 | -105001.026 | 686166.581 | 3335847.99 | 1481513.19 | -39666.6417 | 57821.9733 | -4228.0151 | 296309.332 | 112514.088 | 940761.173 | -24403.5873 | 26536.1023 | 98.9444 | 67090.0756 | 15761.8147 | 170834.856 | -7529.0533
536.32 | 11.6348 | 8.0016 |  | 51044.7551 | -51103.4908 | 687166.404 | 1874197.29 | 1441878.93 | -35258.3984 | 39379.7788 | 4549.3331 | 299007.728 | 13760.8987 | 630950.057 | -20856.0821 | 18497.7004 | 1434.2726 | 68356.3316 | 8936.0488 | 123945.269 | -4085.536
536.52 | 11.6073 | 7.7769 |  | 68918.4386 | -3.176 | 673908.026 | 905786.354 | 1666981.62 | -30946.6282 | 32713.0228 | 11350.4768 | 295956.556 | -31946.7631 | 698716.021 | -16792.6727 | 21964.3715 | 1655.4857 | 67732.5908 | 8215.4129 | 128575.39 | -5509.6822
536.72 | 11.5805 | 7.5369 |  | 132999.573 | -24907.6532 | 655784.538 | 1609904.06 | 3109550.04 | -63578.891 | 52388.1813 | 21459.946 | 289303.079 | -151892.967 | 718175.096 | -33889.1579 | 14724.3564 | 3816.6043 | 65655.7021 | -517.6376 | 73678.4244 | -10023.6281
536.92 | 11.5571 | 7.3147 |  | 166821.483 | -23880.7833 | 622581.567 | 1629845.11 | 3968315.52 | -76853.0682 | 59226.615 | 32097.4204 | 281425.53 | -304232.37 | 748638.415 | -40516.7526 | 13409.8553 | 7153.599 | 64658.7865 | -16847.9228 | 61460.6008 | -11781.0146
537.12 | 11.5464 | 7.117 |  | 177304.645 | 6604.0435 | 587811.537 | 793121.024 | 4080928.38 | -77022.7842 | 42744.5703 | 40359.866 | 274080.972 | -377303.059 | 686696.252 | -37049.6109 | 18689.7984 | 7736.6868 | 63859.983 | -18790.1468 | 109826.935 | -12570.8376
537.32 | 11.5246 | 6.9528 |  | 176870.091 | 25538.7654 | 556159.682 | 372363.796 | 4000554.44 | -59917.6323 | 40265.3558 | 41270.3272 | 268595.538 | -407278.38 | 630165.945 | -26783.717 | 15943.3164 | 8561.8312 | 62805.5039 | -23144.4122 | 99816.6297 | -6746.4594
537.52 | 11.5153 | 6.7659 |  | 189695.452 | 14212.2887 | 519819.959 | 852480.105 | 4380545.95 | -64887.0508 | 53400.0831 | 40741.2226 | 260942.747 | -377984.365 | 701901.674 | -31387.5964 | 13505.986 | 7325.6778 | 61666.7498 | -16891.8836 | 70571.1492 | -7720.1854
537.72 | 11.5079 | 6.5942 |  | 187914.544 | -7356.4758 | 487060.767 | 1501275.04 | 4491792.31 | -65554.4135 | 64544.8451 | 37279.7426 | 252921.754 | -372024.959 | 819999.06 | -36667.2075 | 15658.7693 | 8123.3525 | 59971.4386 | -21402.4716 | 84079.0861 | -12525.9777
537.92 | 11.4726 | 6.4253 |  | 181021.519 | -27420.8865 | 453689.259 | 2049593.52 | 4358006.43 | -58165.6308 | 70295.5518 | 30277.9327 | 246501.155 | -298683.501 | 886290.056 | -28918.3776 | 17546.0736 | 7106.099 | 59803.4211 | -19243.447 | 90990.2795 | -8522.8242
538.12 | 11.4587 | 6.2158 |  | 166876.013 | -47408.1558 | 422174.071 | 2581140.98 | 4103720.11 | -56565.7862 | 72717.7841 | 23894.6055 | 237193.409 | -192977.134 | 1021234.67 | -32618.025 | 22974.7508 | 4649.0194 | 57614.6352 | -7507.0075 | 116238.815 | -11292.2238
538.32 | 11.4573 | 6.0876 |  | 141895.387 | -50939.5145 | 392782.367 | 2811770.74 | 3773608.4 | -42753.3028 | 75277.8811 | 19216.3491 | 229350.397 | -137905.374 | 1199922.1 | -27430.3322 | 31209.611 | 3561.7449 | 56563.8467 | -4694.1209 | 150321.343 | -8062.5244
538.52 | 11.4128 | 5.9848 |  | 105325.636 | -59594.9549 | 370122.82 | 2994000.99 | 3190083.59 | -46213.9643 | 74984.4146 | 13598.4421 | 222509.061 | -89475.2977 | 1325723.85 | -30053.5703 | 38021.203 | 3153.8962 | 54919.965 | -1321.2006 | 222744.33 | -10726.7411
538.72 | 11.3919 | 5.7665 |  | 92485.0046 | -96495.1998 | 361494.308 | 3948904.61 | 2977461.5 | -40437.6762 | 88648.9146 | 2904.7103 | 221926.06 | 48531.8806 | 1358417.64 | -30424.3817 | 33136.231 | 398.3647 | 54978.6175 | 12061.3928 | 189497.269 | -9977.3268
538.92 | 11.3896 | 5.5896 |  | 60607.9146 | -135270.387 | 360267.983 | 4737815.57 | 2378203.51 | -46600.6208 | 92525.529 | -7871.9862 | 221324.024 | 152028.218 | 1412149.33 | -31301.0234 | 32825.3978 | -770.3568 | 54946.1914 | 15015.8022 | 176331.918 | -8035.0115
539.12 | 11.3627 | 5.4573 |  | 17850.588 | -147872.667 | 363552.337 | 5051797.17 | 1520406.03 | -38196.9133 | 82565.6007 | -18095.5374 | 221359.197 | 315163.051 | 1609094.47 | -21992.61 | 51532.8069 | -5378.7902 | 55563.1153 | 38377.4637 | 307640.02 | -9054.2527
539.32 | 11.339 | 5.2605 |  | 6241.7439 | -206022.534 | 374456.832 | 6808165.24 | 1504952.31 | -46929.2577 | 112619.707 | -32640.876 | 223865.562 | 446641.236 | 1757840.02 | -30775.0681 | 45819.2829 | -6295.304 | 55190.0638 | 42440.3871 | 258614.751 | -9380.006
539.52 | 11.3243 | 5.061 |  | 867.4832 | -271593.035 | 400754.878 | 8409058.57 | 1479888.57 | -58185.1522 | 130768.217 | -44739.8917 | 229846.022 | 574420.597 | 1870211.16 | -31112.7053 | 44438.9706 | -8011.5587 | 56410.152 | 49001.7091 | 248172.723 | -9694.8154
539.72 | 11.2985 | 4.8786 |  | -29687.3435 | -288378.717 | 420983.425 | 9004467.41 | 977650.138 | -55203.1269 | 136105.03 | -53281.7876 | 231897.928 | 668601.185 | 2055190.3 | -33234.3194 | 52686.5576 | -9654.9963 | 56895.9426 | 56463.2549 | 294113.435 | -12276.0135
539.92 | 11.2844 | 4.658 |  | -33491.2816 | -300735.915 | 456858.234 | 9367577.4 | 820938.144 | -48484.0538 | 141662.517 | -60219.2531 | 238824.136 | 777666.109 | 2150825.98 | -25876.4918 | 54203.4228 | -12115.5178 | 57927.0175 | 69376.18 | 305267.479 | -8309.0895
540.12 | 11.2706 | 4.4527 |  | -35573.2447 | -312419.316 | 487660.121 | 9931403.34 | 957341.788 | -58425.0198 | 155180.33 | -63557.0048 | 243241.672 | 835010.377 | 2410163.58 | -30578.3305 | 61054.1521 | -13251.1333 | 58641.2917 | 72719.7017 | 329806.779 | -9497.0333
540.32 | 11.2526 | 4.2713 |  | -15972.3478 | -337504.299 | 518562.699 | 10596403 | 1479250.42 | -72555.5301 | 166184.543 | -60958.2929 | 249200.935 | 792888.156 | 2484182.56 | -40861.6812 | 62359.4986 | -12310.4497 | 59489.749 | 72187.5644 | 345266.41 | -11865.2022
540.52 | 11.2255 | 4.0698 |  | -719.8871 | -318483.35 | 548509.521 | 10247876.5 | 1740338.78 | -68740.8839 | 165696.008 | -57257.2307 | 253348.534 | 784204.696 | 2522971.26 | -37330.0596 | 63722.37 | -12904.3988 | 59765.6391 | 76027.0389 | 351041.785 | -11451.0054
540.72 | 11.2291 | 3.8516 |  | 9435.56 | -316934.938 | 581055.83 | 9940350.84 | 1853567.63 | -63146.9833 | 156848.715 | -51570.5367 | 261818.157 | 682724.613 | 2329118.84 | -34379.2477 | 58373.9256 | -10504.0309 | 60940.0803 | 65984.0128 | 331978.3 | -9926.3439
540.92 | 11.219 | 3.7064 |  | 26318.5726 | -278559.788 | 602512.396 | 8793379.14 | 2040936.15 | -59260.0502 | 139867.847 | -39529.7867 | 265258.081 | 572653.801 | 2093639.26 | -35252.9168 | 52111.7213 | -9233.13 | 61167.642 | 63319.0139 | 300459.576 | -11120.9232
541.12 | 11.1794 | 3.5144 |  | 22322.9935 | -225561.324 | 626615.337 | 7152863.68 | 1706760.7 | -33789.823 | 112922.097 | -30564.4254 | 272101.377 | 423978.422 | 1794474.08 | -20582.3747 | 48974.2142 | -6129.3825 | 62645.5706 | 47537.7501 | 283413.919 | -6026.6583
541.32 | 11.1763 | 3.2566 |  | 39469.9762 | -158530.92 | 632358.535 | 5517652.33 | 1820989.28 | -26746.7586 | 95250.5731 | -20293.9653 | 271220.957 | 372043.995 | 1658658.65 | -22398.9504 | 47174.2328 | -6292.815 | 61700.3087 | 48610.2353 | 286155.872 | -8619.0496
541.52 | 11.1712 | 3.0877 |  | 76026.666 | -140204.865 | 641919.829 | 4812493.18 | 2485376.68 | -39822.2677 | 87881.9237 | -6889.676 | 274043.866 | 163293.138 | 1386643.36 | -21671.8184 | 37078.6154 | -1402.2699 | 62211.4239 | 24344.9501 | 223285.161 | -5484.9384
541.72 | 11.1454 | 2.9336 |  | 97253.5735 | -92133.393 | 636557.184 | 3665750.69 | 2931505.48 | -39556.3678 | 81795.4313 | 6459.6369 | 273493.891 | 10526.887 | 1363975.95 | -22193.3675 | 36267.0976 | 1405.8123 | 62168.2668 | 9717.1305 | 205840.163 | -7072.8355
541.92 | 11.1405 | 2.7173 |  | 131524.602 | -71557.6069 | 625638.766 | 3158827 | 3539749.1 | -47552.1458 | 75602.2291 | 16225.8415 | 272601.394 | -81352.1718 | 1311751.86 | -25925.907 | 37117.8427 | 2435.077 | 62591.1716 | 6073.2479 | 223070.99 | -7973.8696
542.12 | 11.1437 | 2.5488 |  | 158428.458 | -46665.2714 | 603862.413 | 2791045.11 | 4103556.74 | -49117.0636 | 81969.7056 | 23218.1754 | 267516.322 | -158323.041 | 1355374.74 | -30293.0048 | 35659.1893 | 3849.658 | 61444.1718 | 283.8422 | 207873.795 | -9162.34
542.32 | 11.1286 | 2.3996 |  | 184797.874 | -51325.7401 | 575039.264 | 2806934.91 | 4594867.52 | -55996.7231 | 82059.0798 | 28514.1497 | 262209.994 | -253164.995 | 1221928.69 | -31102.8803 | 30233.983 | 6139.9873 | 60699.116 | -10522.5285 | 190810.279 | -8339.902
542.52 | 11.1215 | 2.207 |  | 196257.137 | -24160.0146 | 539333.043 | 2208101.13 | 4699440.93 | -54573.9821 | 72685.3448 | 32626.5765 | 253781.334 | -260354.83 | 1185617.91 | -28100.6715 | 33434.7501 | 4908.5145 | 59342.4538 | -3893.1311 | 205095.235 | -8158.2829
542.72 | 11.1213 | 2.0241 |  | 193249.188 | -8765.8387 | 498671.441 | 2009958.46 | 4768698.04 | -39958.3268 | 74673.6945 | 35123.1998 | 243797.28 | -294056.952 | 1323168.85 | -19612.4025 | 39571.5841 | 5100.6789 | 57668.7034 | -7913.0918 | 216363.516 | -4577.0551
542.92 | 11.1007 | 1.8377 |  | 215074.344 | -45613.7726 | 464961.302 | 2948879.2 | 5368149.92 | -65038.9349 | 89770.7118 | 35002.4135 | 236618.068 | -315804.464 | 1369876.98 | -37465.8894 | 34962.1766 | 6837.7191 | 56345.8162 | -14968.6692 | 201699.17 | -10643.5243
543.12 | 11.0881 | 1.6106 |  | 206450.26 | -52793.8034 | 426593.352 | 3053639.93 | 5225042.54 | -60534.3503 | 87541.4002 | 33735.2086 | 227906.858 | -294704.412 | 1348638.81 | -35019.5246 | 35414.9465 | 5969.9717 | 54906.2351 | -10356.6403 | 209130.366 | -10303.4329
543.32 | 11.0611 | 1.3857 |  | 168483.797 | -35943.1646 | 393144.234 | 2596967.26 | 4350164.94 | -49803.8913 | 76382.7472 | 27289.7647 | 220229.974 | -224030.51 | 1325864.49 | -28750.4528 | 37212.6046 | 4867.334 | 53757.9785 | -5951.0726 | 222246.08 | -9765.9909
543.52 | 11.0576 | 1.1391 |  | 151135.755 | -43230.9006 | 368275.808 | 2754540.87 | 3904582.73 | -37363.8387 | 76648.6704 | 19180.3496 | 213889.966 | -103797.1 | 1275523.8 | -19501.8213 | 34464.2791 | 1829.7177 | 52458.1386 | 9384.9775 | 210087.308 | -6456.44
543.72 | 11.056 | 1.0366 |  | 127902.069 | -75479.4722 | 347089.524 | 3571089.52 | 3626488.12 | -35373.7469 | 86370.4698 | 11697.0442 | 208214.933 | -73286.0771 | 1354816.39 | -22509.4755 | 35060.6261 | 2740.8834 | 51126.8962 | 2330.9891 | 203673.399 | -6777.757
543.92 | 11.0438 | 1.0301 |  | 109990.493 | -98706.6283 | 330548.494 | 4175293.47 | 3385656.08 | -42464.9023 | 93228.0974 | 5295.7947 | 204748.52 | 13752.0805 | 1460981.19 | -27842.5344 | 37373.007 | 853.2162 | 50929.6837 | 10771.4234 | 217997.749 | -9373.0364
544.12 | 11.0577 | 1.0334 |  | 84903.1658 | -117691.529 | 326686.441 | 4549996.52 | 2907827.18 | -38063.3127 | 93589.451 | -1863.1964 | 203172.167 | 105182.794 | 1509588.49 | -25072.3533 | 41041.353 | -1256.4807 | 50380.4082 | 20089.7384 | 238791.516 | -7728.4534
544.32 | 11.0807 | 1.0342 |  | 54231.4601 | -137240.605 | 326481.075 | 5151271.81 | 2498195.97 | -38607.3601 | 101041.945 | -9127.6548 | 203595.164 | 193429.717 | 1700555.68 | -28209.8669 | 46746.6894 | -2861.1474 | 50832.8301 | 27746.6291 | 258336.426 | -7602.4042
544.52 | 11.0956 | 1.0341 |  | 33802.4514 | -183919.268 | 340493.215 | 6163967.24 | 2157893.18 | -42816.7205 | 106115.102 | -18600.3787 | 208138.327 | 283883.437 | 1745796.74 | -29577.1219 | 47821.2603 | -3753.7136 | 51596.0145 | 33145.5115 | 285557.14 | -9051.371
544.72 | 11.0732 | 1.0341 |  | 7901.8569 | -218479.163 | 350968.31 | 7074212.41 | 1573088.06 | -43014.0306 | 111310.403 | -31997.5498 | 212577.666 | 438668.759 | 1748328.2 | -25906.8744 | 46155.4767 | -6498.3744 | 52844.9303 | 47486.6226 | 283645.535 | -8003.308
544.92 | 11.0991 | 1.0341 |  | -16380.4229 | -246302.635 | 374723.99 | 7904857.56 | 1012631.36 | -39875.7196 | 120017.659 | -46999.342 | 216680.367 | 629106.266 | 1869805.17 | -23083.1774 | 48042.9797 | -9921.232 | 53271.9885 | 60314.1834 | 283142.586 | -9008.17
545.12 | 11.1026 | 1.0341 |  | -28700.9369 | -284215.886 | 405309.585 | 8965055.56 | 949338.207 | -45266.6667 | 137102.163 | -55366.2552 | 222782.474 | 714440.795 | 2052912.05 | -25466.6791 | 51141.5696 | -11086.8932 | 54368.6849 | 63161.6928 | 285918.237 | -8076.8243
545.32 | 11.0802 | 1.0341 |  | -40432.9799 | -296711.044 | 429448.542 | 9598375.69 | 899012.385 | -46122.3515 | 152554.543 | -61823.5209 | 226333.193 | 777326.276 | 2319672.67 | -28899.6627 | 57748.28 | -11393.9925 | 55213.8762 | 61940.9044 | 311471.047 | -9570.7979
545.52 | 11.0777 | 1.0341 |  | -28814.1747 | -309848.045 | 464835.555 | 10091689.7 | 1187991.16 | -53100.2597 | 162031.602 | -63356.9253 | 232937.506 | 857599.901 | 2520411.34 | -28464.8719 | 64330.291 | -14619.8584 | 56762.545 | 77181.1004 | 337533.332 | -8260.8301
545.72 | 11.1051 | 1.0341 |  | -19799.0446 | -325888.497 | 504309.8 | 10691057.6 | 1500890.93 | -54091.6224 | 175285.743 | -64939.7153 | 241764.25 | 887562.975 | 2724063.76 | -27979.3091 | 68856.5243 | -15167.8574 | 58287.7407 | 79871.1175 | 360468.444 | -6085.3036
545.92 | 11.1184 | 1.0341 |  | -7482.3182 | -331821.822 | 534469.069 | 11146553.7 | 1805636.32 | -63379.0448 | 185072.394 | -65096.596 | 247285.031 | 908727.896 | 2920060.31 | -37423.5136 | 73915.2076 | -15458.9697 | 59495.5876 | 85153.784 | 393053.664 | -9712.1226
546.12 | 11.1427 | 1.0341 |  | 23455.1667 | -336093.099 | 567667.617 | 11288162.2 | 2339463.6 | -68083.7872 | 188290.826 | -61288.106 | 254306.939 | 880600.892 | 2850655.4 | -40038.7774 | 72279.2786 | -16172.3575 | 60040.1578 | 95480.0151 | 399412.239 | -10281.3441
546.32 | 11.1905 | 1.0341 |  | 41169.4726 | -295417.399 | 593478.102 | 10192103.7 | 2652548.81 | -59960.1395 | 176864.457 | -49104.3884 | 258305.438 | 739373.891 | 2724875.53 | -40072.3599 | 69069.646 | -13481.255 | 60149.4674 | 84394.3769 | 385312.74 | -10956.1801
546.52 | 11.2117 | 1.0341 |  | 49138.1331 | -235632.399 | 617065.931 | 8241035.53 | 2647760.02 | -37699.8811 | 144888.365 | -31726.6543 | 264569.672 | 510273.046 | 2363894.66 | -26967.0104 | 65105.7639 | -9466.7696 | 60719.1463 | 67578.1957 | 376045.117 | -7097.3975
546.72 | 11.242 | 1.0341 |  | 63948.5062 | -166284.635 | 634250.82 | 6314748.16 | 2705916.05 | -20800.4976 | 123285.882 | -18851.9051 | 270615.443 | 371164.691 | 2107609.15 | -15740.5747 | 57830.9039 | -6638.3125 | 61939.762 | 53225.5574 | 341610.507 | -4390.0655
546.92 | 11.2643 | 1.0341 |  | 103679.664 | -160284.955 | 645335.656 | 5816021.42 | 3373316.1 | -39790.4819 | 112812.269 | -5368.3709 | 276860.277 | 186696.225 | 1847308.66 | -20492.8815 | 49933.7376 | -2928.2336 | 63273.6743 | 34725.1275 | 295260.676 | -3547.744
547.12 | 11.258 | 1.0341 |  | 123173.721 | -129009.45 | 642351.759 | 5089133.29 | 3749082.53 | -43919.0851 | 108217.612 | 4289.1762 | 277235.489 | 62690.5563 | 1811995.24 | -29208.7623 | 50731.9252 | -312.1879 | 63471.2468 | 23131.9364 | 296610.557 | -8507.206
547.32 | 11.2588 | 1.0341 |  | 153161.567 | -118620.883 | 630452.427 | 4755756.37 | 4218787.31 | -46120.5149 | 101969.697 | 11383.4004 | 276584.614 | 9924.9772 | 1700626.02 | -24368.7708 | 48184.5109 | -434.3324 | 63641.3658 | 25564.4405 | 292453.529 | -5915.9402
547.52 | 11.2846 | 1.0341 |  | 176599.89 | -99704.3316 | 612574.192 | 4403601.26 | 4618180.66 | -49557.6057 | 99459.6772 | 17129.4146 | 271263.489 | -47036.9622 | 1691578.57 | -28156.3736 | 48885.2613 | 543.4139 | 62367.9636 | 20528.4298 | 294193.991 | -7721.8956
547.72 | 11.2866 | 1.0341 |  | 198268.043 | -93570.6518 | 580051.34 | 4354971.83 | 5173376.98 | -48274.764 | 105331.285 | 24491.1023 | 264164.439 | -167170.081 | 1677473.15 | -29841.1985 | 45357.6987 | 3516.269 | 61002.5027 | 6626.8403 | 278425.022 | -7264.8182
547.92 | 11.2984 | 1.0341 |  | 220926.31 | -76163.9418 | 552954.238 | 4044479.65 | 5648582.61 | -46512.1979 | 105897.684 | 30567.6554 | 258854.588 | -209857.704 | 1726778.57 | -26738.9091 | 48686.1777 | 3216.6095 | 60553.8174 | 8183.9701 | 291981.77 | -7333.2941
548.12 | 11.349 | 1.0341 |  | 232560.767 | -77863.1952 | 516552.159 | 4194014.46 | 6047728 | -47808.9775 | 112360.168 | 34499.8456 | 250482.881 | -274475.2 | 1814103.95 | -27417.5454 | 49179.4398 | 5101.1928 | 59019.8299 | -4002.3907 | 279744.484 | -8279.4278
548.32 | 11.3605 | 1.0341 |  | 237599.031 | -89625.3422 | 483778.825 | 4435633.88 | 6193424.63 | -54496.9632 | 115574.69 | 35161.8353 | 246382.974 | -318346.799 | 1763890.83 | -30670.2141 | 44815.8715 | 6895.1639 | 58989.1853 | -12329.4105 | 261505.947 | -8997.2167
548.52 | 11.3768 | 1.0341 |  | 220714.957 | -87348.7183 | 452043.344 | 4299456.79 | 5784532.88 | -45870.1893 | 111535.622 | 31187.7059 | 240500.406 | -276644.068 | 1668616.42 | -29979.0314 | 44511.9263 | 5444.166 | 57789.9713 | -3815.6746 | 268417.091 | -9127.0839
548.72 | 11.4126 | 1.0341 |  | 193236.145 | -102808.914 | 417023.788 | 4587546.72 | 5165057.62 | -43201.3941 | 110381.224 | 21644.1428 | 234583.945 | -197487.31 | 1594046.93 | -27210.176 | 39811.2875 | 5066.1447 | 57365.6548 | -6058.6101 | 237292.636 | -8109.0347
548.92 | 11.4189 | 1.0341 |  | 165738.647 | -100163.301 | 388782.758 | 4418638.82 | 4522859.14 | -44531.2723 | 101391.3 | 15625.3839 | 226991.432 | -67962.4255 | 1550754.56 | -26965.5652 | 40687.7078 | 1212.2729 | 55945.4933 | 12493.6028 | 237687.659 | -8394.0527
549.12 | 11.4267 | 1.0341 |  | 124087.119 | -102262.409 | 371703.113 | 4397214.42 | 3601041.42 | -30782.2638 | 96123.2532 | 4444.5534 | 222128.198 | 3172.4056 | 1577579.68 | -19270.4228 | 42801.2097 | 1777.5308 | 54755.1866 | 6322.5855 | 252208.392 | -7792.7826
549.32 | 11.468 | 1.0341 |  | 112841.877 | -139675.719 | 361163.735 | 5338299.62 | 3606381.2 | -25291.2176 | 112916.84 | -1645.5587 | 221562.245 | 72676.8146 | 1571820.6 | -18673.0127 | 35160.4224 | 334.3913 | 54649.5615 | 14468.4847 | 208380.463 | -4303.5946
549.52 | 11.4904 | 1.0341 |  | 84553.9912 | -173491.857 | 364264.195 | 6244343.98 | 3251333.79 | -32142.9749 | 122899.892 | -10549.5329 | 224064.048 | 188429.695 | 1900056.41 | -22767.4672 | 46186.7532 | -1420.269 | 56232.8527 | 20878.045 | 267545.161 | -6972.6058
549.72 | 11.5101 | 1.0341 |  | 61426.199 | -198312.432 | 362349.121 | 7192576.13 | 2964497.34 | -49545.8503 | 133973.444 | -20222.8495 | 222493.467 | 347524.445 | 2151455.71 | -39372.3918 | 56174.3469 | -5303.7299 | 56054.0233 | 40407.8367 | 308562.754 | -12231.8758
549.92 | 11.5616 | 1.0341 |  | 35385.1493 | -231955.654 | 382603.682 | 7753106.53 | 2339872.69 | -48541.414 | 129634.178 | -29923.8868 | 227413.924 | 454585.985 | 2124005.56 | -30180.4654 | 57843.0752 | -7467.8325 | 56297.5157 | 51158.6839 | 332200.854 | -8650.7313
550.12 | 11.5918 | 1.0341 |  | 2320.3633 | -241114.016 | 396532.949 | 8315150.43 | 1824787.35 | -37584.5473 | 138820.33 | -40514.7626 | 230177.136 | 578352.473 | 2264819.37 | -26255.3774 | 60707.4992 | -9570.075 | 56697.2341 | 59803.8389 | 348904.835 | -7781.8754
550.32 | 11.6033 | 1.0341 |  | -9707.1122 | -273812.1 | 427193.685 | 9103255.67 | 1509793.04 | -57938.6552 | 145274.325 | -50730.9484 | 238527.659 | 727451.992 | 2442492.28 | -34534.9358 | 65898.4326 | -12511.1681 | 59473.6507 | 72082.244 | 367758.773 | -9290.4235
550.52 | 11.629 | 1.0341 |  | -22852.503 | -291079.454 | 455786.137 | 9690056.52 | 1388079.54 | -55880.3393 | 158586.752 | -56856.4534 | 241806.606 | 792032.727 | 2520095.85 | -36555.432 | 64541.3234 | -13125.6295 | 58319.461 | 77409.1687 | 363955.268 | -10586.3525
550.72 | 11.6373 | 1.0341 |  | -32964.1086 | -303720.799 | 493540.812 | 9978342.78 | 1194811.7 | -55493.7819 | 160682.224 | -60952.4524 | 251466.971 | 817094.065 | 2607493.93 | -33333.6794 | 69810.8083 | -13366.1621 | 60963.037 | 75648.752 | 389387.889 | -9197.7214
550.92 | 11.659 | 1.0341 |  | -22561.4941 | -306324.939 | 529993.348 | 10156559.8 | 1431275.68 | -65533.3512 | 167195.277 | -59887.347 | 258413.503 | 847270.878 | 2692380.47 | -39715.8349 | 68790.5458 | -14311.5477 | 62008.0779 | 84543.5388 | 383766.715 | -10589.8308
551.12 | 11.692 | 1.0341 |  | -18761.5599 | -296873.07 | 569596.244 | 10005427.8 | 1561784.44 | -55053.7157 | 167282.959 | -57733.5336 | 267863.583 | 813053.088 | 2654362.77 | -33795.5394 | 68886.627 | -13870.1517 | 63354.5209 | 83108.905 | 388092.549 | -8709.4296
551.32 | 11.7327 | 1.0341 |  | 6444.4403 | -300749.025 | 615454.107 | 9888134.91 | 1868285.07 | -61459.7491 | 159522.842 | -53250.6831 | 280140.682 | 735108.767 | 2492249.91 | -33619.092 | 65229.7473 | -11786.287 | 65452.8882 | 75871.2014 | 382331.207 | -10363.7769
551.52 | 11.7881 | 1.0341 |  | 25153.9571 | -270589.456 | 651493.299 | 8995844.52 | 2178064.56 | -52873.0467 | 147653.571 | -41513.7441 | 288640.97 | 643512.352 | 2353549.78 | -29704.8111 | 62664.0257 | -11747.3022 | 66842.088 | 76438.3273 | 353767.513 | -6595.4147
551.72 | 11.8527 | 1.0341 |  | 48798.0657 | -230003.248 | 668393.587 | 7845294.13 | 2584393.44 | -47564.6123 | 132890.868 | -26949.4016 | 290568.179 | 461469.349 | 2272130.27 | -31704.2682 | 65403.4117 | -8140.3726 | 66448.6596 | 61465.1977 | 388538.824 | -9830.3462
551.92 | 11.8821 | 1.0341 |  | 87616.3104 | -192478.726 | 696518.063 | 6863275.72 | 3322612.71 | -38742.7061 | 130605.633 | -13142.0773 | 301296.808 | 288820.358 | 2137740.46 | -26683.8311 | 56974.7321 | -4292.4193 | 68917.3599 | 43661.683 | 334590.629 | -7225.3795
552.12 | 11.9101 | 1.0341 |  | 122697.584 | -181632.902 | 701143.584 | 6486910.65 | 3998908.5 | -48010.4165 | 128743.283 | -2151.1418 | 305459.598 | 122011.607 | 2009246.26 | -30045.4984 | 52546.7006 | -461.0441 | 70164.7939 | 23272.9611 | 306598.477 | -7995.0766
552.32 | 11.9145 | 1.0341 |  | 154777.579 | -157953.57 | 695041.112 | 5944738.88 | 4454932.39 | -50118.6164 | 122599.318 | 4910.3759 | 306631.376 | 55144.8947 | 1905663.84 | -30968.8953 | 49785.8633 | 484.2792 | 70794.914 | 18020.1023 | 294152.788 | -9464.3907
552.52 | 11.9252 | 1.0341 |  | 178838.411 | -144915.194 | 683422.724 | 5535220.48 | 4792591.87 | -46941.6228 | 116366.793 | 10903.9918 | 303813.473 | 19740.6705 | 1876255.57 | -24835.8346 | 50557.056 | 0.81204 | 70150.1908 | 21216.2613 | 296006.252 | -7121.1423
552.72 | 11.9496 | 1.0341 |  | 199971.95 | -121585.447 | 652300.238 | 5381113.72 | 5354079.66 | -37473.4978 | 126504.572 | 16257.2873 | 295742.379 | -51317.2494 | 1994526.02 | -26679.6524 | 51480.432 | 1724.3137 | 68697.0917 | 12523.0837 | 297273.959 | -8299.2818
552.92 | 11.9697 | 1.0341 |  | 235294.54 | -129399.292 | 627748.613 | 5720490.48 | 6185188.97 | -41384.7548 | 138240.764 | 22033.6295 | 291440.082 | -138868.416 | 2053499.78 | -28972.6806 | 50442.3405 | 3724.3315 | 68337.4947 | 1843.6078 | 277778.119 | -8128.2648
553.12 | 11.9938 | 1.0341 |  | 251631.844 | -127488.064 | 598973.066 | 5902060.18 | 6696872.58 | -35019.2484 | 147152.669 | 26281.8559 | 286281.606 | -189307.197 | 2173076.79 | -26722.3567 | 52697.5106 | 4677.7059 | 67515.5321 | -1870.1049 | 289213.199 | -8786.6842
553.32 | 12.0524 | 1.0341 |  | 258510.383 | -136953.7 | 567289.048 | 6252832 | 6886746.86 | -33177.9866 | 152352.85 | 25786.2784 | 282260.807 | -191452.353 | 2218761.77 | -27835.8478 | 54189.0531 | 4656.5926 | 67773.0675 | -2559.6428 | 297879.929 | -8596.0598
553.52 | 12.1007 | 1.0341 |  | 250444.335 | -131012.99 | 533688.307 | 6236863.39 | 6752104.11 | -34716.0956 | 153326.975 | 24449.9243 | 274092.525 | -159166.227 | 2269757.72 | -33748.8766 | 55635.9603 | 3685.2175 | 66016.7362 | 3410.9763 | 305535.239 | -11051.2974
553.72 | 12.1047 | 1.0615 |  | 225970.35 | -118785.015 | 500082.506 | 5708058.43 | 6156887.84 | -32294.9862 | 143102.029 | 20934.6369 | 267634.975 | -136608.761 | 2142695.37 | -31785.08 | 53315.9048 | 3722.1721 | 65236.6157 | 2811.2017 | 303561.608 | -9925.9296
553.92 | 12.117 | 1.1149 |  | 199160.738 | -97345.3924 | 473115.163 | 4982995.25 | 5372897.43 | -33248.1817 | 126945.746 | 15605.7317 | 260520.034 | -37685.9572 | 2059220.65 | -23777.0363 | 53781.665 | 1295.916 | 63400.8498 | 13424.6116 | 308818.513 | -8508.6307
554.12 | 12.1423 | 1.2123 |  | 158949.411 | -106328.337 | 443403.43 | 4904630.38 | 4675015.76 | -34640.0926 | 115179.694 | 13997.8563 | 253628.412 | -22931.5028 | 1957623.9 | -22441.6705 | 53684.7055 | 301.6543 | 61830.7414 | 20383.9126 | 313820.269 | -6229.7046
554.32 | 12.1476 | 1.315 |  | 128370.719 | -132742.668 | 430993.7 | 5441559.48 | 4130208.99 | -33455.2966 | 117391.226 | 5574.9736 | 253381.735 | 52597.1596 | 1982164.18 | -25991.8274 | 53218.9487 | -305.9213 | 62677.8485 | 20702.7942 | 307053.439 | -7304.7816
554.52 | 12.1417 | 1.3647 |  | 100932.663 | -166557.235 | 421016.429 | 6385555.03 | 3643802.68 | -43119.0321 | 129037.963 | -8031.4901 | 252717.596 | 192339.261 | 2042308.76 | -32652.1535 | 52057.6407 | -1876.7803 | 62810.9965 | 24939.664 | 297456.922 | -9525.869
554.72 | 12.1787 | 1.4071 |  | 72524.6114 | -215711.285 | 431693.951 | 7422240.48 | 3118974.22 | -50208.1252 | 134732.722 | -19618.7005 | 256281.573 | 311957.6 | 2024893.22 | -34941.0143 | 50924.1616 | -3869.6509 | 63513.1001 | 34430.0989 | 294182.453 | -9153.3325
554.92 | 12.2098 | 1.5291 |  | 31732.3038 | -235333.164 | 443173.06 | 7818111.08 | 2381949.56 | -50909.5261 | 132361.415 | -28067.4604 | 257639.177 | 422735.96 | 2091030.83 | -34505.5478 | 56949.8227 | -6616.3751 | 63219.5826 | 51905.3025 | 341794.797 | -11162.9956
555.12 | 12.225 | 1.6447 |  | -1663.2494 | -244516.832 | 467801.778 | 8259805.87 | 1653313.63 | -39558.9867 | 139488.629 | -43162.7625 | 264800.21 | 594579.086 | 2250120.46 | -27145.6631 | 57739.8015 | -8610.7521 | 65461.163 | 54774.5994 | 327554.704 | -8720.7866
555.32 | 12.2439 | 1.7443 |  | -7708.5195 | -286928.474 | 498551.887 | 9291545.96 | 1548914.89 | -63099.5756 | 147746.984 | -51069.0547 | 271965.743 | 724075.496 | 2337340.22 | -36275.9038 | 59671.7642 | -11813.9837 | 66634.101 | 68269.733 | 321329.595 | -9209.8467
555.52 | 12.2535 | 1.8452 |  | -27583.2504 | -306101.178 | 529469.84 | 9611478.43 | 1163147.25 | -62292.0201 | 146217.2 | -55167.0275 | 276111.161 | 754465.255 | 2389430.16 | -33314.1298 | 63820.4195 | -12011.8152 | 66564.7881 | 71864.6072 | 364176.425 | -9537.4256
555.72 | 12.2592 | 1.9121 |  | -30631.445 | -294057.828 | 559046.866 | 9787869.59 | 1235789.13 | -55504.6358 | 160450.075 | -59241.0833 | 281975.065 | 826909.226 | 2585054.87 | -34053.7354 | 68238.7658 | -14080.0971 | 68342.6844 | 79586.4631 | 369485.52 | -8607.9424
555.92 | 12.2759 | 1.992 |  | -12457.4797 | -323156.549 | 599249.78 | 10502963.6 | 1714759.15 | -75180.6409 | 167842.422 | -57195.7843 | 289924.454 | 797220.693 | 2686269.36 | -43870.5148 | 73057.701 | -13332.1557 | 69155.0071 | 78586.5609 | 400503.249 | -11631.5892
556.12 | 12.273 | 2.0968 |  | -11140.6038 | -303085.071 | 633299.174 | 10204411.2 | 1815159.61 | -68897.0438 | 173446.992 | -55031.5675 | 297486.31 | 785088.437 | 2795963.92 | -42346.7027 | 72369.2272 | -12666.0879 | 70905.2317 | 77887.2095 | 400673.947 | -11535.4203
556.32 | 12.3021 | 2.1859 |  | 6866.967 | -291883.206 | 666561.548 | 9881817.39 | 1949760.68 | -59203.8185 | 166368.762 | -53020.1458 | 304536.532 | 785564.015 | 2710526.89 | -35473.0691 | 71411.0234 | -13408.236 | 71022.1164 | 86379.8084 | 419196.421 | -10099.4956
556.52 | 12.3513 | 2.3332 |  | 33299.5219 | -288841.433 | 701115.123 | 9616405.95 | 2386953.6 | -68332.5847 | 160602.689 | -44723.1167 | 312806.495 | 689579.912 | 2600879.24 | -40079.1665 | 67579.8744 | -11646.895 | 72755.2336 | 79203.3337 | 391394.238 | -9901.0634
556.72 | 12.3552 | 2.4927 |  | 52244.618 | -251780.95 | 719432.669 | 8541673.57 | 2740181.18 | -58604.9232 | 148179.595 | -31173.1794 | 315443.052 | 494201.131 | 2414980.73 | -39043.2027 | 64482.5613 | -7311.5871 | 72259.8758 | 59096.575 | 383225.09 | -12466.8213
556.92 | 12.37 | 2.5823 |  | 89734.1384 | -204993.612 | 737115.115 | 7309339.63 | 3342879.57 | -37038.0617 | 141009.492 | -18457.8126 | 322849.356 | 352640.287 | 2211194.68 | -25111.5999 | 53855.1386 | -4616.7135 | 74126.7538 | 41404.7696 | 313728.852 | -5720.3742
557.12 | 12.3945 | 2.6709 |  | 119140.706 | -161843.34 | 743340.766 | 6075681.75 | 3799033.7 | -45293.1383 | 119745.603 | -2070.6519 | 324276.275 | 179928.584 | 2078379.28 | -28351.6595 | 59618.359 | -2905.6745 | 74539.4933 | 35925.4765 | 347748.032 | -6957.0588
557.32 | 12.3776 | 2.7244 |  | 149434.484 | -126774.208 | 730448.298 | 5305798.18 | 4364478.48 | -45524.7217 | 116472.612 | 8731.5079 | 322480.543 | 37761.8402 | 2028598.43 | -32461.8365 | 58213.1145 | 315.7234 | 74000.236 | 23509.4761 | 352848.07 | -9579.4997
557.52 | 12.3654 | 2.6913 |  | 187975.592 | -112099.17 | 711283.79 | 5025554.88 | 5071960.21 | -50286.9492 | 119100.748 | 16567.4316 | 320103.835 | -31968.2652 | 1966527.54 | -34230.7181 | 54676.7257 | 880.076 | 74046.4259 | 20005.8803 | 321088.644 | -8926.7576
557.72 | 12.3546 | 2.6455 |  | 208685.037 | -103179.05 | 681865.483 | 4802968.48 | 5480488.58 | -47342.1473 | 114612.652 | 23571.0383 | 312479.593 | -118508.414 | 1922533.17 | -28740.5696 | 54262.7012 | 2384.7699 | 72234.3831 | 10556.0036 | 313026.496 | -9193.1899
557.92 | 12.3603 | 2.6013 |  | 235337.508 | -108133.301 | 640213.786 | 5171004.53 | 6134201.24 | -43260.257 | 130089.471 | 26677.1749 | 305896.653 | -175031.947 | 1953989.8 | -29562.5417 | 48342.5284 | 3888.0332 | 72473.416 | 349.3289 | 256011.216 | -6804.3971
558.12 | 12.3963 | 2.5741 |  | 256570.698 | -117129.574 | 607690.198 | 5453163.08 | 6692161.28 | -45448.1091 | 137936.618 | 30846.0123 | 298099.154 | -245365.383 | 1961641.26 | -37645.3194 | 46331.6664 | 5801.2681 | 70224.1417 | -5235.763 | 264442.585 | -10596.5471
558.32 | 12.3669 | 2.5662 |  | 236417.599 | -104999.826 | 569637.843 | 4986464.53 | 6260047.06 | -47266.9122 | 124232.561 | 31642.9642 | 291038.766 | -265303.175 | 1981826.68 | -32201.0556 | 54973.303 | 5862.8307 | 70007.5612 | -9329.0312 | 300758.901 | -10756.0156
558.52 | 12.3577 | 2.4866 |  | 215710.87 | -85406.7386 | 527885.753 | 4758075.53 | 5762339.71 | -39100.0068 | 124697.802 | 24513.9925 | 282158.87 | -140774.926 | 1982209.27 | -31894.2084 | 50494.8973 | 3171.2989 | 68583.2273 | 5331.3041 | 285714.619 | -10012.4075
558.72 | 12.3534 | 2.4187 |  | 196658.25 | -105984.876 | 502004.244 | 4959544.01 | 5239692.38 | -44932.4765 | 115822.255 | 18311.157 | 274929.502 | -74342.3877 | 1867384.01 | -33075.2932 | 51299.7915 | 1503.1611 | 66637.0125 | 14296.8266 | 299934.52 | -8929.5133
558.92 | 12.3183 | 2.3456 |  | 162784.82 | -105711.589 | 466566.199 | 4911854.97 | 4629227.07 | -44055.0812 | 111998.773 | 13211.4146 | 264783.739 | -19015.2745 | 1842427.64 | -30691.2632 | 52346.9879 | 228.2816 | 64445.8317 | 22152.0981 | 318534.167 | -9163.4828
559.12 | 12.2979 | 2.2139 |  | 142764.781 | -132082.104 | 448565.033 | 5409358.93 | 4190171.27 | -45154.0753 | 112301.763 | 4447.7309 | 260503.856 | 70079.1439 | 1855226.49 | -28546.7745 | 53967.1083 | -1024.1009 | 63653.9489 | 27713.1102 | 338482.731 | -8911.9336
559.32 | 12.292 | 2.0895 |  | 112381.327 | -148959.437 | 434099.525 | 6092347.86 | 3861136.01 | -41389.2864 | 132441.813 | -4668.3477 | 256825.611 | 154805.855 | 2024047.43 | -32092.47 | 48438.9626 | -1112.937 | 62992.0832 | 23377.4323 | 275245.465 | -9485.2434
559.52 | 12.2778 | 1.9689 |  | 93310.1227 | -203508.376 | 434370.183 | 7512448.37 | 3658871.71 | -39708.9645 | 150552.114 | -17652.6459 | 260669.331 | 267168.819 | 2131707 | -30338.6872 | 48611.5476 | -2131.0517 | 65076.0146 | 22730.8943 | 251736.311 | -9282.4701
559.72 | 12.3033 | 1.8495 |  | 74914.9767 | -255071.689 | 444550.949 | 8698809.28 | 3311833.5 | -68016.6164 | 157806.189 | -28864.7911 | 263353.349 | 400730.489 | 2178699.58 | -45518.6434 | 51091.6772 | -4691.8643 | 65439.9317 | 37412.3098 | 288564.324 | -13647.3464
559.92 | 12.2957 | 1.7417 |  | 10267.7771 | -233959.176 | 456558.138 | 8255965.45 | 1954426.22 | -46184.8665 | 142686.764 | -39595.5188 | 262640.29 | 554750.269 | 2295913.82 | -32679.6312 | 60386.4251 | -8178.4398 | 64983.3388 | 52836.1521 | 331857.514 | -11914.8208
560.12 | 12.2682 | 1.5931 |  | -15458.1114 | -267688.621 | 487141.575 | 8828911.27 | 1252174.79 | -54191.7388 | 137000.187 | -50791.0146 | 270998.941 | 704814.361 | 2201926.95 | -33240.3783 | 59759.6462 | -11838.121 | 66431.0698 | 74816.3452 | 356799.284 | -8845.3138
560.32 | 12.2657 | 1.4265 |  | -31862.2615 | -273856.245 | 515943.635 | 9047980.97 | 912084.196 | -61191.6146 | 141545.581 | -57690.0157 | 272629.903 | 817382.405 | 2283007.92 | -37861.3885 | 61612.5581 | -14117.7356 | 65354.9868 | 86921.3232 | 367652.748 | -10893.493
560.52 | 12.237 | 1.2272 |  | -54877.1292 | -263775.093 | 548094.141 | 8977330.76 | 586811.473 | -46704.2387 | 145684.832 | -61302.0575 | 276427.751 | 827450.972 | 2504752.97 | -29017.515 | 69385.9477 | -13027.8094 | 66316.6413 | 71061.171 | 377197.232 | -10299.5965
560.72 | 12.2291 | 1.109 |  | -19932.8293 | -303301.06 | 591618.1 | 9928753.42 | 1486496.51 | -67916.1791 | 162908.987 | -56615.0283 | 287779.176 | 793252.488 | 2536883.7 | -40171.9703 | 65049.8547 | -13001.3713 | 68488.1231 | 78528.6466 | 364055.706 | -10265.6181
560.92 | 12.2148 | 1.1008 |  | -21601.5518 | -290281.079 | 624655.903 | 9755796.57 | 1581981.37 | -65914.8204 | 166044.358 | -53888.6531 | 293120.468 | 741419.141 | 2689777.81 | -39281.5777 | 69925.8454 | -11087.7563 | 69351.702 | 67359.9082 | 386974.339 | -11449.3475
561.12 | 12.211 | 1.1111 |  | 3207.0513 | -288153.113 | 663610.768 | 9692663.77 | 1869541 | -65283.9657 | 162639.538 | -51658.8454 | 303934.174 | 758197.277 | 2666473.24 | -38511.8602 | 70347.5949 | -12609.528 | 71880.2759 | 81189.2922 | 409558.406 | -11033.5369
561.32 | 12.252 | 1.1206 |  | 30159.7598 | -284511.225 | 692368.207 | 9727421.21 | 2371881.27 | -59256.8642 | 169084.808 | -47954.9592 | 309131.069 | 724907.424 | 2640225.61 | -34738.2126 | 66234.1356 | -12240.1412 | 71875.3692 | 77919.5927 | 362608.41 | -8208.3235
561.52 | 12.2293 | 1.1285 |  | 49012.7896 | -261497.341 | 704168.069 | 9150419.91 | 2742068.33 | -63836.9928 | 160525.256 | -37936.1797 | 310067.807 | 588444.168 | 2618735.86 | -42904.9594 | 72446.9165 | -9847.0836 | 72262.7541 | 67492.28 | 411342.383 | -12441.5999
561.72 | 12.2019 | 1.1387 |  | 82269.3052 | -221440.847 | 718695.526 | 8038208.26 | 3212975.61 | -44337.5993 | 147644.088 | -25889.3587 | 312776.782 | 487964.725 | 2453709.49 | -30924.336 | 68162.8754 | -9300.5597 | 71730.3791 | 71435.8222 | 402262.166 | -8767.1238
561.92 | 12.2138 | 1.1484 |  | 106402.393 | -184759.002 | 721015.751 | 7092233.62 | 3662737.99 | -47449.8109 | 139732.213 | -13680.9509 | 312340.08 | 319901.273 | 2325588.96 | -34515.8632 | 63779.03 | -5228.6803 | 71415.4151 | 48982.5395 | 373585.252 | -10365.572
562.12 | 12.1709 | 1.1568 |  | 136800.864 | -163256.459 | 718773.435 | 6356031.18 | 4223975.09 | -41389.269 | 131786.13 | -923.4556 | 314680.942 | 145503.292 | 2120934.02 | -24804.5258 | 55392.8308 | -1666.4131 | 72394.0548 | 30125.345 | 318830.836 | -5670.572
562.32 | 12.1635 | 1.1665 |  | 178666.31 | -156350.655 | 704015.829 | 6297152.39 | 5034607.98 | -47709.273 | 137037.153 | 6590.9217 | 312662.769 | 45104.7041 | 2061536.93 | -32687.2809 | 50956.3708 | 687.3937 | 72172.8278 | 18635.2352 | 302303.019 | -8740.6207
562.52 | 12.1539 | 1.1667 |  | 204882.606 | -139616.638 | 680458.455 | 5991020.46 | 5609641.11 | -42057.6117 | 139319.472 | 14766.136 | 308524.922 | -47256.4062 | 2071197.67 | -29716.8332 | 49831.7529 | 2232.519 | 71933.6194 | 8021.5679 | 267707.213 | -7155.661
562.72 | 12.1255 | 1.1611 |  | 216073.261 | -105779.923 | 648564.746 | 5426626.12 | 5793820.43 | -34114.4355 | 135149.947 | 19052.2954 | 300157.481 | -44316.3628 | 2237860.48 | -30114.0649 | 59207.1694 | 741.8259 | 70755.9622 | 15204.1707 | 321966.668 | -9045.2133
562.92 | 12.1293 | 1.1558 |  | 236948.833 | -108799.128 | 608137.374 | 5437454.9 | 6186253.79 | -49562.103 | 134239.687 | 23434.5822 | 289817.032 | -88939.4134 | 2185076.84 | -38394.2829 | 59444.7145 | 1058.5622 | 68258.7159 | 20576.9352 | 345009.242 | -11139.2975
563.12 | 12.0984 | 1.15 |  | 227610.136 | -84040.3744 | 559865.718 | 4770594.94 | 6013316.52 | -42391.04 | 126726.154 | 27079.8124 | 277953.133 | -164686.915 | 2060984.31 | -33872.1021 | 55563.9759 | 3158.8303 | 65676.3427 | 9088.3329 | 324785.568 | -10020.0419
563.32 | 12.0496 | 1.1455 |  | 212628.196 | -73048.2256 | 522968.424 | 4244400.57 | 5530175.69 | -32342.4922 | 113850.295 | 24970.2336 | 271297.857 | -153676.465 | 1891245.55 | -22154.9434 | 51640.3313 | 3020.7225 | 65342.1778 | 7062.3218 | 306744.693 | -6234.8499
563.52 | 12.0384 | 1.1417 |  | 206396.492 | -93656.9756 | 484831.755 | 4779320.02 | 5472703.2 | -34812.9623 | 124136.434 | 19482.3966 | 262471.673 | -102218.722 | 1867672.43 | -26599.4873 | 45571.1978 | 2552.7153 | 63242.8975 | 7940.5009 | 264929.559 | -7295.9336
563.72 | 11.9856 | 1.1373 |  | 186719.45 | -128296.458 | 451636.95 | 5638618.25 | 5213849.21 | -42507.6659 | 131202.54 | 11896.385 | 255546.34 | -68127.7883 | 1936312.1 | -28587.5655 | 47017.9578 | 3399.5109 | 62671.4317 | 1149.9309 | 267915.155 | -9466.5035
563.92 | 11.9398 | 1.1339 |  | 161250.851 | -164108.758 | 420648.866 | 6641634.06 | 4825076.56 | -40175.1244 | 143863.946 | -110.6228 | 248833.474 | 73787.314 | 2041233.76 | -30945.1738 | 47898.3907 | 447.5466 | 61664.0908 | 15739.29 | 274853.971 | -9249.7893
564.12 | 11.9189 | 1.1304 |  | 124849.206 | -181932.731 | 402446.973 | 7113715.39 | 4068569.58 | -38295.9732 | 144850.399 | -12315.9754 | 242435.177 | 245954.707 | 2165260.56 | -31126.8217 | 52821.2834 | -3104.2556 | 60605.2709 | 29849.9888 | 289130.551 | -9715.7083
564.32 | 11.8717 | 1.1261 |  | 83676.3102 | -201261.857 | 389830.603 | 7578009.19 | 3267589.43 | -34631.3949 | 144038.137 | -24299.77 | 237046.425 | 371582.043 | 2204901.96 | -27255.2356 | 55568.6283 | -4979.3617 | 58968.6443 | 38270.5614 | 317360.397 | -8844.79
564.52 | 11.8322 | 1.1227 |  | 59117.3575 | -221265.456 | 389306.59 | 8114059.21 | 2761314.82 | -40847.9219 | 150253.916 | -34874.0339 | 235282.535 | 514821.904 | 2258953.93 | -30630.2435 | 54190.393 | -7702.8171 | 58895.1964 | 50290.15 | 301575.362 | -9337.2779
564.72 | 11.8113 | 1.119 |  | 32904.3631 | -254636.35 | 399052.573 | 8683558.22 | 2344544.62 | -41816.0259 | 149651.698 | -40065.92 | 235848.848 | 539962.088 | 2228705.99 | -28569.1213 | 54837.1485 | -7818.7598 | 58052.3043 | 52542.6542 | 311748.063 | -8610.5776
564.92 | 11.733 | 1.1149 |  | -5213.7178 | -254926.579 | 412419.713 | 8573946.91 | 1536147.53 | -46067.1463 | 141701.729 | -46918.6099 | 238631.326 | 621952.441 | 2253729.17 | -29933.2865 | 59495.8436 | -9359.5051 | 59223.0069 | 60261.327 | 346618.186 | -10029.895
565.12 | 11.6913 | 1.1128 |  | -18701.5604 | -277618.221 | 435281.06 | 8989806.67 | 1114908.2 | -48319.9657 | 140303.333 | -55345.9211 | 242347.183 | 747541.586 | 2164949.59 | -27223.8288 | 55911.9799 | -12455.4944 | 58757.247 | 79138.2856 | 346566.021 | -8451.9091
565.32 | 11.6527 | 1.1105 |  | -35902.7107 | -307494.74 | 458533.71 | 9790397.76 | 896734.633 | -53988.4341 | 149464.238 | -62307.9759 | 246596.639 | 784994.422 | 2232307.91 | -29999.6318 | 55550.1822 | -11707.0974 | 59535.0204 | 69018.6094 | 322052.571 | -8673.4451
565.52 | 11.5701 | 1.1084 |  | -46412.1085 | -302262.916 | 483226.213 | 9816010.21 | 771809.086 | -59343.1434 | 154606.162 | -64421.8249 | 249467.084 | 831499.356 | 2353070.48 | -36609.024 | 58462.7657 | -12603.5933 | 60492.5235 | 72579.2135 | 326523.334 | -11404.9396
565.72 | 11.5311 | 1.1078 |  | -45035.2032 | -297091.682 | 519459.465 | 9749611.18 | 753706.636 | -46615.6218 | 155469.809 | -66470.0423 | 255430.917 | 860514.571 | 2358627.83 | -24357.021 | 58680.5214 | -13358.0808 | 60887.8495 | 76395.1994 | 331822.763 | -7584.1102
565.92 | 11.5105 | 1.1063 |  | -30919.9667 | -317337.366 | 556428.094 | 10086743 | 1089091.15 | -61318.3662 | 155295.597 | -61638.4656 | 263436.838 | 801740.047 | 2351667.69 | -31124.403 | 61069.5832 | -12999.6738 | 62326.0681 | 78638.8374 | 352321.361 | -8079.705
566.12 | 11.4543 | 1.1045 |  | -21986.0443 | -286277.081 | 582232.57 | 9598607.45 | 1236357.05 | -48418.4174 | 154349.663 | -58222.3899 | 266801.618 | 827730.622 | 2528995.73 | -29024.9932 | 68685.9514 | -15073.176 | 62955.4446 | 87859.1985 | 386755.359 | -7654.5895
566.32 | 11.4446 | 1.1037 |  | 4507.7408 | -279840.061 | 606334.527 | 9623516.18 | 1774390.15 | -56300.4238 | 160011.722 | -53593.6743 | 269358.057 | 805677.205 | 2627085.7 | -36170.4356 | 70783.592 | -14991.0452 | 62855.7386 | 92892.5813 | 408038.068 | -9650.2836
566.52 | 11.4172 | 1.102 |  | 38818.8622 | -269031.416 | 628398.33 | 9338603.49 | 2473840.57 | -54329.6798 | 160606.522 | -43512.4076 | 273406.024 | 654389.788 | 2524713.59 | -36270.0389 | 66106.4541 | -11343.9598 | 63318.7559 | 74611.1216 | 375317.62 | -9880.5921
566.72 | 11.3613 | 1.1008 |  | 71342.1821 | -235620.089 | 637879.757 | 8443143.99 | 2969731.18 | -42261.9337 | 153220.745 | -33144.7306 | 275563.437 | 519802.468 | 2384692.84 | -29179.495 | 62220.1871 | -8767.6895 | 63514.2749 | 61866.2296 | 356747.366 | -8202.3166
566.92 | 11.3373 | 1.1005 |  | 97365.6579 | -201625.565 | 644787.518 | 7340896.9 | 3359020.69 | -39195.4809 | 138659.674 | -19904.5996 | 276518.448 | 363023.74 | 2174252.98 | -26775.1826 | 56058.1273 | -5711.5038 | 63328.2771 | 47880.5883 | 325609.696 | -7785.1683
567.12 | 11.2855 | 1.1 |  | 123157.437 | -160620.881 | 636530.865 | 6246112.71 | 3826698 | -32438.9507 | 131148.428 | -6877.5791 | 275042.241 | 212678.095 | 2008750.73 | -21557.4289 | 50589.0553 | -3468.4436 | 63115.8147 | 37927.5137 | 293743.271 | -3866.265
567.32 | 11.2119 | 1.1008 |  | 147231.543 | -137419.079 | 621406.753 | 5800331.69 | 4213201.58 | -31960.8972 | 128058.228 | -1542.9155 | 271168.965 | 112600.586 | 1972051.99 | -21976.4596 | 50479.2516 | -548.4572 | 62370.2188 | 22175.6228 | 300214.968 | -6733.9692
567.52 | 11.164 | 1.1024 |  | 193615.966 | -163893.764 | 601263.646 | 6324311.48 | 5130537.08 | -43379.7475 | 133578.939 | 5579.2279 | 268150.771 | 24439.8271 | 1840878.55 | -26183.7207 | 43908.9968 | 808.1766 | 62039.5155 | 17106.7823 | 260935.665 | -7087.2338
567.72 | 11.1358 | 1.1034 |  | 204680.016 | -131612.928 | 570464.011 | 5866834.11 | 5430675.68 | -29272.6256 | 137926.97 | 9910.1556 | 259155.65 | -7124.0819 | 2016496.03 | -21883.3363 | 48865.7397 | 1202.5097 | 60689.7231 | 9670.7403 | 259355.395 | -6375.6408
567.92 | 11.0916 | 1.1037 |  | 212598.019 | -102979.422 | 537713.459 | 5457159.22 | 5659905.39 | -24180.7717 | 139369.033 | 13764.216 | 250156.609 | -6053.9895 | 2207736.58 | -25653.1791 | 56309.9584 | 368.7992 | 59490.0255 | 14692.0949 | 305515.521 | -7849.0384
568.12 | 11.0858 | 1.1042 |  | 222598.669 | -84727.5245 | 502671.166 | 4998895.01 | 5869913.7 | -38420.195 | 130449.803 | 21021.8543 | 238555.496 | -38509.3553 | 2214412.72 | -33123.2168 | 61150.5445 | -914.0219 | 56408.1479 | 26907.4149 | 344332.394 | -10730.5098
568.32 | 11.0639 | 1.104 |  | 219231.122 | -72382.1786 | 471225.978 | 4369923.22 | 5741476.37 | -35473.2107 | 116639.724 | 26790.2109 | 232715.298 | -143147.859 | 1977047.49 | -25524.1601 | 56014.2452 | 1106.2407 | 55367.0779 | 19069.7319 | 325263.183 | -7034.5133
568.52 | 11.0447 | 1.1041 |  | 205573.735 | -50650.0697 | 436240.143 | 3566321.39 | 5297667.17 | -29324.9905 | 101867.659 | 27763.5111 | 225921.522 | -164772.461 | 1734248.31 | -17243.6945 | 50097.6185 | 1322.764 | 54098.6284 | 18075.9032 | 301718.11 | -3180.4594
568.72 | 11.0305 | 1.1045 |  | 191066.745 | -65998.8444 | 404542.958 | 3717847.79 | 4973850.83 | -33112.9772 | 95377.5959 | 24970.3996 | 218970.172 | -176009.291 | 1609559.19 | -18074.0418 | 46536.527 | 2821.4552 | 52439.5421 | 9559.1945 | 294833.745 | -4709.5207
568.92 | 10.9742 | 1.1049 |  | 181616.546 | -97923.6904 | 374791.233 | 4369108.2 | 4795733.91 | -44956.6694 | 99832.1456 | 19158.9289 | 213564.746 | -123166.979 | 1589047.18 | -26486.1953 | 43089.8893 | 2555.1105 | 52230.2022 | 6729.3196 | 260671.775 | -7401.5
569.12 | 10.926 | 1.1068 |  | 146144.86 | -109642.61 | 342227.26 | 4612508.74 | 4101982.07 | -43822.8561 | 99123.2443 | 10191.1712 | 204828.095 | -32083.9367 | 1571352.25 | -30260.9174 | 40523.5997 | 1629.6957 | 50436.3054 | 9465.1658 | 248270.092 | -9390.599
569.32 | 10.9098 | 1.1088 |  | 113359.949 | -110270.496 | 320547.229 | 4584955.57 | 3365392.76 | -25176.7142 | 94009.0396 | 1214.6303 | 198646.213 | 98166.7812 | 1575472.72 | -16823.1184 | 43953.7605 | -1974.6955 | 49406.3299 | 25267.3097 | 260881.727 | -5021.0486
569.52 | 10.8643 | 1.11 |  | 85047.0118 | -151416.015 | 311008.96 | 5737495.45 | 3049199.83 | -29607.7127 | 116431.192 | -11118.5898 | 195922.803 | 177992.433 | 1727636.73 | -22029.1546 | 38502.8449 | -768.5447 | 48457.2114 | 16349.8227 | 221417.287 | -6538.0042
569.72 | 10.837 | 1.1122 |  | 81259.5569 | -219287.561 | 309587.649 | 7485624.51 | 3116944.69 | -36906.8268 | 137971.95 | -23825.9124 | 198533.52 | 319220.274 | 1857735.38 | -23358.9878 | 37895.9681 | -3200.625 | 50199.9642 | 26147.3994 | 200564.163 | -6988.5719
569.92 | 10.8842 | 1.1138 |  | 46579.7334 | -241386.645 | 312639.207 | 8337688.13 | 2578455.82 | -34444.5591 | 147206.43 | -36051.464 | 196510.864 | 464278.845 | 2121561.35 | -25340.3166 | 48842.9968 | -5831.0397 | 49284.7058 | 36392.6766 | 261211.999 | -9360.819
570.12 | 10.8733 | 1.1129 |  | 13871.2601 | -270168.052 | 327545.836 | 9031356.2 | 2007974.86 | -39124.1758 | 153146.719 | -46226.0934 | 200396.779 | 562794.29 | 2207586.61 | -27787.8084 | 52053.3283 | -7252.2884 | 50403.3583 | 45041.6294 | 292735.239 | -9545.5225
570.32 | 10.8526 | 1.1133 |  | -7329.5618 | -284133.813 | 345288.631 | 9324115.65 | 1420919.93 | -45076.33 | 151741.947 | -56912.3337 | 203746.519 | 730937.079 | 2229060.29 | -25460.9655 | 52608.0172 | -10959.4841 | 50967.2852 | 61548.2134 | 289053.658 | -8466.7427
570.52 | 10.8873 | 1.1143 |  | -27118.4179 | -289011.537 | 369446.669 | 9227484.31 | 971233.215 | -44744.5994 | 140268.788 | -57949.1326 | 205361.365 | 777765.028 | 2180992.47 | -25911.073 | 56839.0612 | -13395.9431 | 50131.1256 | 80017.5778 | 334359.353 | -8585.6158
570.72 | 10.8491 | 1.1141 |  | -46513.5498 | -285121.308 | 396929.603 | 9012514.63 | 661263.852 | -43033.3801 | 137399.071 | -57457.2866 | 210755.011 | 733060.16 | 2200316.42 | -26750.4196 | 56366.9296 | -10993.2789 | 51058.2788 | 63713.1748 | 317302.247 | -8492.9454
570.92 | 10.7975 | 1.1163 |  | -37159.6061 | -295683.902 | 430933.003 | 9042670.6 | 780130.122 | -51992.5171 | 132188.475 | -55262.9813 | 219949.309 | 743023.219 | 2073479.8 | -27382.3724 | 54573.9806 | -12684.8837 | 52917.3409 | 77365.5914 | 322239.756 | -8123.7601
571.12 | 10.8023 | 1.1193 |  | -50026.8575 | -276133 | 462787.042 | 8641639.2 | 495955.636 | -43689.1121 | 127897.4 | -55857.1016 | 225583.072 | 767681.119 | 2151560.99 | -24451.7866 | 59551.9077 | -13646.7835 | 53800.5189 | 76906.6754 | 330393.94 | -6351.501
571.32 | 10.7894 | 1.1205 |  | -50773.1929 | -264900.027 | 489945.709 | 8575602.1 | 577855.037 | -44311.3011 | 129009.206 | -53980.3117 | 230712.214 | 782821.911 | 2312456.79 | -27241.2818 | 66396.3685 | -14740.5398 | 54808.4509 | 85645.2013 | 376023.633 | -7897.5881
571.52 | 10.7674 | 1.1218 |  | -32208.7251 | -271391.746 | 522062.959 | 8847330.48 | 896747.744 | -51908.3429 | 133343.542 | -53421.7465 | 238523.029 | 782585.946 | 2322291.9 | -31616.3353 | 64695.8914 | -14524.843 | 56387.0987 | 85473.9099 | 361429.038 | -8398.0327
571.72 | 10.8043 | 1.1236 |  | -8340.9666 | -253818.082 | 550495.159 | 8586706.18 | 1318753.97 | -43032.5082 | 138764.881 | -50398.3582 | 242803.265 | 776670.22 | 2320798.56 | -25928.5815 | 63406.5639 | -15382.1367 | 56329.9471 | 92760.3779 | 361994.432 | -6102.962
571.92 | 10.8247 | 1.1237 |  | 17827.9637 | -247432.275 | 574134.808 | 8522460.98 | 1980577.15 | -35872.2345 | 146339.078 | -42106.1766 | 247941.989 | 600014.516 | 2344456.18 | -26185.6042 | 61475.4032 | -9753.937 | 56961.689 | 62550.068 | 345273.271 | -7092.205
572.12 | 10.8131 | 1.1238 |  | 58641.2061 | -228280.275 | 590151.079 | 8137674.31 | 2891319.68 | -39710.319 | 151555.02 | -29631.8168 | 252733.754 | 482199.791 | 2346673.58 | -28709.8967 | 58401.2595 | -8115.6576 | 58352.471 | 56623.6216 | 321594.931 | -8337.2249
572.32 | 10.8235 | 1.1249 |  | 86128.4632 | -207603.838 | 601203.079 | 7563272.04 | 3292844.79 | -38693.8356 | 146739.911 | -22481.416 | 257184.014 | 358020.39 | 2229550.2 | -29910.3418 | 53842.3853 | -4356.2967 | 59380.6995 | 36503.4253 | 300038.493 | -8861.2995
572.52 | 10.8032 | 1.1261 |  | 110918.986 | -167415.343 | 601387.264 | 6501770.77 | 3622192.38 | -28340.6712 | 132450.934 | -11378.4044 | 257176.409 | 274863.647 | 2042092.17 | -19633.9344 | 53031.0673 | -5459.0293 | 59070.6139 | 46979.006 | 303895.925 | -5470.2748
572.72 | 10.7734 | 1.1283 |  | 133980.125 | -149847.434 | 587993.927 | 6161740.1 | 3895649.25 | -28216.583 | 133770.763 | -9449.9347 | 254818.005 | 179621.243 | 1920224.37 | -22550.7821 | 45409.0231 | -1142.1346 | 58790.1074 | 21081.1673 | 257374.784 | -6225.5867
572.92 | 10.7475 | 1.1309 |  | 169225.785 | -136744.711 | 571460.647 | 5679869.1 | 4545840.13 | -32560.1141 | 125371.376 | 2604.0493 | 249138.194 | 93620.1771 | 1836756.04 | -18588.4588 | 45536.0237 | -1727.4741 | 57160.3303 | 28140.9264 | 265162.644 | -4920.397
573.12 | 10.716 | 1.1335 |  | 186280.155 | -118513.653 | 543171.478 | 5312227.57 | 5003449.02 | -25429.8358 | 126593.804 | 10706.2634 | 241801.74 | -28910.7251 | 1911006.91 | -18977.1511 | 47284.7821 | 1720.3463 | 56074.073 | 9153.4073 | 265287.336 | -6317.4035
573.32 | 10.7079 | 1.136 |  | 217138.212 | -112148.238 | 517128.228 | 5272568.62 | 5706675.38 | -30798.2266 | 132392.876 | 17704.7196 | 237030.469 | -104900.125 | 1919456.53 | -23242.1705 | 45382.8067 | 2894.5171 | 55555.6112 | 3459.6348 | 251402.307 | -6825.5849
573.52 | 10.6925 | 1.1375 |  | 220061.328 | -87868.1293 | 489464.224 | 4735233.77 | 5793330.88 | -27630.3134 | 126689.587 | 23480.0158 | 230446.422 | -141438.769 | 1991026.05 | -21908.7912 | 49635.9506 | 3109.5421 | 54457.6256 | 1699.9855 | 272997.439 | -6434.3709
573.72 | 10.696 | 1.1389 |  | 220788.389 | -74591.3146 | 458782.007 | 4546013.18 | 5781970.58 | -23235.9108 | 124017.184 | 23421.5489 | 223976.025 | -111203.394 | 2031257.99 | -17343.4124 | 54359.3339 | 1274.9353 | 53678.4981 | 11283.5501 | 298499.601 | -5870.3556
573.92 | 10.7032 | 1.1393 |  | 222472.287 | -92193.7611 | 424235.927 | 5070531.26 | 5861535.49 | -28248.3815 | 132443.41 | 20136.2856 | 216580.643 | -97520.7562 | 2005383.52 | -22549.8386 | 48181.2086 | 1859.4776 | 52060.5969 | 12232.8919 | 274077.725 | -6017.906
574.12 | 10.7198 | 1.139 |  | 218762.083 | -98372.1624 | 396545.316 | 4951658.45 | 5694435.83 | -36747.7457 | 122571.619 | 20727.7009 | 208920.738 | -104764.903 | 1914287.37 | -26521.6889 | 50314.2879 | 1404.2605 | 50548.1551 | 13557.4671 | 290889.474 | -7750.795
574.32 | 10.6988 | 1.1387 |  | 192002.131 | -75357.4764 | 358737.189 | 4346925.62 | 5235182.91 | -26182.9828 | 115524.27 | 21383.4687 | 198580.475 | -118150.041 | 1919165.99 | -20922.0896 | 52252.5826 | 1514.7325 | 48334.2967 | 11756.7281 | 299248.36 | -6317.9486
574.52 | 10.6794 | 1.1394 |  | 175228.383 | -86138.2217 | 335042.533 | 4432432.32 | 4879860.14 | -31807.4816 | 109096.342 | 17872.9399 | 195119.272 | -70949.4262 | 1884472.32 | -23940.8752 | 53524.8726 | 530.9362 | 48114.6491 | 17407.4922 | 322144.805 | -6668.9624
574.72 | 10.6839 | 1.1405 |  | 149176.224 | -95723.5289 | 313314.845 | 4455894.46 | 4248521.45 | -38976.9002 | 99658.8082 | 11867.428 | 189877.068 | 9420.4933 | 1863373.04 | -25912.6556 | 54362.2634 | -1015.092 | 47364.8005 | 22562.8293 | 309482.23 | -7662.9556
574.92 | 10.6513 | 1.141 |  | 111036.996 | -109686.322 | 296876.684 | 4702001.14 | 3525356.27 | -34876.5441 | 101202.674 | 2660.1409 | 185848.353 | 93178.7076 | 1810446.95 | -22696.9072 | 50350.6631 | -1716.942 | 46126.8225 | 24872.0857 | 296221.822 | -6527.136
575.12 | 10.6254 | 1.1425 |  | 92648.487 | -161288.211 | 289488.808 | 5956532.55 | 3166829.23 | -38217.2924 | 114236.102 | -11334.477 | 186942.075 | 214904.429 | 1763273.44 | -25157.0978 | 43793.5465 | -2758.6236 | 47332.8181 | 24873.3358 | 247164.904 | -6283.9432
575.32 | 10.6217 | 1.1438 |  | 62187.9613 | -189212.027 | 288240.186 | 6632848.37 | 2593653.56 | -36339.825 | 116812.818 | -21639.8755 | 184871.557 | 354674.499 | 1873462.34 | -22851.1041 | 49485.669 | -5976.344 | 46547.3381 | 38695.3991 | 264768.204 | -7329.013
575.52 | 10.6132 | 1.1447 |  | 26403.4083 | -208994.156 | 292524.293 | 7195140.05 | 1991301.49 | -34722.4699 | 121146.747 | -31744.2484 | 184654.935 | 461657.711 | 2009064.95 | -22730.5495 | 53303.1374 | -7271.9513 | 46632.4446 | 44034.0299 | 295005.17 | -7419.4022
575.72 | 10.5953 | 1.1455 |  | 2792.2387 | -226399.137 | 309359.926 | 7663898.03 | 1559520.33 | -41415.4488 | 125180.466 | -39455.4302 | 188004.114 | 564568.423 | 2046335.7 | -29082.5985 | 53695.8555 | -9433.3357 | 46986.697 | 57919.8505 | 302295.416 | -9104.9804
575.92 | 10.588 | 1.1461 |  | -25661.4726 | -234865.905 | 326255.451 | 7888483.63 | 975783.389 | -34390.8887 | 126957.369 | -48186.9288 | 191194.887 | 639753.905 | 2039041.76 | -24792.4136 | 53361.3707 | -10305.7302 | 47453.8913 | 62077.3344 | 302161.965 | -8042.6196
576.12 | 10.5724 | 1.1463 |  | -40020.9162 | -254135.499 | 358238.363 | 8113839.8 | 642653.962 | -37158.0928 | 123025.748 | -52282.1373 | 198167.442 | 693906.062 | 2000481.74 | -22936.318 | 54087.0166 | -11528.0642 | 48278.8994 | 69948.0792 | 323835.062 | -7219.9954
576.32 | 10.5363 | 1.147 |  | -58812.8983 | -246418.235 | 378503.969 | 8089318.1 | 305988.651 | -37247.1795 | 123991.542 | -55891.9158 | 201245.683 | 756566.079 | 2103651.8 | -25598.2867 | 57537.6536 | -12964.0274 | 49027.2685 | 73857.7009 | 326252.34 | -8172.2163
576.52 | 10.534 | 1.1484 |  | -55407.8986 | -261691.191 | 412196.045 | 8409051.3 | 362276.357 | -42082.8919 | 124794.319 | -57137.9318 | 208566.896 | 803658.008 | 2119724.11 | -24051.5753 | 59860.9998 | -15150.4873 | 50188.7855 | 87952.5334 | 345156.782 | -6587.1155
576.72 | 10.5324 | 1.149 |  | -50996.5815 | -272457.898 | 442739.25 | 8723911.9 | 517391.678 | -42889.0209 | 130936.191 | -57348.5634 | 214739.976 | 789067.425 | 2195961.86 | -26234.9379 | 60841.9789 | -14113.5976 | 51067.5675 | 81610.9072 | 343558.312 | -7779.678
576.92 | 10.5168 | 1.1495 |  | -46851.6286 | -265244.625 | 472137.984 | 8633815.76 | 638423.288 | -45556.2023 | 132819.358 | -55524.2588 | 220858.345 | 772085.361 | 2241639.35 | -27986.7661 | 59804.9879 | -13161.9337 | 52216.7164 | 76530.2082 | 336619.155 | -8587.9733
577.12 | 10.5285 | 1.1506 |  | -27991.0591 | -260970.121 | 502617.938 | 8491159.18 | 933445.305 | -47421.6511 | 127481.343 | -50767.1625 | 227899.035 | 748848.287 | 2204592.47 | -28154.816 | 61297.0813 | -13970.7922 | 53605.7159 | 82828.4194 | 347571.262 | -7682.0099
577.32 | 10.532 | 1.1512 |  | -14526.1709 | -253672.021 | 528127.412 | 8244527.83 | 1217173.45 | -43512.7091 | 125478.514 | -44488.46 | 232729.483 | 626216.381 | 2094796.45 | -27858.6471 | 58539.2759 | -10758.1774 | 53528.7255 | 69195.7499 | 340265.957 | -8345.9235
577.52 | 10.518 | 1.1522 |  | 13844.9957 | -239062.003 | 552729.397 | 7838940.08 | 1724913.83 | -43856.7591 | 128288.54 | -38070.8498 | 240679.307 | 524063.749 | 1953417.95 | -27716.1756 | 50285.3529 | -8054.9644 | 55557.406 | 55879.8698 | 300392.638 | -8100.8166
577.72 | 10.5094 | 1.1534 |  | 29298.7637 | -192852.127 | 567252.697 | 6714561.07 | 1900540.81 | -31727.0617 | 120577.49 | -29892.3312 | 242626.657 | 443914.334 | 1902639.44 | -22655.8573 | 49227.776 | -6890.3919 | 55517.5188 | 50006.6489 | 285105.229 | -7753.1568
577.92 | 10.5004 | 1.154 |  | 52978.1511 | -153875.69 | 579084.033 | 5715761.48 | 2231125.85 | -31828.7794 | 107082.92 | -19042.7336 | 244965.382 | 356575.653 | 1830454.61 | -18966.2429 | 51225.0425 | -6568.8906 | 56109.8305 | 47714.4662 | 291671.634 | -5831.4546
578.12 | 10.4695 | 1.1545 |  | 84918.9054 | -141240.223 | 576670.794 | 5419988.39 | 2856806.15 | -31722.7712 | 111506.103 | -11270.8515 | 244294.829 | 218584.872 | 1756568.78 | -19757.8285 | 41855.1938 | -1689.6664 | 55689.3324 | 23661.6547 | 236125.244 | -7050.5081
578.32 | 10.4559 | 1.1558 |  | 137977.831 | -153433.511 | 574561.366 | 5688325.79 | 3899308.2 | -36597.5534 | 118424.682 | -2778.1213 | 246394.512 | 110450.183 | 1623724.83 | -20404.7974 | 36128.1074 | -349.9623 | 56626.7431 | 16248.331 | 200163.855 | -4680.5506
578.52 | 10.4755 | 1.1563 |  | 163477.719 | -122893.424 | 553931.257 | 5109437.03 | 4454418.62 | -33884.5912 | 113577.351 | 8026.4212 | 239338.811 | 15334.321 | 1762412.87 | -18023.6806 | 45554.7188 | 331.7125 | 54954.4719 | 13103.6026 | 240154.679 | -6301.2165
578.72 | 10.4693 | 1.1561 |  | 184756.011 | -109742.698 | 533559.303 | 4942009.27 | 5018858.14 | -33341.1031 | 115044.926 | 16823.6659 | 235436.473 | -81255.3835 | 1878388.93 | -19066.0144 | 52072.9511 | 1467.6678 | 54736.7052 | 13315.1756 | 302264.498 | -6024.318
578.92 | 10.4756 | 1.1567 |  | 211619.317 | -99254.0491 | 505560.062 | 5098482.17 | 5650158.27 | -33994.7354 | 126782.582 | 20184.8777 | 229559.77 | -65213.9906 | 2049840.7 | -25157.3795 | 55254.138 | -123.2029 | 53869.2426 | 21294.886 | 302952.585 | -7410.353
579.12 | 10.5082 | 1.157 |  | 224301.72 | -105054.368 | 478256.356 | 5225648.84 | 5949754.12 | -44911.3965 | 131952.054 | 22500.3304 | 222772.083 | -127004.082 | 2060954.82 | -31429.588 | 51563.7311 | 2655.6236 | 52509.0256 | 7005.5114 | 288648.998 | -9659.0548
579.32 | 10.5107 | 1.1567 |  | 227422.723 | -78532.3025 | 448197.368 | 4644919.6 | 5958878.89 | -25036.0604 | 126997.205 | 25297.4269 | 217541.424 | -140900.794 | 1992959.86 | -19854.5627 | 51435.5705 | 1565.2779 | 51992.9903 | 13166.2203 | 290181.759 | -4123.4559
579.52 | 10.5438 | 1.157 |  | 212700.795 | -56822.8299 | 416492.83 | 4124386.62 | 5585451.23 | -23052.0952 | 117036.58 | 24639.6363 | 208919.215 | -104068.119 | 2046531.5 | -18560.91 | 57118.4316 | 210.9848 | 50031.2459 | 21182.0346 | 328132.285 | -5489.3343
579.72 | 10.5622 | 1.1571 |  | 214822.288 | -68515.321 | 392256.047 | 4263716.47 | 5618888.81 | -32454.5154 | 113951.586 | 25440.4272 | 204107.334 | -112480.405 | 1975770.95 | -24139.6109 | 56606.2885 | -114.8568 | 49214.0501 | 25548.8824 | 330422.02 | -5801.5269
579.92 | 10.5624 | 1.1581 |  | 199411.987 | -79026.379 | 363332.137 | 4350773.7 | 5302455.75 | -32651.5783 | 110967.357 | 22325.2635 | 197601.233 | -105747.046 | 1941009.03 | -21576.4463 | 55779.1004 | 531.375 | 47828.8685 | 20566.7739 | 327141.408 | -6153.7162
580.12 | 10.5849 | 1.1598 |  | 190156.865 | -85731.3993 | 334895.093 | 4715853.38 | 5180301.26 | -19354.8542 | 123856.413 | 15082.1417 | 193358.777 | -25075.303 | 1961675.49 | -17273.1061 | 49319.0681 | -239.4466 | 47624.2318 | 22388.1572 | 285327.619 | -3878.5971
580.32 | 10.6356 | 1.1605 |  | 172435.82 | -115376.466 | 314607.368 | 5323054.84 | 4951748.56 | -30632.9626 | 127282.515 | 10432.4321 | 187690.369 | -18071.4027 | 1989224.13 | -24058.9004 | 49224.6233 | 1155.0787 | 46352.6564 | 10910.7255 | 277946.068 | -7243.5175
580.52 | 10.6347 | 1.1606 |  | 150076.64 | -135169.858 | 299103.087 | 5743342.15 | 4632877.63 | -28125.5099 | 128797.06 | 5817.9228 | 186269.029 | 29999.5212 | 2037822.32 | -21429.3419 | 51393.9125 | 132.7585 | 46792.3287 | 12921.6467 | 281600.872 | -6379.9213
580.72 | 10.6695 | 1.1624 |  | 125301.013 | -167770.099 | 289283.882 | 6514073.62 | 4134066.92 | -39156.5313 | 132543.094 | -4585.2052 | 185577.55 | 141228.614 | 2061346.51 | -28745.0235 | 51804.4077 | -1567.4891 | 46883.6591 | 21276.9843 | 290052.85 | -8848.7617
580.92 | 10.7251 | 1.1639 |  | 94145.9501 | -198525.796 | 293024.417 | 7050800.05 | 3519337.78 | -36108.3855 | 131349.828 | -12999.3151 | 187198.96 | 243845.309 | 2003753.76 | -22273.4496 | 49958.5375 | -3909.4697 | 46895.4656 | 33975.345 | 282576.258 | -7136.6434
581.12 | 10.7513 | 1.1648 |  | 49405.6555 | -217715.756 | 298696.236 | 7542455.75 | 2658725.47 | -36414.8436 | 131524.43 | -25053.1686 | 190632.666 | 354897.878 | 2069890.31 | -21412.6271 | 54270.1463 | -5309.7343 | 48346.0523 | 37985.7305 | 307281.421 | -6631.3758
581.32 | 10.7785 | 1.1673 |  | 21448.7029 | -231845.277 | 317637.966 | 7992887.94 | 1933771.42 | -29609.7798 | 132220.879 | -39945.098 | 195577.618 | 581595.108 | 2157383.09 | -19410.2333 | 59420.1424 | -10973.1082 | 49297.0922 | 70241.9112 | 350834.481 | -6748.4604
581.52 | 10.8577 | 1.1698 |  | 2095.4979 | -266237.473 | 339143.9 | 8945377.65 | 1631655.82 | -45549.5575 | 147037.264 | -51230.0352 | 198868.546 | 715419.774 | 2280141.1 | -28319.2461 | 58722.6789 | -12724.3405 | 49279.1159 | 73344.0874 | 327653.146 | -7590.4635
581.72 | 10.8917 | 1.1707 |  | -13931.5955 | -290971.971 | 367213.149 | 9526320.37 | 1517417.82 | -48423.4483 | 155230.753 | -54576.7696 | 204210.164 | 690961.202 | 2348147.07 | -28998.0903 | 58981.904 | -10427.3426 | 49908.4764 | 60147.8852 | 323926.567 | -9766.5427
581.92 | 10.9066 | 1.1728 |  | -17550.4108 | -307437.24 | 403986.768 | 9825855.97 | 1505649.11 | -47413.2685 | 157673.566 | -55816.2322 | 216145.701 | 699856.825 | 2329984.37 | -25079.5957 | 57327.7507 | -10662.8922 | 53066.3913 | 61829.6291 | 316728.371 | -6971.329
582.12 | 10.9699 | 1.1751 |  | -28144.243 | -297656.729 | 438827.03 | 9739419.07 | 1289867.2 | -48928.4446 | 157620.25 | -57968.4054 | 223959.817 | 760555.213 | 2396835.28 | -28986.9836 | 60502.4841 | -12453.7625 | 54087.8779 | 73522.6111 | 339701.693 | -8838.9614
582.32 | 11.0093 | 1.1714 |  | -31875.0477 | -310079.117 | 475568.325 | 9914039.84 | 1161651.36 | -50733.2054 | 152858.081 | -58773.6822 | 234697.083 | 780280.627 | 2392228.12 | -24451.6105 | 63719.3918 | -13730.1456 | 56472.9155 | 80541.235 | 360856.844 | -5517.7692
582.52 | 11.0454 | 1.1642 |  | -27844.3675 | -298585.715 | 510953.75 | 9859304.83 | 1164869.98 | -50912.1173 | 157920.404 | -61792.9351 | 241825.175 | 850666.539 | 2478068.4 | -28473.9235 | 64475.703 | -15003.5898 | 57620.4524 | 87222.275 | 362094.159 | -7694.1264
582.72 | 11.1227 | 1.1572 |  | -7131.2585 | -303252.78 | 543207.272 | 10025448.6 | 1610715.64 | -49161.5952 | 160738.931 | -57822.3971 | 248103.522 | 814000.377 | 2526233.93 | -26197.2976 | 65903.9016 | -14643.2012 | 58115.9004 | 84635.3703 | 371222.65 | -6415.3769
582.92 | 11.1889 | 1.15 |  | 16199.7684 | -304108.031 | 571860.931 | 10007181.1 | 2233206.2 | -49170.4961 | 163044.004 | -47579.5189 | 255243.311 | 681018.042 | 2555829.91 | -28730.9764 | 66763.3953 | -11889.7891 | 59391.4528 | 73811.7533 | 371886.848 | -8000.1493
583.12 | 11.229 | 1.1449 |  | 41988.1075 | -288482.687 | 602106.902 | 9662846.91 | 2752668.67 | -50721.1597 | 162778.214 | -39379.3626 | 264990.812 | 578347.283 | 2556457.68 | -32029.712 | 65395.8659 | -9203.8698 | 61983.6694 | 58969.2997 | 359681.639 | -8392.9381
583.32 | 11.2978 | 1.1423 |  | 69216.3851 | -253763.654 | 623206.593 | 8880601.38 | 3216589.19 | -36054.9894 | 157645.115 | -30251.3244 | 269790.05 | 521290.687 | 2549371.48 | -26536.7704 | 68953.9371 | -10176.4037 | 62175.2609 | 71134.4554 | 398644.67 | -7830.205
583.52 | 11.3592 | 1.138 |  | 92453.8248 | -230784.784 | 644071.013 | 8459643.01 | 3583188.4 | -35364.5076 | 159785.074 | -26443.5357 | 277244.117 | 445122.284 | 2557225.67 | -24845.0652 | 66841.8464 | -7139.0293 | 64238.9202 | 51449.0857 | 373685.577 | -7086.7085
583.72 | 11.3764 | 1.1364 |  | 129897.188 | -221569.972 | 643726.147 | 8154015.18 | 4204517.73 | -43671.5443 | 153755.053 | -16265.5152 | 278334.462 | 351014.825 | 2426691.33 | -29902.4148 | 65742.7467 | -7183.6459 | 64408.6997 | 57775.6956 | 372451.456 | -8643.9158
583.92 | 11.4311 | 1.1371 |  | 163629.94 | -191108.927 | 636162.252 | 7459367 | 4742322.48 | -32058.5273 | 152392.532 | -8412.6544 | 276774.952 | 240031.836 | 2294403.67 | -22382.7461 | 58614.5713 | -4756.443 | 63914.1403 | 49029.6257 | 334399.173 | -5774.2786
584.12 | 11.473 | 1.1361 |  | 197391.396 | -180146.455 | 621949.865 | 7095092.24 | 5456353 | -27002.6834 | 149727.235 | 2988.6253 | 274836.047 | 73041.5956 | 2221781.1 | -19290.9796 | 56165.7109 | -487.0758 | 63052.1432 | 23648.0352 | 320835.444 | -4680.2623
584.32 | 11.4908 | 1.1351 |  | 223602.871 | -143961.601 | 599454.367 | 6408013.65 | 6091100.25 | -25929.071 | 150125.062 | 14613.7553 | 271385.148 | -19167.3812 | 2327082.52 | -22737.4734 | 60101.185 | 176.9546 | 63733.7622 | 18678.8748 | 331535.617 | -5903.0183
584.52 | 11.5317 | 1.1376 |  | 242211.746 | -121073.411 | 565386.039 | 6001995.36 | 6546083.6 | -28762.2919 | 151808.092 | 22034.0279 | 263760.745 | -90984.3844 | 2369265.41 | -28420.5998 | 61333.1637 | 1221.1001 | 62062.0735 | 16589.1475 | 342254.402 | -8336.3791
584.72 | 11.5868 | 1.1409 |  | 251771.958 | -110360.006 | 540398.479 | 5638826.04 | 6681571.52 | -28298.5275 | 143598.986 | 26721.0636 | 261380.178 | -132668.854 | 2315381.26 | -22906.1707 | 63083.3641 | 739.3727 | 62333.1337 | 21144.9768 | 360824.378 | -4440.9429
584.92 | 11.6513 | 1.1425 |  | 243213.771 | -84912.9154 | 505234.946 | 5341910.2 | 6579173.86 | -22856.3854 | 146920.783 | 25502.7502 | 252358.703 | -88589.6682 | 2464481.75 | -26166.3169 | 65794.1303 | 190.3675 | 60266.5703 | 23403.0602 | 373949.63 | -7855.6799
585.12 | 11.7039 | 1.1437 |  | 241774.927 | -116569.508 | 482532.918 | 5870793.43 | 6580395.98 | -38826.1885 | 147229.031 | 24673.407 | 250843.454 | -120338.46 | 2397374.08 | -33090.2197 | 62321.9876 | 1914.6448 | 60800.2544 | 14248.6187 | 353043.187 | -8599.0181
585.32 | 11.7405 | 1.1436 |  | 225569.088 | -107648.281 | 450264.603 | 5534117.23 | 6201044.95 | -36959.9708 | 136158.976 | 24437.9319 | 243948.991 | -99980.7846 | 2259857.35 | -30817.8694 | 61654.5767 | 476.2174 | 59390.4753 | 23636.8801 | 352608.398 | -9156.8015
585.52 | 11.7938 | 1.1401 |  | 195541.495 | -106597.515 | 429567.372 | 5223004.47 | 5479460.68 | -31414.0793 | 123717.095 | 19547.9771 | 240964.284 | -88320.8563 | 2073584.8 | -25408.8305 | 58531.2702 | 1151.0307 | 58492.7431 | 17340.0835 | 348584.644 | -7225.761
585.72 | 11.8291 | 1.1351 |  | 165950.854 | -115681.562 | 412013.794 | 5273524.43 | 4872122.47 | -29831.6719 | 122245.172 | 12906.289 | 239904.424 | -42556.9963 | 1971689.91 | -25521.423 | 52672.0979 | 1321.44 | 58770.8044 | 15026.8064 | 314765.67 | -7155.6172
585.92 | 11.8109 | 1.1301 |  | 131563.995 | -141377.678 | 400965.254 | 5685894.42 | 4162589.63 | -37845.8215 | 122264.142 | 3625.1427 | 239664.282 | 42625.448 | 1858979.78 | -27594.914 | 45463.2978 | 661.3735 | 58979.6185 | 15061.771 | 264361.761 | -8157.6487
586.12 | 11.8281 | 1.1262 |  | 106590.389 | -169909.02 | 395057.663 | 6310185.11 | 3511565.64 | -32818.3967 | 124873.276 | -11039.5802 | 239751.315 | 210901.01 | 1830732.86 | -21366.0329 | 43470.9157 | -2292.0756 | 59667.5909 | 25986.3646 | 254933.878 | -6463.8723
586.32 | 11.8725 | 1.1215 |  | 81504.7326 | -212185.889 | 396445.818 | 7491479.4 | 3218523.67 | -37382.092 | 140479.405 | -22250.7563 | 239430.125 | 327793.502 | 2063854.85 | -23151.3387 | 47157.1155 | -3664.448 | 59545.0625 | 32358.3127 | 268005.06 | -6324.3831
586.52 | 11.8442 | 1.1162 |  | 54700.7712 | -259692.497 | 402291.057 | 8690559.44 | 2933255.8 | -52804.211 | 150411.597 | -30471.0815 | 241348.418 | 416327.964 | 2235737.28 | -32680.7242 | 55732.9341 | -5487.5111 | 60214.0145 | 39445.2237 | 308582.496 | -10143.8056
586.72 | 11.8239 | 1.1135 |  | 9750.9251 | -267681.419 | 417830.863 | 9269154.92 | 2029948.44 | -41537.0333 | 156544.822 | -47321.7147 | 243022.192 | 658399.989 | 2544022.84 | -29119.8828 | 66887.2798 | -10508.8343 | 60899.1295 | 60832.1724 | 361004.249 | -10498.5229
586.92 | 11.8521 | 1.1111 |  | 6028.614 | -336350.716 | 444831.54 | 11048011.4 | 1952208.71 | -63549.8776 | 177981.958 | -63204.1703 | 249915.868 | 855955.427 | 2670611.68 | -34039.9351 | 66052.93 | -14255.8666 | 62443.4081 | 75790.0719 | 340531.482 | -8208.4494
587.12 | 11.8666 | 1.1069 |  | -2525.0321 | -369630.008 | 471363.379 | 12021573.8 | 1987239.06 | -70905.3225 | 192927.398 | -68985.6669 | 251512.162 | 893714.012 | 2806749.36 | -36565.5851 | 66606.4301 | -13734.1929 | 61450.7125 | 74296.5106 | 346264.398 | -10186.1769
587.32 | 11.8531 | 1.1026 |  | -19478.3227 | -381788.884 | 507899.833 | 12386490.1 | 1793241.34 | -65303.8219 | 196230.439 | -71822.8926 | 260744.478 | 898527.677 | 2945533.87 | -32929.8317 | 73526.1505 | -13646.1778 | 63820.0979 | 74953.5221 | 399776.617 | -8809.5177
587.52 | 11.8395 | 1.0996 |  | -13325.7985 | -361777.362 | 542665.2 | 12019277.9 | 1727752.78 | -82776.6072 | 190363.397 | -71281.9472 | 264599.965 | 1014880.87 | 3046286.54 | -47649.6153 | 81779.5832 | -18772.4666 | 64071.6249 | 110144.214 | 463136.887 | -13224.0452
587.72 | 11.8744 | 1.0965 |  | -10516.9607 | -342360.33 | 581371.448 | 11581670.9 | 1803997.61 | -62789.3348 | 191079.051 | -69007.5043 | 270943.85 | 982457.952 | 2983204.94 | -35561.4568 | 77016.3545 | -17985.1418 | 63945.9283 | 108201.177 | 432160.677 | -8268.2463
587.92 | 11.8837 | 1.0919 |  | 14469.3711 | -344075.458 | 620913.294 | 11364734.9 | 2117849.57 | -69188.0118 | 182114.341 | -63347.9576 | 281183.239 | 900719.91 | 2929689.01 | -34323.1697 | 78027.5914 | -16094.7027 | 66182.3466 | 96538.7985 | 447549.772 | -8010.6927
588.12 | 11.8303 | 1.0879 |  | 18796.5054 | -310821.245 | 643058.962 | 10701835.7 | 2297610.92 | -50373.2645 | 181733.205 | -55915.2932 | 285259.492 | 793984.67 | 2868767.29 | -33660.0477 | 75855.0527 | -14105.0705 | 66206.8548 | 88466.6723 | 425121.657 | -8448.1551
588.32 | 11.8396 | 1.086 |  | 58648.0193 | -295331.101 | 661083.452 | 10305442.1 | 2905075.83 | -46823.1482 | 182180.71 | -51283.256 | 291094.101 | 727690.18 | 2741823.95 | -29491.8582 | 69719.7668 | -12229.1439 | 68083.4632 | 76392.01 | 395598.548 | -7331.3415
588.52 | 11.8528 | 1.0829 |  | 84829.7541 | -254472.253 | 673679.639 | 9353630.14 | 3507858.49 | -44193.1515 | 175357.207 | -35801.1607 | 290309 | 588575.867 | 2754787.64 | -31121.0465 | 71766.5972 | -10607.1168 | 66737.6969 | 71003.5735 | 405929.269 | -8515.3094
588.72 | 11.8145 | 1.0793 |  | 104394.929 | -223219.886 | 679881.164 | 8413994.85 | 3920064.26 | -43420.9581 | 163431.734 | -21307.3033 | 293367.313 | 388038.297 | 2627917.39 | -33375.9242 | 70475.1589 | -6389.9937 | 67732.2937 | 52543.5082 | 402922.896 | -10153.1013
588.92 | 11.7731 | 1.0773 |  | 140010.566 | -189896.14 | 676717.974 | 7602862.22 | 4361742.73 | -31755.0009 | 154681.415 | -13483.8253 | 295900.747 | 330225.559 | 2426712.76 | -23715.2937 | 64920.9323 | -7179.8724 | 68594.4563 | 61407.317 | 377764.981 | -4949.6508
589.12 | 11.7741 | 1.0755 |  | 164342.294 | -182704.793 | 668450.304 | 7283634.63 | 4683206.4 | -31917.8712 | 151445.025 | -9200.49 | 293242.027 | 240277.404 | 2284521.13 | -20258.2004 | 58856.5659 | -4117.4656 | 67225.6587 | 45672.4603 | 351523.883 | -4922.9394
589.32 | 11.7464 | 1.0737 |  | 193026.617 | -178099.727 | 641770.098 | 7302842.21 | 5341977.51 | -23458.6299 | 156620.219 | -2241.338 | 287703.561 | 155298.038 | 2355636.55 | -19747.7752 | 59465.5343 | -1974.0574 | 67061.0503 | 23447.5384 | 311847.084 | -5955.7291
589.52 | 11.7105 | 1.0741 |  | 221118.273 | -158120.337 | 605591.117 | 7225578.39 | 6001273.14 | -23045.6342 | 166583.54 | 2717.4853 | 278311.132 | 139591.36 | 2564174.06 | -25837.16 | 65397.7483 | -2873.5867 | 66111.57 | 29347.6641 | 343353.385 | -7866.958
589.72 | 11.6856 | 1.0754 |  | 240712.911 | -152208.211 | 572223.745 | 7073151.87 | 6483999.96 | -30926.133 | 167501.789 | 10477.4904 | 268373.813 | 66216.0997 | 2585816.06 | -30623.1822 | 66331.8619 | -2093.6167 | 63366.3444 | 34583.4388 | 371073.872 | -9028.2021
589.92 | 11.6546 | 1.0761 |  | 236932.166 | -121838.546 | 523836.32 | 6405733.16 | 6409049.6 | -23825.808 | 158879.444 | 14732.1175 | 256357.822 | 33080.0887 | 2583636.83 | -24461.6769 | 69063.0912 | -2439.1074 | 61405.7647 | 37257.6397 | 389031.932 | -6337.6391
590.12 | 11.6592 | 1.0756 |  | 236155.431 | -118257.721 | 488394.505 | 6395222.17 | 6371941.52 | -10757.2992 | 157966.287 | 13077.0237 | 249209.843 | 62463.2245 | 2558793.76 | -17224.8347 | 68542.3112 | -3587.675 | 59929.8835 | 44035.2261 | 389308.968 | -3482.659
590.32 | 11.6596 | 1.0746 |  | 226984.043 | -143247.765 | 448098.952 | 6944731.86 | 6306529.8 | -28812.5502 | 165459.186 | 9454.3664 | 240217.292 | 67622.174 | 2608643.68 | -30370.5849 | 65971.2279 | -1636.6523 | 58917.8327 | 28671.7336 | 363932.888 | -7440.6726
590.52 | 11.601 | 1.0739 |  | 205738.3 | -152314.895 | 414721.319 | 6972347.9 | 5860672.34 | -34974.6505 | 159117.775 | 6112.2005 | 232370.318 | 72017.5253 | 2499528.15 | -33976.0529 | 64322.1813 | -1010.487 | 57260.1064 | 25647.9334 | 364599.337 | -10743.1472
590.72 | 11.562 | 1.0736 |  | 168775.288 | -153636.136 | 387467.114 | 6586308.85 | 4951569.04 | -31115.4985 | 141443.348 | 1113.2639 | 226665.562 | 137439.586 | 2276486.61 | -25044.8063 | 60938.0258 | -3199.7235 | 56127.0494 | 35361.1264 | 343817.918 | -6733.4619
590.92 | 11.5394 | 1.0736 |  | 129734.568 | -165092.377 | 369496.708 | 6601887.05 | 4085013.15 | -30105.9948 | 132438.433 | -6763.0403 | 221779.217 | 211376.209 | 2162133.12 | -22088.4038 | 57864.601 | -4131.6788 | 54799.6615 | 39962.8911 | 335494.648 | -5643.8939
591.12 | 11.4742 | 1.0735 |  | 106754.423 | -196030.559 | 357123.282 | 7270767.57 | 3648915.45 | -39227.0372 | 138243.686 | -16587.0221 | 220029.479 | 302781.782 | 2130958.56 | -26970.0953 | 53430.7604 | -4734.8229 | 55232.1789 | 38661.7628 | 300935.315 | -6535.8182
591.32 | 11.4236 | 1.0735 |  | 71818.7135 | -206604.758 | 348859.533 | 7557016.95 | 2982068.48 | -38274.0552 | 138111.912 | -26184.2868 | 214532.484 | 416821.631 | 2188931.84 | -26194.518 | 57909.3086 | -6979.7688 | 53374.6282 | 48160.0365 | 331674.99 | -8419.9739
591.52 | 11.3941 | 1.0731 |  | 44438.0668 | -220260.441 | 346243.605 | 8115722.7 | 2562460.16 | -31817.468 | 148276.388 | -36029.6552 | 212917.168 | 511268.434 | 2334069.29 | -25577.9512 | 61324.5671 | -8267.9096 | 53542.6469 | 53037.1896 | 347124.693 | -8050.4485
591.72 | 11.3804 | 1.0729 |  | 32993.3957 | -266034.824 | 360198.633 | 9274751.74 | 2494046.55 | -41136.2338 | 166464.976 | -45916.6974 | 216587.514 | 603292.945 | 2478836.68 | -29029.1644 | 59367.0446 | -8582.6233 | 53926.2272 | 56134.5763 | 334773.429 | -9007.8626
591.92 | 11.3569 | 1.0724 |  | 9791.1103 | -293525.334 | 379420.707 | 9916379.52 | 2074011.69 | -47207.1374 | 169697.69 | -54240.0063 | 221946.115 | 729208.7 | 2590016.7 | -26732.2329 | 65441.3274 | -11907.4634 | 55761.1234 | 67219.0338 | 358305.618 | -7173.6806
592.12 | 11.3651 | 1.0723 |  | -17849.7737 | -288579.671 | 397547.491 | 10141154.4 | 1522209.47 | -53585.7682 | 171203.116 | -62627.3846 | 221759.074 | 905201.095 | 2812340.71 | -35282.9727 | 75745.0556 | -17239.5963 | 55594.8974 | 97034.3163 | 416117.643 | -9904.6151
592.32 | 11.3376 | 1.0721 |  | -31093.6439 | -322905.09 | 435229.223 | 10651829.2 | 1180965.1 | -68670.1977 | 168545.185 | -67306.1523 | 230987.148 | 948621.476 | 2741324.49 | -39377.7423 | 73144.0937 | -17485.4239 | 56576.9852 | 102500.549 | 416594.854 | -9187.1458
592.52 | 11.2952 | 1.0715 |  | -49376.4562 | -298363.479 | 460418.865 | 10146308.8 | 640361.234 | -58586.5532 | 158365.492 | -71836.5866 | 232329.775 | 1062385.3 | 2770525.69 | -32245.7422 | 78188.7153 | -21253.9968 | 56325.0581 | 118263.278 | 442549.292 | -7794.498
592.72 | 11.2995 | 1.0708 |  | -41587.3539 | -315550.752 | 502841.542 | 10230828.7 | 764779.04 | -64950.7099 | 151877.294 | -67024.2474 | 241262.999 | 974421.142 | 2563822.43 | -36827.1451 | 73518.8042 | -19429.2139 | 57158.7751 | 116278.405 | 425554.046 | -8720.3585
592.92 | 11.2515 | 1.0703 |  | -33814.6513 | -297551.266 | 537887.473 | 9667015.8 | 984428.28 | -51419.0381 | 147318.99 | -58850.4935 | 248388.342 | 856174.231 | 2486587.36 | -30806.3427 | 70165.6061 | -16754.7042 | 57765.624 | 100834.645 | 399399.018 | -6883.9473
593.12 | 11.2023 | 1.0706 |  | -30423.808 | -255577.374 | 565859.94 | 8699347.75 | 982153.051 | -38836.5277 | 137972.118 | -52602.0914 | 254955.574 | 811402.832 | 2505154.1 | -23728.0138 | 72422.1038 | -16710.7811 | 60259.3874 | 95087.5369 | 401713.577 | -4488.0839
593.32 | 11.2013 | 1.0726 |  | 8364.879 | -259699.034 | 598807.636 | 8739904.37 | 1669610.23 | -49282.165 | 143091.795 | -46910.4898 | 261775.117 | 716751.362 | 2346575.57 | -31788.0481 | 63660.8315 | -13464.6755 | 60167.7082 | 88508.8237 | 371869.124 | -8824.0104
593.52 | 11.1965 | 1.0735 |  | 46899.2196 | -250252.376 | 618353.789 | 8462163.42 | 2462862.51 | -42777.6829 | 145059.81 | -36431.1958 | 267301.677 | 542810.105 | 2238232.07 | -24027.9173 | 58305.8937 | -9343.5852 | 61355.4308 | 64417.3559 | 334970.549 | -5363.7555
593.72 | 11.1859 | 1.0741 |  | 73798.6048 | -221942.053 | 629795.516 | 7845779.39 | 3119968.55 | -34608.599 | 142560.942 | -22964.7389 | 269284.579 | 392647.489 | 2285475.08 | -25648.0842 | 61334.8066 | -6658.2545 | 61649.0064 | 51420.6169 | 348186.674 | -7907.8705
593.92 | 11.1824 | 1.0747 |  | 116754.346 | -216663.966 | 635502.827 | 7636090.84 | 3920140.68 | -45534.7733 | 142317.683 | -12773.1916 | 273705.907 | 278481.486 | 2182344.31 | -31655.201 | 56687.3791 | -4689.762 | 63070.1972 | 44242.0361 | 326210.28 | -9277.7481
594.12 | 11.1552 | 1.075 |  | 136514.733 | -182933.596 | 629938.183 | 6687549.8 | 4032628.58 | -37163.4499 | 126274.901 | -5734.913 | 272864.578 | 196358.697 | 1996915.4 | -21634.1137 | 54855.9107 | -3784.6738 | 62879.7265 | 40227.5797 | 318969.07 | -6055.9989
594.32 | 11.1292 | 1.0756 |  | 143383.76 | -140069.431 | 614855.83 | 5694825.65 | 3980026.25 | -25356.0028 | 112252.276 | -431.2377 | 268672.336 | 178821.002 | 1958191.67 | -15436.7567 | 56524.8693 | -4481.8962 | 62193.0828 | 41166.2736 | 324808.541 | -2769.4869
594.52 | 11.0946 | 1.0764 |  | 164992.492 | -111184.548 | 589351.032 | 5490907.17 | 4459637 | -21004.1294 | 127045.894 | 300.7061 | 259315.862 | 194420.66 | 2176653.67 | -18931.0596 | 58887.1865 | -4461.067 | 60122.4973 | 37392.5427 | 314475.482 | -6106.7946
594.72 | 11.0704 | 1.0782 |  | 216571.359 | -166655.82 | 568089.678 | 6850601.08 | 5748140.91 | -33104.0298 | 150882.75 | 5441.7028 | 256288.178 | 55788.3946 | 2198662.85 | -22625.5725 | 52091.2213 | 157.5878 | 59810.7382 | 13961.2997 | 274033.718 | -5535.3364
594.92 | 11.0349 | 1.0811 |  | 233444.88 | -152046.627 | 529008.53 | 6828295.58 | 6344554.16 | -30484.6319 | 161469.393 | 12352.0853 | 246365.111 | -17412.0655 | 2389633.91 | -28873.9513 | 57136.1566 | 1384.9169 | 58635.936 | 6128.8542 | 286053.143 | -8704.1164
595.12 | 11.0084 | 1.0837 |  | 238328.357 | -139888.539 | 495992.56 | 6408351.47 | 6285512.29 | -33912.3506 | 147859.029 | 15804.5431 | 238770.71 | -30466.8191 | 2309637.26 | -28389.5726 | 60228.9807 | 79.2302 | 57071.6229 | 22768.4114 | 347106.413 | -9015.7501
595.32 | 11.0185 | 1.0857 |  | 229611.299 | -107728.966 | 462137.216 | 5714500.07 | 6005328.69 | -19196.3728 | 142384.112 | 14766.1941 | 229174.083 | 11023.05 | 2255788.03 | -18213.2283 | 57702.3097 | -1174.5434 | 54710.5002 | 30347.2472 | 330590.367 | -5357.0219
595.52 | 11.0102 | 1.0869 |  | 214820.372 | -106746.852 | 423463.896 | 5657988.78 | 5764360.23 | -14486.8256 | 140576.258 | 13341.9136 | 220992.819 | -14177.7974 | 2234972.22 | -16880.7636 | 57911.4511 | -144.4092 | 53646.7489 | 21767.4558 | 328127.137 | -3246.1246
595.72 | 10.9826 | 1.0876 |  | 211009.767 | -109616.725 | 388263.217 | 5674386.59 | 5688242.34 | -28427.6075 | 137363.557 | 12978.0692 | 211335.985 | 11050.4169 | 2213633.29 | -25871.8455 | 59007.3182 | -1120.9789 | 51521.8169 | 27756.9351 | 341108.841 | -8348.2749
595.92 | 10.973 | 1.0878 |  | 193202.618 | -128035.816 | 358760.517 | 5758434.46 | 5402072.79 | -31495.7325 | 133599.899 | 12655.8596 | 205261.025 | -24877.5692 | 2076315.61 | -23849.3298 | 52982.3894 | 347.7909 | 50281.1752 | 18655.1455 | 301644.336 | -6108.0798
596.12 | 10.9633 | 1.0878 |  | 160918.569 | -139305.001 | 333212.462 | 5798308.99 | 4795637.11 | -28665.0395 | 127513.962 | 7794.7793 | 201417.938 | -10734.7115 | 1953877.31 | -20239.7398 | 49719.9768 | 991.7411 | 49751.2648 | 14713.4457 | 296181.503 | -5743.2643
596.32 | 10.9186 | 1.0878 |  | 116470.868 | -146193.538 | 319635.967 | 5940750.18 | 3790512.21 | -25226.7808 | 124587.109 | -5621.3981 | 200062.94 | 155346.738 | 1997455.57 | -20045.5103 | 50147.3298 | -1528.1483 | 50477.5818 | 20097.4397 | 280672.988 | -6750.8486
596.52 | 10.8754 | 1.0878 |  | 92469.8946 | -187970.876 | 309539.536 | 6933410.74 | 3186977.01 | -37247.5063 | 130373.859 | -20595.5091 | 197739.302 | 354127.551 | 1957136.14 | -24149.4336 | 46657.3101 | -5729.7245 | 49911.6891 | 40883.3534 | 263494.127 | -6728.2184
596.72 | 10.848 | 1.0897 |  | 53343.9507 | -202041.323 | 302919.208 | 7358305.84 | 2414513.03 | -32070.5316 | 131960.504 | -32709.6893 | 191939.087 | 478342.897 | 2036310.63 | -22567.8014 | 51980.9629 | -7649.0847 | 48234.996 | 45462.9262 | 277850.591 | -7722.1892
596.92 | 10.8024 | 1.0922 |  | 23917.666 | -218478.583 | 302914.926 | 7882245.09 | 2044162.57 | -30587.0405 | 141237.537 | -39769.5692 | 189460.685 | 549068.551 | 2199416.93 | -22230.4368 | 55564.3159 | -8843.6292 | 47901.1606 | 52305.5757 | 301170.734 | -7080.6867
597.12 | 10.8028 | 1.095 |  | 20279.3251 | -262532.247 | 314217.525 | 9000095.2 | 2176327.45 | -38087.4938 | 153261.365 | -44832.9188 | 191750.986 | 597959.521 | 2295074.22 | -24162.3515 | 57010.6236 | -9609.7578 | 47761.4838 | 59257.4694 | 320612.382 | -7947.6982
597.32 | 10.7871 | 1.0965 |  | 3377.7556 | -291456.509 | 336562.297 | 9696862.38 | 1959620.17 | -49119.2418 | 159886.196 | -50467.0042 | 198648.771 | 653137.075 | 2425262.02 | -29411.4565 | 61396.0516 | -10150.4403 | 50158.8446 | 56905.6373 | 328320.148 | -8715.9859
597.52 | 10.7871 | 1.0978 |  | -23657.1266 | -283078.588 | 356948.877 | 9550414.34 | 1317508.16 | -48277.7232 | 152828.246 | -56710.3853 | 201074.221 | 815421.574 | 2538424.17 | -30601.1132 | 68870.514 | -15359.5442 | 50247.7837 | 86660.1657 | 381149.168 | -9836.0447
597.72 | 10.8006 | 1.0987 |  | -39743.0713 | -296920.534 | 390016.239 | 9622258.07 | 778277.631 | -54890.3414 | 143387.449 | -62674.0323 | 208393.271 | 881997.817 | 2407717.71 | -30483.048 | 67548.6242 | -16745.6973 | 50962.7429 | 97212.5575 | 390535.535 | -8003.8037
597.92 | 10.799 | 1.0994 |  | -56903.081 | -272960.67 | 415328.774 | 9007904.18 | 411377.152 | -47494.9554 | 136528.423 | -62210.7923 | 210958.489 | 872960.785 | 2324810.87 | -30263.5455 | 65016.3218 | -16251.1046 | 50572.2358 | 94117.1021 | 373868.091 | -8697.2784
598.12 | 10.7896 | 1.1009 |  | -48411.3479 | -277806.733 | 453302.882 | 8631802.17 | 482917.762 | -47473.0347 | 120726.485 | -54663.7082 | 220961.043 | 753226.439 | 2063970.4 | -25790.9247 | 62104.5183 | -14216.7166 | 52191.5228 | 85687.6926 | 365307.07 | -6511.1187
598.32 | 10.8048 | 1.103 |  | -40210.714 | -249857.115 | 490789.385 | 7888143.84 | 704732.486 | -43894.9551 | 119476.378 | -47094.1233 | 229364.697 | 673896.399 | 2016411.52 | -25805.5139 | 55486.5175 | -12005.5681 | 53618.9533 | 73876.3773 | 321532.041 | -6767.5983
598.52 | 10.799 | 1.1044 |  | -29804.0455 | -247926.837 | 529175.569 | 7676090.2 | 884770.705 | -44013.8345 | 115400.398 | -42047.7078 | 241465.287 | 561702.408 | 1954925.93 | -23952.046 | 52781.044 | -8160.1086 | 56322.2679 | 53626.479 | 308437.629 | -6358.1691
598.72 | 10.7966 | 1.1061 |  | -2342.3204 | -248529.098 | 563115.874 | 7849045.99 | 1318577.69 | -36492.5182 | 120287.707 | -40871.5352 | 252176.967 | 590709.995 | 1931449.95 | -20292.0394 | 51633.5788 | -10245.3109 | 58668.3665 | 67744.5031 | 301183.481 | -5562.7816
598.92 | 10.8141 | 1.1078 |  | 22823.6741 | -257348.664 | 584046.508 | 8258575.94 | 1776142.73 | -44679.9411 | 130515.09 | -41173.3782 | 255639.799 | 584958.319 | 2003529.7 | -25484.5521 | 50703.6699 | -9311.1885 | 59104.1661 | 58508.2019 | 284374.027 | -7324.8666
599.12 | 10.8501 | 1.1084 |  | 60374.3024 | -229677.468 | 593149.32 | 7925645.41 | 2641119.64 | -39711.8162 | 138561.253 | -31247.9763 | 253897.979 | 497089.792 | 2141893.19 | -26104.0417 | 53895.1062 | -8200.9122 | 58407.0274 | 53711.0685 | 292350.908 | -8781.1724
599.32 | 10.8781 | 1.1082 |  | 104394.374 | -224147.305 | 607025.96 | 7705081.86 | 3667202.36 | -39938.793 | 141565.039 | -16077.7012 | 258075.345 | 267473.178 | 2095283.34 | -25639.6697 | 50727.8275 | -2940.1798 | 58949.0167 | 29989.4265 | 280368.563 | -7797.6708
599.52 | 10.8984 | 1.1085 |  | 136803.11 | -186505.635 | 606827.138 | 6705432.67 | 4309844.69 | -42084.9271 | 131166.785 | 48.056 | 260447.163 | 134568.574 | 2037578.23 | -27357.3683 | 53301.3243 | -2732.8444 | 59997.3302 | 33374.927 | 296540.506 | -7509.6676
599.72 | 10.9427 | 1.109 |  | 153386.643 | -144310.208 | 605394.214 | 5657759.88 | 4400449.28 | -30164.0481 | 118152.798 | 5842.9058 | 261680.237 | 58105.0214 | 1923354.31 | -17164.9144 | 53246.3637 | -1106.492 | 60141.9018 | 26620.1182 | 318304.288 | -4961.9605
599.92 | 10.9867 | 1.1086 |  | 182611.619 | -139664.508 | 591008.243 | 5775860.68 | 5000635.12 | -26627.8946 | 128347.552 | 9269.3326 | 261174.549 | 17017.3071 | 1931442 | -17297.3234 | 48110.9311 | -9.3239 | 60370.6446 | 20963.3091 | 277940.711 | -3052.2758
600.12 | 10.9951 | 1.1083 |  | 205608.462 | -139497.71 | 568486.22 | 6142025.41 | 5519871.76 | -26177.8507 | 140914.693 | 9335.4743 | 256946.209 | 13691.5171 | 2133954.01 | -20617.8219 | 52467.9454 | 616.0162 | 60357.3238 | 14746.6072 | 289013.718 | -5775.1537
600.32 | 11.0115 | 1.1089 |  | 226880.89 | -141674.966 | 541952.74 | 6428450.64 | 6059287.51 | -25370.5355 | 148897.083 | 12629.681 | 249218.239 | 13957.189 | 2285464.14 | -23446.9911 | 57809.0372 | -448.3563 | 58768.0494 | 20233.7998 | 313729.892 | -7440.7562
600.52 | 11.0712 | 1.1091 |  | 241615.061 | -133364.107 | 507459.077 | 6405352.15 | 6444663.29 | -26397.4328 | 155532.975 | 15994.4656 | 240011.96 | -22655.7623 | 2391041.14 | -26607.0593 | 59261.1442 | 342.9332 | 57004.3581 | 17621.8045 | 317345.84 | -9243.986
600.72 | 11.1116 | 1.1078 |  | 253465.662 | -137048.001 | 483185.758 | 6288704.89 | 6735872.43 | -28506.6401 | 150178.756 | 23549.9104 | 235699.611 | -152593.153 | 2249910.11 | -24053.3586 | 57359.0877 | 2533.6137 | 55826.9776 | 10313.7865 | 328591.978 | -6250.6471
600.92 | 11.1555 | 1.1065 |  | 237611.445 | -104930.051 | 450154.501 | 5579067.55 | 6478181.36 | -18837.7017 | 145934.603 | 24705.0829 | 229860.774 | -147191.79 | 2352177.4 | -19186.3987 | 62252.3538 | 1959.884 | 55545.9436 | 12799.1655 | 348948.341 | -6057.4984
601.12 | 11.1983 | 1.1053 |  | 228501.475 | -111628.257 | 423896.286 | 5910384.98 | 6240044.32 | -15916.0014 | 147034.374 | 18451.8753 | 227536.762 | -58465.1555 | 2346533.18 | -16396.236 | 61374.3103 | 83.9807 | 55848.0144 | 22941.7881 | 348401.965 | -4372.8943
601.32 | 11.2431 | 1.1038 |  | 218615.483 | -164401.85 | 400710.407 | 6975587.84 | 6015485.12 | -29267.9763 | 153653.62 | 9342.6996 | 224228.693 | 35069.595 | 2288627.92 | -22463.967 | 57473.7339 | -1361.4813 | 54905.051 | 29604.447 | 328245.517 | -4968.4203
601.52 | 11.2478 | 1.1025 |  | 188562.669 | -179461.876 | 370162.654 | 7537599.34 | 5384136.18 | -33179.327 | 158813.842 | -4034.9417 | 217951.345 | 178598.795 | 2451612.42 | -25845.3956 | 61566.7697 | -3027.3332 | 54827.0363 | 28365.8598 | 333216.174 | -5787.8273
601.72 | 11.2786 | 1.1023 |  | 157748.455 | -181904.136 | 344994.695 | 7594152.21 | 4797367.72 | -30468.5984 | 152965.247 | -9776.2219 | 207146.963 | 303550.825 | 2555103.56 | -24450.7661 | 70066.8209 | -6945.8009 | 51992.8067 | 47322.6565 | 378464.721 | -8282.5521
601.92 | 11.3089 | 1.1002 |  | 126183.033 | -211355.564 | 334251.203 | 8214669.41 | 4344001.23 | -29420.4841 | 158270.761 | -16571.4177 | 206068.611 | 328329.918 | 2555439.33 | -22423.1684 | 68213.8442 | -6690.111 | 51597.9634 | 50826.3562 | 385216.44 | -5427.2305
602.12 | 11.3098 | 1.094 |  | 95831.2843 | -225228.874 | 331321.046 | 8750271.68 | 3783399.51 | -32134.3446 | 165221.807 | -28690.9325 | 208066.169 | 498593.673 | 2642232.31 | -23958.9506 | 70498.3509 | -10274.018 | 52803.8104 | 61982.0146 | 384149.204 | -4753.4709
602.32 | 11.3731 | 1.0878 |  | 53550.1542 | -250865.401 | 340200.809 | 9539092.38 | 3005530.4 | -29610.5069 | 175600.471 | -44085.0378 | 207661.708 | 622415.125 | 2808516.11 | -24843.2831 | 75422.9206 | -10912.2097 | 52542.8098 | 65550.5241 | 419888.74 | -8594.8922
602.52 | 11.3915 | 1.0825 |  | 44129.3802 | -305262.352 | 354591.503 | 10843500.3 | 3022349.88 | -52899.0536 | 186677.32 | -49351.2859 | 214308.209 | 750601.029 | 2924833.04 | -36022.7114 | 75416.7832 | -14679.5017 | 54558.4776 | 86154.6903 | 414178.974 | -7151.3994
602.72 | 11.4148 | 1.0813 |  | 13379.7817 | -321418.517 | 377514.464 | 11194318.6 | 2318218.96 | -61239.0145 | 187088.221 | -61152.4899 | 216123.024 | 868770.812 | 3017098.81 | -38106.8841 | 80958.383 | -16059.7172 | 54043.0716 | 94089.2513 | 454845.683 | -11072.9214
602.92 | 11.4622 | 1.0812 |  | 162.2119 | -347672.774 | 407273.741 | 11682640.2 | 2076410.15 | -64431.0312 | 190166.088 | -65936.2674 | 225877.084 | 905559.997 | 2858500.1 | -37779.1119 | 73142.033 | -16690.6971 | 55619.0551 | 101598.374 | 417613.556 | -9065.6931
603.12 | 11.4886 | 1.0805 |  | -17473.4984 | -342940.776 | 441144.392 | 11233845.9 | 1548559.89 | -63664.2472 | 177230.103 | -67856.3025 | 232624.906 | 910009.234 | 2741941.17 | -32323.2455 | 70736.5298 | -15770.0617 | 56455.7451 | 92443.847 | 403521.508 | -8832.1253
603.32 | 11.5046 | 1.0797 |  | -30538.062 | -327007.653 | 480536.171 | 10735529.1 | 1323919.98 | -53039.5152 | 171506.821 | -65736.1033 | 242788.858 | 884312.657 | 2671534.18 | -28489.1699 | 68355.5409 | -15115.0703 | 58519.0004 | 87300.4911 | 384031.022 | -6220.4656
603.52 | 11.5163 | 1.0793 |  | -23670.3594 | -317324.105 | 516322.334 | 10226002.5 | 1306569.72 | -60136.3293 | 157878.291 | -60287.2779 | 250954.923 | 847029.407 | 2580728.94 | -30678.3142 | 70141.5105 | -15452.5984 | 60084.723 | 90722.2493 | 397486.617 | -7741.1821
603.72 | 11.5494 | 1.079 |  | -16618.3705 | -313003.155 | 556565.323 | 10069748.4 | 1532614.42 | -54952.7772 | 157979.879 | -55431.7784 | 260814.488 | 789777.558 | 2523450.79 | -27130.0991 | 65029.5066 | -13876.6849 | 61229.7268 | 83407.4347 | 362869.068 | -6571.3321
603.92 | 11.611 | 1.0787 |  | 9515.196 | -325226.686 | 592052.487 | 10300670.6 | 2017969.2 | -55427.6364 | 163608.738 | -52610.0146 | 273032.279 | 683351.701 | 2453932.41 | -27682.4196 | 61097.3141 | -9910.1844 | 64384.9107 | 61201.6587 | 342926.614 | -6931.2957
604.12 | 11.6382 | 1.0779 |  | 33408.9963 | -322348.626 | 633823.976 | 10292248.4 | 2526557.27 | -48464.512 | 168307.902 | -46820.2144 | 284709.711 | 623993.384 | 2478942.78 | -23932.3023 | 59996.4692 | -8953.09 | 66089.0112 | 57978.9921 | 328378.7 | -6737.4564
604.32 | 11.6407 | 1.0764 |  | 53237.6396 | -310249.588 | 650625.922 | 10232760.2 | 2822547.72 | -50849.0192 | 169199.818 | -44432.9742 | 289954.721 | 635324.881 | 2562643.93 | -29652.1723 | 62750.4375 | -9584.3871 | 68269.8648 | 60123.7015 | 343546.226 | -8630.9527
604.52 | 11.7143 | 1.0759 |  | 87768.5487 | -280056.888 | 666084.17 | 9744925.78 | 3392893.05 | -42823.0199 | 174605.349 | -40195.9404 | 289791.048 | 597432.376 | 2572790.31 | -29604.7657 | 61676.2671 | -9180.7807 | 67074.5698 | 60732.1774 | 337591.689 | -9119.9619
604.72 | 11.7371 | 1.0758 |  | 127224.978 | -253303.309 | 667192.777 | 8977437.71 | 4308588.76 | -46311.1824 | 168553.943 | -20606.8717 | 288694.251 | 385305.339 | 2519744.88 | -33088.5197 | 62353.1074 | -6326.4039 | 66748.3049 | 50515.5192 | 341674.118 | -8285.3893
604.92 | 11.7391 | 1.0751 |  | 148717.784 | -189200.324 | 665626.989 | 7442098.35 | 4714788.74 | -29377.1699 | 150670.832 | -4119.9281 | 287246.923 | 220234.548 | 2548415.26 | -22969.7288 | 70523.828 | -4527.9568 | 66065.5995 | 44583.1927 | 402758.505 | -7031.7332
605.12 | 11.7714 | 1.0736 |  | 198656.343 | -187694.514 | 657008.089 | 7420141.16 | 5632162.84 | -36945.5014 | 149424.741 | 6041.7162 | 290806.405 | 135845.67 | 2484381.23 | -27828.7289 | 67097.2181 | -3804.2807 | 67781.7882 | 41048.1569 | 375371.235 | -5641.4231
605.32 | 11.8 | 1.0722 |  | 216678.066 | -174085.428 | 639474.048 | 7315163.06 | 6053053.18 | -32237.3133 | 158931.199 | 9357.7144 | 286841.628 | 61401.9026 | 2498216.89 | -28419.7332 | 64382.7517 | -1249.1417 | 66239.9984 | 32137.1703 | 373098.748 | -8237.505
605.52 | 11.834 | 1.0711 |  | 239654.833 | -178319.48 | 610165.877 | 7385671.2 | 6455683.6 | -36407.7201 | 162193.336 | 12016.586 | 284956.433 | -33419.2803 | 2375811.59 | -28654.4371 | 55820.619 | 2383.9958 | 67257.8043 | 12991.868 | 322804.873 | -6957.7809
605.72 | 11.8758 | 1.0706 |  | 238158.352 | -125932.22 | 572542.055 | 6417717.62 | 6442247.04 | -19679.001 | 159348.231 | 15895.0492 | 273304.342 | -22767.1492 | 2433597.29 | -22415.1845 | 60287.2359 | 453.9752 | 64603.6982 | 17991.5691 | 329868.18 | -7829.146
605.92 | 11.8798 | 1.0706 |  | 242192.217 | -131914.982 | 541547.328 | 6288582.16 | 6461901.82 | -22680.0068 | 149339.903 | 19278.4873 | 268390.237 | -98537.9209 | 2329708.04 | -24492.2877 | 61291.2238 | 2261.6505 | 64132.1276 | 12126.0231 | 359047.018 | -7233.3013
606.12 | 11.9103 | 1.0703 |  | 244800.474 | -119304.073 | 507064.935 | 6011023.35 | 6584925.64 | -23692.0358 | 150750.335 | 22289.7731 | 260023.137 | -72131.9813 | 2386812.08 | -23740.8897 | 61264.4734 | 269.373 | 62405.2315 | 23282.5834 | 342580.711 | -6919.5389
606.32 | 11.9607 | 1.069 |  | 235613.218 | -144031.106 | 476125.09 | 6605764.58 | 6551822.71 | -20170.1027 | 156769.568 | 19894.2727 | 256463.276 | -114211.587 | 2361871.86 | -20997.9646 | 59057.8464 | 2306.4102 | 62362.8464 | 13304.1573 | 333926.074 | -5272.3739
606.52 | 11.9559 | 1.0669 |  | 217870.027 | -177259.061 | 451717.916 | 7454280.03 | 6236127.58 | -32932.6643 | 166166.99 | 9715.3525 | 255203.427 | -27967.8837 | 2405483.72 | -24636.6989 | 58259.9542 | 1666.7718 | 62985.6666 | 13859.2163 | 331170.998 | -6568.765
606.72 | 11.9528 | 1.0644 |  | 188734.634 | -191644.131 | 431322.878 | 7982775.83 | 5442545.07 | -32636.9435 | 167532.598 | -7660.9964 | 250865.414 | 240609.379 | 2597591.49 | -26552.7461 | 66469.5288 | -4456.1045 | 63358.509 | 35617.7912 | 352166.253 | -7820.7398
606.92 | 11.9978 | 1.0617 |  | 157926.154 | -222020.081 | 402939.897 | 8971929.19 | 4890476.72 | -34769.9122 | 174944.686 | -20751.3967 | 239379.682 | 426332.602 | 2773290.51 | -26146.9614 | 73010.5341 | -9008.3731 | 59659.8638 | 63843.3989 | 411887 | -6925.4251
607.12 | 12.0072 | 1.0589 |  | 127193.727 | -249881.503 | 388199.991 | 9846993.62 | 4523553.35 | -37897.1376 | 186423.454 | -29869.8073 | 233537.232 | 535660.653 | 3028598.41 | -30828.1019 | 84381.8626 | -11969.5767 | 59195.5991 | 73362.799 | 461481.583 | -8328.6716
607.32 | 12.0077 | 1.0553 |  | 109607.82 | -299980.393 | 380922.41 | 11169795.3 | 4402643.11 | -54936.8914 | 204074.132 | -39234.8314 | 230397.19 | 621560.82 | 3155997.1 | -41041.8501 | 82834.7948 | -11977.7323 | 57695.2228 | 78798.54 | 467347.592 | -10096.3639
607.52 | 12.0267 | 1.051 |  | 82941.1581 | -322351.166 | 388235.133 | 11882254.6 | 4016422.27 | -53548.0428 | 216474.034 | -49947.1768 | 233638.945 | 728621.391 | 3311612.2 | -37699.6927 | 84748.2363 | -13468.27 | 59562.3671 | 81743.7724 | 464323.831 | -7900.7918
607.72 | 12.0614 | 1.0461 |  | 50183.4464 | -347725.78 | 411190.706 | 12469374.4 | 3340596 | -66851.4549 | 213436.124 | -60414.4472 | 237855.194 | 898052.669 | 3412669.42 | -40787.8761 | 92850.1958 | -17919.8858 | 59510.0382 | 103938.584 | 520470.581 | -9644.991
607.92 | 12.0896 | 1.0412 |  | 14661.6178 | -389836.712 | 442139.934 | 13396845.1 | 2552692.94 | -79321.1692 | 214835.919 | -74503.7747 | 248815.551 | 1071338.67 | 3447522.97 | -41662.7261 | 94343.8911 | -21561.0374 | 62832.2246 | 120202.806 | 525277.021 | -7738.3107
608.12 | 12.1055 | 1.0514 |  | -7212.6658 | -399445.426 | 469938.243 | 13647596.8 | 1923243.49 | -98133.5881 | 218225.048 | -86388.8696 | 251125.695 | 1225100.03 | 3445732.4 | -55781.8073 | 90088.1253 | -22526.8773 | 62161.5483 | 127674.088 | 507488.667 | -14253.4352
608.32 | 12.1037 | 1.3713 |  | -14158.9203 | -385956.056 | 509563.344 | 12856178.6 | 1671972.34 | -87062.6728 | 202437.822 | -81203.7157 | 256441.182 | 1175253.97 | 3262039.2 | -42326.7495 | 86588.4505 | -22877.6262 | 62382.309 | 129817.813 | 482814.086 | -7762.9581
608.52 | 12.1381 | 1.9799 |  | -9648.0687 | -356520.978 | 557195.315 | 11789992.6 | 1855816.64 | -55241.6432 | 189168.042 | -68361.2774 | 265863.986 | 1008136.76 | 3142999.92 | -25914.3017 | 86806.1177 | -20607.5368 | 62755.9957 | 119007.512 | 487625.51 | -3252.477
608.72 | 12.175 | 2.7405 |  | 6413.935 | -351960.453 | 602547.594 | 11419348.8 | 2337301.84 | -66259.0636 | 185948.902 | -55831.9955 | 280576.229 | 772345.958 | 3026924.8 | -40826.0086 | 82102.3107 | -12841.5355 | 65899.9026 | 82484.2451 | 470650.136 | -9589.1346
608.92 | 12.1877 | 3.5449 |  | 37150.021 | -332707.777 | 646901.969 | 10596788.9 | 2884837.1 | -62393.7078 | 175596.703 | -41773.8227 | 297048.511 | 629379.049 | 2730150.2 | -36590.3022 | 71174.7361 | -11045.3431 | 69707.4368 | 77412.4625 | 410483.488 | -7472.087
609.12 | 12.2399 | 4.2436 |  | 39708.1501 | -298365.684 | 688477.15 | 9661759.68 | 2617758.67 | -49490.6305 | 158384.669 | -39487.1404 | 309787.809 | 581489.65 | 2578939.47 | -27173.0449 | 69413.9459 | -9467.2729 | 72166.303 | 64055.3071 | 397192.617 | -5733.0887
609.32 | 12.301 | 4.963 |  | 66658.9938 | -275671.895 | 715733.109 | 9159119.73 | 3002793.44 | -49549.1567 | 154658.264 | -33678.4835 | 317504.606 | 541956.597 | 2464929.35 | -31987.9129 | 65120.5851 | -9116.2267 | 73911.949 | 62970.2253 | 365516.922 | -7917.0545
609.52 | 12.3549 | 5.7301 |  | 104068.78 | -262296.147 | 733414.26 | 8643694.81 | 3712964.69 | -51594.4817 | 150272.279 | -21021.1508 | 321565.548 | 355759.854 | 2230539.85 | -33532.5321 | 57211.0133 | -4944.7858 | 73596.2419 | 44146.2362 | 327835.819 | -8242.1748
609.72 | 12.3887 | 6.531 |  | 120828.377 | -186799.892 | 737657.961 | 6679164.49 | 3945490.33 | -51307.9357 | 129716.024 | -3857.6411 | 321903.46 | 154693.854 | 2064814.22 | -39843.5335 | 55221.6504 | -772.3672 | 74070.0302 | 23927.8202 | 318823.946 | -12541.1119
609.92 | 12.3921 | 7.2875 |  | 135320.379 | -112680.207 | 740619.805 | 4375015.67 | 3877335.19 | -46714.2336 | 95269.2792 | 12488.8371 | 324927.77 | -25653.7949 | 1595818.74 | -30601.2138 | 45787.3656 | 1643.0744 | 74268.1673 | 16063.5287 | 285146.821 | -8477.5424

## Costs
Costs
Single Blade [$] | 120901.5661
Three Blades [$] | 362704.6983
Hub [$] | 90802.0781
Pitch System [$] | 199448.9965
Nose [$] | 10496.665
Rotor Total [$] | 663452.4378
Shaft [$] | 12675.1894
Bearing [$] | 106101.8461
GearBox [$] | 266760
Brakes [$] | 7161.7259
Generator [$] | 197028
Electronics [$] | 284400
Yaw [$] | 125013.7521
Main Frame [$] | 206219.0688
Electrical System [$] | 144000
Cooling System [$] | 43200
Nacelle [$] | 45382.9
Nacelle Total [$] | 1437942.4823
Tower [$] | 829755.2825
Marinization [$] | 0
Turbine Capital Cost [$] | 2931185.2027
Foundation [$] | 93399.0293
Transportation [$] | 448551.36
Civil Work [$] | 163667.52
Installation [$] | 147932.9536
Electrical Interface [$] | 271333.44
Engineering and Permits [$] | 85998.24
Balance of Station [$] | 1210882.5429
Initial Capital Cost [$] | 4142067.7456
Operation and Maintenance [$] | 97554.4717
Cost of Energy [$/MWh] | 44.1813

## NoiseAnalysis
Wind Speed [m/s] | OASPL [dB] | OASPL A [dB(A)]
7 | 70.8164 | 50.9792
13 | 70.6872 | 54.4021